## iSlims_WO_Problem_Code_Complete
WO Date | Wo ID | Address1 | Address2 | Quad | Close Date | Streetlight # | VALIDID | Problem Code | comments (trnWO) | Lighttype | Lat_X | Lon_Y
11/16/16 | 1209661 | 0000 | H ST | NE | 11/17/16 | 68247DC | 68247 | (Light out) |  | High Pressure Sodium | 38.90004666000 | -77.00500029000
11/14/16 | 1209298 | 2800 | BLADENSBURG RD | NE | 11/22/16 | 50092 | 5A078 | (Light out) | Jose Recinos at 11/22/2016 3:30:03 PM: Installed 200 ft of #10 wire from pole base to manhole also make splicing on manhole light work properly 100% completed Naji Carson at 11/16/2016 4:26:19 AM: no current underground | High Pressure Sodium | 38.92548918000 | -76.96461140000
11/13/16 | 1209270 | 1418 | BRUCE PL | SE | 11/15/16 | 81788 | 88065 | (Light out) | Jose Mancia at 11/15/2016 10:18:25 PM: 100% REPLACED 250W HPS LAMP 16-00802750-on the corner cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85054078000 | -76.98359853000
| 1209198 | 3200 | CAMDEN ST | SE | 11/15/16 | 74754DC | 7A068DC | (Light out) | Jose Mancia at 11/15/2016 8:57:30 PM: 100% REPLACED 250W HPS LAMP 16-00801674-Streetlight Repair Investigation Additional details and/or comments at http://seeclickfix.com/issues/3053007. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85947917000 | -76.96057358000
11/10/16 | 1209073 | 705 | ANACOSTIA AVE | NE | 11/10/16 | 72356DC | 7A478 | (Light out) | Steve Redifer 11-9-16-Replaced 100w bulb | High Pressure Sodium | 38.90141616000 | -76.95127149000
11/9/16 | 1208787 | 0400 | TAYLOR ST | NE | 11/9/16 | 50087 | 5A068 | (Light out) | Jose Mancia at 11/9/2016 11:20:53 PM: 100% REPLACED. 400W HPS LAMP NSV | High Pressure Sodium | 38.94068700000 | -77.00116728000
11/9/16 | 1208786 | 0400 | TAYLOR ST | NE | 11/23/16 | 50086 | 5A067 | (Light out) | Carlos Ruiz at 11/23/2016 1:11:21 PM: 100% Done- splice damaged wire at manhole Jose Mancia at 11/9/2016 11:02:30 PM: NO CURRENT UNDERGROUND NSV | High Pressure Sodium | 38.94068754000 | -77.00205144000
11/9/16 | 1208775 | 0000 | SOUTH DAKOTA AVE | NE | 11/14/16 | 50068 | 5M186 | (Light out) | Juan Escobar at 11/14/2016 12:07:23 AM: 100% PHOTOCELL | High Pressure Sodium | 38.91891047000 | -76.95612724000
11/9/16 | 1208773 | 2800 | LINCOLN RD | NE | 11/9/16 | 50065 | 5A056 | (Light out) | : Juan Escobar at 11/9/2016 8:50:31 PM: 100% PHOTOCELL | High Pressure Sodium | 38.92549974000 | -77.00275988000
11/9/16 | 1208772 | 1625 | NEW YORK AVE | NE | 11/14/16 | 50062 | 5A053 | (Light out) | Juan Escobar at 11/14/2016 1:23:16 AM: 100% PHOTOCELL | High Pressure Sodium | 38.91708690000 | -76.98011488000
11/9/16 | 1208771 | 1765 | NEW YORK AVE | NE | 11/14/16 | 50060 | 5A051 | (Light out) | Juan Escobar at 11/14/2016 1:21:51 AM: 100% PHOTOCELL | High Pressure Sodium | 38.91711198000 | -76.97897966000
11/9/16 | 1208770 | 1765 | NEW YORK AVE | NE | 11/14/16 | 50059 | 5A050 | (Light out) | Juan Escobar at 11/14/2016 2:26:28 AM: 100% PHOTOCELL | High Pressure Sodium | 38.91711725000 | -76.97869992000
11/4/16 | 1208238 | 0329 | RHODE ISLAND AVE | NE | 11/6/16 | 50083 | 5A064 | (Light out) | Juan Escobar at 11/6/2016 1:15:38 AM: 100% PHOTOCELL | High Pressure Sodium | 38.91949870000 | -77.00096444000
11/3/16 | 1208048 | 5656 | 3RD ST | NE | 11/18/16 | 4P473DC | 4U162 | (Light out) | Jose Recinos at 11/18/2016 11:20:01 AM: Installed 160 ft of #2 insulation cable from pole #4P473DC to pole #4P472DC also installed one photo cell 100% Jose Mancia at 11/3/2016 8:57:48 PM: DONT HAVE FEEDER/ SECONDARY MISSING | High Pressure Sodium | 38.95791886000 | -77.00307597000
11/2/16 | 1207969 | 2222 | WISCONSIN AVE | NW | 11/5/16 | 30162 | 3G082 | (Light out) | Ismael Hernandez at 11/4/2016 10:42:45 PM: 100% replaced 400w HPS ballast, replace TLPC and replaced 400w HPS lamp | High Pressure Sodium | 38.91993778000 | -77.07113468000
10/31/16 | 1207592 | 3402 | 15TH ST | NE | 10/31/16 | 51213DC | 5A102DC | (Light out) | 100% complete | High Pressure Sodium | 38.93214204000 | -76.98444256000
10/31/16 | 1207283 | 0 | NEW YORK AVE | NE | 10/31/16 | 50005 | 5A039 | (Light out) | Cristian 10-27-16-replaced 400w bulb and photocell | High Pressure Sodium | 38.91734425000 | -76.96859446000
10/31/16 | 1207121 | 0 | KENILWORTH AVE | SE | 11/4/16 | 79496 | 7A149 | (Light out) | Naji Carson at 11/4/2016 1:08:05 AM: 100% replaced 250 watt HPS lamp TLPC | High Pressure Sodium | 38.88522570000 | -76.96311007000
| 1207069 | 2800 | BLADENSBURG RD | NE | 11/8/16 | 50092 | 5A078 | (Light out) | Alexander Portales at 11/8/2016 1:43:16 PM: 100% replaced TLPC Cristian Hudisteanu at 11/2/2016 9:19:13 PM: NO CURRENT 16-00777936-Streetlight Repair Investigation Streetlight off during night time hours. Additional details and/or comments | High Pressure Sodium | 38.92548918000 | -76.96461140000
10/28/16 | 1207046 | 1530 | 11TH ST | NW | 10/30/16 | 25286 | 2U045 | (Light out) | Juan Escobar at 10/30/2016 8:49:49 PM: 100% 400W HPS LAMP 16-00777208- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91105847000 | -77.02715860000
10/27/16 | 1206851 | 0 | RHODE ISLAND AVE | NE | 10/29/16 | 50104 | 56340 | (Light out) | : Naji Carson at 10/29/2016 2:36:55 AM: 100% replaced 250w HPS lamp----NSV | High Pressure Sodium | 38.91934333000 | -77.00215180000
10/27/16 | 1206804 | 2911 | RHODE ISLAND AVE | NE | 10/28/16 | 52505DC | 5A166DC | (Light out) | Jose Mancia at 10/28/2016 5:28:43 PM: 100%. REPLACED 400W HPS LAMP WP | High Pressure Sodium | 38.93345368000 | -76.96676649000
10/27/16 | 1206795 | 2826 | BLADENSBURG RD | NE | 10/29/16 | 50095 | 5A081 | (Light out) | Naji Carson at 10/29/2016 1:01:40 AM: 100% replaced 250w HPS lamp and photocell--- NSV | High Pressure Sodium | 38.92629564000 | -76.96361882000
10/27/16 | 1206789 | 2800 | BLADENSBURG RD | NE | 12/14/16 | 50092 | 5A078 | (Light out) | 100% 180 feet of new streetlight cable installed. Spliced feeder Carlos Ruiz at 11/8/2016 9:05:53 AM: No current with cut. SLP is in new foundation and there's a obstruction inside conduit Naji Carson at 10/29/2016 12:55:04 AM: no current undergroun | High Pressure Sodium | 38.92548918000 | -76.96461140000
10/27/16 | 1206788 | 2838 | BLADENSBURG RD | NE | 11/3/16 | 51238DC | 5A134DC | (Light out) | Carlos Ruiz at 11/3/2016 10:28:12 AM: 100% Done - Replaced burn out 250w tear drop fixture, and 60' of #10 wire Naji Carson at 10/29/2016 1:29:21 AM: no current overhead | High Pressure Sodium | 38.92682989000 | -76.96333203000
10/27/16 | 1206781 | 0 | NEW YORK AVE | NE | 10/28/16 | 50013 | 5A048 | (Light out) | Jose Aguilar at 10/28/2016 8:51:28 PM: 100% replace 400W HPS fixture , 2 bulbs 400W and 2 photocell . NSV | High Pressure Sodium | 38.91696428000 | -76.96182720000
10/27/16 | 1206780 | 0 | NEW YORK AVE | NE | 10/29/16 | 50010 | 5A044 | (Light out) | Jose Aguilar at 10/28/2016 9:33:42 PM: 100% replace 400W power door , 400W bulb and photocell . NSV | High Pressure Sodium | 38.91713437000 | -76.96502016000
10/27/16 | 1206779 | 0 | NEW YORK AVE | NE | 10/28/16 | 50009 | 5A043 | (Light out) | Jose Aguilar at 10/28/2016 8:19:53 PM: 100% replace 400W bulb and photocell . NSV | High Pressure Sodium | 38.91719217000 | -76.96575011000
10/27/16 | 1206741 | 0 | INTERSTATE 295 | SE | 10/31/16 | 68050 | 6L972 | (Light out) | Jose Aguilar at 10/31/2016 3:21:05 AM: 100% replaced 400 Watts HPS POWERDOOR, lamp and TLPC NSV | High Pressure Sodium | 38.87795866000 | -76.99246087000
10/27/16 | 1206706 | 0 | INTERSTATE 295 | SE | 10/31/16 | 68050 | 6L972 | (Light out) | Jose Aguilar at 10/31/2016 1:11:07 AM: 100% replaced 400 Watts HPS POWERDOOR, lamp and TLPC NSV | High Pressure Sodium | 38.87795866000 | -76.99246087000
10/27/16 | 1206702 | 0 | LEE ST | NE | 11/1/16 | 70327 | 7M082 | (Light out) | Juan Escobar at 11/1/2016 1:40:36 AM: 100% replaced photocell | High Pressure Sodium | 38.90317749000 | -76.94336293000
10/27/16 | 1206698 | 0 | ANACOSTIA FWY | SE | 10/30/16 | 79465 | 7A129 | (Light out) | Jose Aguilar at 10/30/2016 10:04:23 PM: 100% replaced 400w HPS lamp and TLPC NSV | High Pressure Sodium | 38.88861563000 | -76.96080132000
10/27/16 | 1206697 | 0 | KENILWORTH AVE | SE | 10/31/16 | 79492 | 7A161 | (Light out) | Jose Aguilar at 10/31/2016 3:14:35 AM: 100% replaced 400 Watts HPS POWERDOOR, and TLPC NSV | High Pressure Sodium | 38.88905101000 | -76.96038452000
10/25/16 | 1206269 | 4811 | NORTH CAPITOL ST | NW | 10/29/16 | 4R751 | 4A792 | (Light out) | Jose Mancia at 10/28/2016 10:09:04 PM: 100% replaced 400W HPS lamp-NSV | High Pressure Sodium | 38.94920682000 | -77.00886682000
10/21/16 | 1205876 | 1200 | 11TH ST | SE | 11/1/16 | 67740 | 6L938 | (Light out) | Jose Mancia at 10/25/2016 10:44:57 PM: NO CURRENT UNDERGROUND xchngeMcDean; Brian Maynard at 11/1/2016 7:55:49 AM: DUPLICATE TO WO#1204705 Jose Mancia at 10/25/2016 10:44:57 PM: NO CURRENT UNDERGROUND | High Pressure Sodium | 38.87633690000 | -76.99165150000
10/21/16 | 1205812 | 5412 | E ST | SE | 10/26/16 | 75501 | 75501DC | (Light out) | Thomas Wallace at 10/26/2016 3:51:49 PM: 100% Complete reconnected loose wire Juan Escobar at 10/25/2016 1:47:22 AM: NO CURRENT OVERHEAD | High Pressure Sodium | 38.88126024000 | -76.92504376000
10/21/16 | 1205795 | 4479 | F ST | SE | 10/25/16 | 75749 | 75749DC | (Light out) | ose Mancia at 10/25/2016 8:31:39 PM: 100% REPLACED 250W HPS LAMP WP | High Pressure Sodium | 38.88184868000 | -76.93731162000
| 1205541 | 1401 | V ST | SE | 10/26/16 | 80878 | 8M028DC | (Light out) | Juan Escobar at 10/26/2016 2:30:59 AM: 100% replaced 400W HPS lamp 16-00760917-on V at the stop sign lights are out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86497272000 | -76.98559684000
10/19/16 | 1205302 | 1020 | 1ST ST | SE | 10/24/16 | 67447 | 6A077 | (Light out) | Jose Mancia at 10/24/2016 8:26:15 PM: 100% REPLACED 250W HPS LAMP NSV 16-00760176-Bulb appears to be out. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.87776178000 | -77.00603158000
10/17/16 | 1204717 | 0 | H ST | NW | 10/22/16 | 22569 | 2M434 | (Light out) | Ismael Hernandez at 10/21/2016 11:55:33 PM: 100% replaced 400w HPS lamp---- NSV | High Pressure Sodium | 38.89973622000 | -77.02284281000
10/17/16 | 1204705 | 1200 | 11TH ST | SE | 11/3/16 | 67740 | 6L938 | (Light out) | : Thomas Wallace at 11/3/2016 12:39:22 PM: 100% Complete installed 125' #10 wire from manhole to fixture for bad hot wire Jose Mancia at 10/19/2016 11:22:32 PM: upon arrival at this location have no current underground-SV | High Pressure Sodium | 38.87633690000 | -76.99165150000
10/13/16 | 1204308 | 206 | RHODE ISLAND AVE | NW | 10/18/16 | 59996 | 5A188 | (Light out) | Naji Carson at 10/17/2016 10:52:15 PM: 100% replaced 400 watt HPS lamp TLPC 16-00749288-The street light that needs to be repair is right in front of this location. cwDesc: STREETLIGHT REPAIR | Incandescent | 38.91473859000 | -77.01463730000
10/11/16 | 1203884 | 4500 | ROCK CREEK CHURCH RD | NE | 10/14/16 | 4R757 | 4A798 | (Light out) | Jose Mancia at 10/13/2016 10:06:35 PM: 100% replaced 250W HPS lamp | High Pressure Sodium | 38.94697525000 | -77.00871139000
10/11/16 | 1203762 | 0400 | TAYLOR ST | NE | 10/19/16 | 50087 | 5A068 | (Light out) | Steven Redifer at 10/19/2016 1:56:06 PM: 100%, replaced 400 watt bulb CRISTIAN-10/07/2016-NO CURRENT | High Pressure Sodium | 38.94068700000 | -77.00116728000
10/11/16 | 1203704 | 1771 | N ST | NW | 12/21/16 | 27182 | 2U512 | (Light out) | Alexander Portales at 11/1/2016 10:50:01 AM: PEPCO refer no current on PEPCO line. Ismael Hernandez at 10/17/2016 8:40:51 PM: NO CURRENT UNDERGROUND ,THIS IS LED TEAR DROP 16-00742724-undefined cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90719403000 | -77.04157485000
10/7/16 | 1203351 | 2826 | BLADENSBURG RD | NE | 10/13/16 | 51239DC | 5A135DC | (Light out) | Jose Mancia at 10/13/2016 5:39:47 PM: 100% REPLACED 250W HPS LAMP WP 1 16-00737797-Streetlight Repair Investigation 51239DC Additional details and/or comments at http://seeclickfix.com/issues/2976089. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92654970000 | -76.96367069000
10/5/16 | 1202961 | 0000 | H ST | NE | 10/5/16 | 68243DC | 68243 | (Light out) | Cristian 10-4-16-replaced 400w bulb and photocell and 400w power door | High Pressure Sodium | 38.90008908000 | -77.00731064000
10/5/16 | 1202959 | 0000 | H ST | NE | 10/5/16 | 68242DC | 68242 | (Light out) | Cristian 10-4-16-replaced 400w bulb and photocell | High Pressure Sodium | 38.90009857000 | -77.00808944000
10/5/16 | 1202650 | 0400 | TAYLOR ST | NE | 10/7/16 | 50087 | 5A068 | (Light out) | Cristian Hudisteanu at 10/7/2016 9:19:34 PM: 100% replace 400W bulb and photocell 16-00732347-THIS IS THE 300 BLOCK OF TAYLOR STREET NE -- EASTBOUND LANE. AGAIN, TWO STREET LIGHTS THAT ARE DARK. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94068700000 | -77.00116728000
9/28/16 | 1201683 | 0000 | MONTANA AVE | NE | 10/3/16 | 50075 | 5A060 | (Light out) | Cristian Hudisteanu at 10/3/2016 10:49:56 PM: 100% replace 400W bulb and photocell . NSV 16-00718827- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91680835000 | -76.97824997000
9/26/16 | 1201010 | 0 | 7TH ST | NW | 9/26/16 | 22409 | 6M688 | (Light out) | KEITH BURRESS-09/25/2016-REPLACED LAMP | High Pressure Sodium | 38.90199325000 | -77.02201951000
9/26/16 | 1200842 | 1718 | 7TH ST | NW | 9/27/16 | 25707 | 6A836 | (Light out) | Cristian Hudisteanu at 9/27/2016 1:30:47 AM: 100% replace 400W and photocell 16-00713732-Alleylight Repair Investigation Street lights out on both sides of street in dangerous area. Multiple lights out along 7th street. Please repair. Addition | High Pressure Sodium | 38.91317833000 | -77.02182199000
9/25/16 | 1200701 | 0 | OVERLOOK AVE | SE | 10/2/16 | 81816 | 88089 | (Light out) | Thomas Wallace at 10/2/2016 1:38:15 AM: 100% this light has everything new and it is working 100% Installed new lamp and PC. 9/30/16 | High Pressure Sodium | 38.83181785000 | -77.01472372000
9/22/16 | 1200390 | 3216 | 15TH PL | SE | 9/24/16 | 81721 | 87998 | (Light out) | Naji Carson at 9/24/2016 3:38:25 AM: 100% Replaced 400w HPS lamp 16-00709643-fgf cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84905775000 | -76.98211177000
9/22/16 | 1200333 | 80 | 1ST ST | SE | 9/27/16 | 67445 | 6A015 | (Light out) | Jose Mancia at 9/27/2016 12:22:13 AM: 100% REPLACED 300W INCANDESCENT | High Pressure Sodium | 38.87689360000 | -77.00599612000
9/22/16 | 1200329 | 80 | M ST | SE | 9/24/16 | 67325 | 68565 | (Light out) | Naji Carson at 9/24/2016 2:58:57 AM: 1026 3rd St SE 100% replaced 250 watt HPS lamp; TLPC; starter | High Pressure Sodium | 38.87639069000 | -77.00569976000
9/22/16 | 1200321 | 0000 | INTERSTATE 295 | SE | 9/22/16 | 395-039N-4 | SCSN610 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88267813000 | -77.01154240000
9/22/16 | 1200320 | 0000 | INTERSTATE 295 | SE | 9/22/16 | 395-037N-4 | SCSN606 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88089442000 | -77.00887168000
9/22/16 | 1200319 | 0000 | INTERSTATE 295 | SE | 9/22/16 | 395-038N-4 | SCSN604 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.87965588000 | -77.00887004000
9/22/16 | 1200318 | 0000 | INTERSTATE 395 | SW | 9/22/16 | 395-021W-8 | 695W615 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88146328000 | -77.00806581000
9/22/16 | 1200317 | 0 | INTERSTATE 395 | SW | 9/22/16 | 395-028S-4 | 395S603 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88448494000 | -77.01260002000
9/22/16 | 1200315 | 0 | INTERSTATE 695 | SE | 9/22/16 | 695-002W-6 | 695W611 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88104238000 | -77.00567540000
9/22/16 | 1200314 | 0 | INTERSTATE 695 | SE | 9/22/16 | 695-001W-9 | 695W613 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88110666000 | -77.00656804000
9/19/16 | 1199498 | 819 | 6TH ST | NW | 9/19/16 | 60541 | 6M706 | (Light out) | JOSE M-09/15/2016-REPLACED LAMP | High Pressure Sodium | 38.90043550000 | -77.01979597000
9/14/16 | 1199012 | 815 | 6TH ST | NW | 9/19/16 | 60542 | 6M707 | (Light out) | jose Mancia at 9/19/2016 5:52:38 PM: 100% REPLACED 400W HPS LAMP NSV In front of property. 16-00695104- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90031850000 | -77.01979505000
9/14/16 | 1199010 | 815 | 6TH ST | NW | 9/19/16 | 60542 | 6M707 | (Light out) | Jose Mancia at 9/19/2016 5:54:45 PM: 100% replaced 250W HPS lamp In front of property. 16-00695098- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90031850000 | -77.01979505000
9/14/16 | 1198826 | 2222 | WISCONSIN AVE | NW | 9/18/16 | 30162 | 3G082 | (Light out) | Juan Escobar at 9/18/2016 3:33:52 AM: 100% PHOTOCELL | High Pressure Sodium | 38.91993778000 | -77.07113468000
9/14/16 | 1198766 | 600 | 5TH ST | NW | 9/19/16 | 60082 | 6S532 | (Light off/on) | Jose Mancia at 9/19/2016 7:02:22 PM: 100% REPLACED 400W HPS LAMP NSV | High Pressure Sodium | 38.89786611000 | -77.01883805000
9/14/16 | 1198764 | 5600 | 3RD ST | NE | 9/16/16 | 4P471DC | 4U158 | (Light out) | Ismael Hernandez at 9/15/2016 10:08:41 PM: 100% REPLACED 400W HPS LAMP,TLPC---WP | High Pressure Sodium | 38.95858464000 | -77.00292664000
9/14/16 | 1198746 | 1512 | 7TH ST | NW | 9/16/16 | 25701 | 6A810 | (Light out) | Jose Mancia at 9/16/2016 9:10:24 PM: 100% replaced 400W HPS lamp | High Pressure Sodium | 38.91011315000 | -77.02182614000
9/13/16 | 1198642 | 819 | 6TH ST | NW | 9/16/16 | 60541 | 6M706 | (Light out) | Jose Mancia at 9/15/2016 11:00:30 PM: 100% REPLACED 250 CONVERSION KIT NSV | High Pressure Sodium | 38.90043550000 | -77.01979597000
9/13/16 | 1198640 | 815 | 6TH ST | NW | 9/16/16 | 60542 | 6M707 | (Light out) | Jose Mancia at 9/15/2016 11:00:30 PM: 100% REPLACED 250 CONVERSION KIT NSV | High Pressure Sodium | 38.90031850000 | -77.01979505000
| 1196793 | 1900 | 37TH ST | NW | 8/30/16 | 36891 | 30482 | (Light out) | Alexander Portales at 8/30/2016 9:32:41 PM: 100% replaced 150w HPS lamp (WP) pole 36891dc 16-00666550-Streetlight Repair Investigation Burnt out streetlight on 37 NW at intersection with UNW Additional details and/or comments at http://seeclick | High Pressure Sodium | 38.91672906000 | -77.07292654000
8/24/16 | 1196096 | 0000 | UPSHUR ST | NW | 8/25/16 | 4R786 | 4R794 | (Light out) | Carlos Ruiz at 8/25/2016 9:07:59 PM: 100% finished 400w HPS lamp | High Pressure Sodium | 38.94192153000 | -77.02684910000
8/16/16 | 1194962 | 0 | H ST | NW | 8/22/16 | 22569 | 2M434 | (Light out) | Darrell Vines at 8/21/2016: 100% Installed 250w HPS lamp NW., NW., The Streetlight is a few yards east of 702 H Street 16-00643746- cwDesc: STREETLIGHT REPAIR xchngeMcDean; Darrell Vines at 8/21/2016: 100% Installed 250w HPS lamp NW., The Streetli | High Pressure Sodium | 38.89973622000 | -77.02284281000
8/12/16 | 1194712 | 0 | 7TH ST | NW | 8/17/16 | 22409 | 6M688 | (Light out) | xchngeMcDean; Carlos Ruiz at 8/16/2016: 100% replaced 400w hps lamps INTERSECTION OF MASS, 7TH, AND K ST | High Pressure Sodium | 38.90199325000 | -77.02201951000
8/12/16 | 1194687 | 0000 | OVERLOOK AVE | SE | 8/12/16 | 81815 | 88088 | (Light out) | eanette Lindsay at 8/12/2016 11:48:07 AM: Tony A 8-11-16-Replaced 400w HPS bulb Tony A 8-11-16-Replaced 400w HPS bulb | High Pressure Sodium | 38.83154015000 | -77.01497801000
8/11/16 | 1194452 | 0000 | OVERLOOK AVE | SW | 8/13/16 | 81832 | 88093 | (Light out) | Jose Aguilar at 8/13/2016 12:17:34 AM: 100% replaced 400 watts HPS bulb and TLPC | High Pressure Sodium | 38.83453118000 | -77.01284962000
8/11/16 | 1194451 | 0000 | OVERLOOK AVE | SW | 8/13/16 | 81831 | 88092 | (Light out) | Jose Aguilar at 8/13/2016 12:14:15 AM: 100% replaced 250 watts HPS bulb and TLPC | High Pressure Sodium | 38.83482648000 | -77.01263154000
8/11/16 | 1194450 | 0000 | OVERLOOK AVE | SW | 8/13/16 | 81829 | 88090 | (Light out) | Jose Aguilar at 8/12/2016 11:56:32 PM: 100% replaced 250 watts HPS bulb | High Pressure Sodium | 38.83542082000 | -77.01218955000
8/8/16 | 1194148 | 2200 | H ST | NW | 9/21/16 | 27996 | 2A218 | (Light out) | Cristian Hudisteanu at 8/19/2016 2:43:45 PM: Refer to DDOT construction area street light job not finish Alexander Portales at 7/6/2016 3:45:55 AM: no current underground | High Pressure Sodium | 38.89963734000 | -77.04920747000
8/5/16 | 1193760 | 1020 | 1ST ST | SE | 8/10/16 | 67447 | 6A077 | (Light out) | Alexander Portales at 8/9/2016 11:30:00 PM: 100% replaced 250W HPS lamp -- NSV -- POLE 67447 6A077 | High Pressure Sodium | 38.87776178000 | -77.00603158000
7/28/16 | 1192754 | 600 | MAINE AVE | SW |  | 66552 | 6S515 | (Light out) | Cristian Hudisteanu at 8/8/2016 1:49:49 PM: Refer to DDOT. Refer to DDOT - inside fence at D.C. Wharf construction project - Maine ave 16-00613140- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.87706636000 | -77.02074410000
7/28/16 | 1192667 | 0 | KENILWORTH AVE | NE | 8/3/16 | 79463 | 7A127 | (Light out) |  | High Pressure Sodium | 38.88994563000 | -76.95813630000
7/26/16 | 1192479 | 1443 | LAWRENCE ST | NE | 7/26/16 | 52488DC | 5A159DC | (Light out) | Glenn/Alex-7-24-16-Replaced 150w light bulb | High Pressure Sodium | 38.93180662000 | -76.98505493000
7/20/16 | 1192031 | 0 | EAST CAPITOL ST | SE | 7/26/16 | 73588 | 73588DC | (Light out) | Thomas Wallace at 7/25/2016 11:59:37 PM: 100% Complete replaced 250w bulb & TLPC corner 16-00596882- By KENNEY, BRENDA L: 7/20/2016 1:39:07 PM 53RD AND EAST CAPITOL STREET, SE cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88965078000 | -76.92405517000
7/20/16 | 1191948 | 1443 | LAWRENCE ST | NE | 7/23/16 | 52488DC | 5A159DC | (Light out) | Jose Aguilar at 7/23/2016 10:28:21 PM: 100% replaced 150w HPS light bulb FRONT 16-00596417- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93180662000 | -76.98505493000
7/19/16 | 1191869 | 803 | EASTERN AVE | NE | 7/21/16 | 79471 | 7A135 | (Light out) | Jose Mancia at 7/21/2016 5:23:32 PM: 100% replaced 250W HPS lamp | High Pressure Sodium | 38.88055222000 | -76.96517808000
7/19/16 | 1191867 | 0000 | BENNING RD | NE | 7/26/16 | 70022 | 7A061 | (Light out) | Thomas Wallace at 7/25/2016 11:37:23 PM: 100% Complete replaced 2-400w bulbs | High Pressure Sodium | 38.88979475000 | -76.93755144000
7/12/16 | 1191209 | 4431 | F ST | SE | 7/14/16 | 75747 | 75747DC | (Light out) | Carlos Ruiz at 7/14/2016 12:57:35 AM: 100% complete replaced 250w power door HPS and TLPC 16-00586583-across the street from the house cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88175349000 | -76.93806754000
7/5/16 | 1190378 | 1401 | V ST | SE | 7/12/16 | 80878 | 8M028DC | (Light out) | Mary Jones at 7/12/2016 12:06:40 AM: 100% INSTALED 1 400 HPS BULB NSV | High Pressure Sodium | 38.86497272000 | -76.98559684000
7/5/16 | 1190377 | 1401 | V ST | SE | 7/5/16 | 80878 | 8M028DC | (Light out) | JOSE MANICA-06/30/2016-REPLACED 250W TEAR DROP BALLAST, LAMP AND PC | High Pressure Sodium | 38.86497272000 | -76.98559684000
7/5/16 | 1190354 | 1200 | 11TH ST | SE | 7/5/16 | 67740 | 6L938 | (Light off/on) | CRISTIAN-07/02/2016- CLEANED GLOBE FOR T-DROP FIXTURE | High Pressure Sodium | 38.87633690000 | -76.99165150000
| 1189565 | 3641 | BANGOR ST | SE | 7/8/16 | 74815DC | 7A087DC | (Light out) | Jose Aguilar at 7/8/2016 4:36:19 AM: 100% replaced 150 Watts HPS lamp ****** WP ** 16-00565584-street light out in the alley beside address listed. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86030331000 | -76.95456197000
6/20/16 | 1188946 | 1421 | 34TH ST | NW | 6/25/16 | 21073 | 2G189 | (Light out) | Jose Aguilar at 6/25/2016 2:50:23 AM: 100% replaced 400 Watts HPS lamp | High Pressure Sodium | 38.90848178000 | -77.06790108000
6/20/16 | 1188913 | 1401 | V ST | SE | 7/1/16 | 80878 | 8M028DC | (Light out) | Jose Mancia at 7/1/2016 12:07:13 PM: 100% reconnected wires to main feeder on MH near north west corne Thomas Wallace at 6/22/2016 1:19:09 AM: NC UNDERGROUND-NSV | High Pressure Sodium | 38.86497272000 | -76.98559684000
6/16/16 | 1188724 | 1400 | ROBINSON ST | SE | 6/21/16 | 81738 | 88015 | (Light out) | Thomas Wallace at 6/21/2016 6:28:21 PM: 100% Complete replaced 150w bulb-NSV | High Pressure Sodium | 38.84949808000 | -76.98421107000
6/7/16 | 1187262 | 0000 | BENNING RD | NE | 6/10/16 | 70022 | 7A061 | (Light out) | Jose Mancia at 6/10/2016 1:47:56 PM: 100% installed 400W HPS power door, T/L photocell and 100ft of #10 insulated wire Thomas Wallace at 6/8/2016 1:17:20 AM: repaired one light but other needs new wire ran upp pole. | High Pressure Sodium | 38.88979475000 | -76.93755144000
6/6/16 | 1187253 | 0000 | ROBINSON ST | SE | 6/7/16 | 81757 | 88034 | (Light out) | Thomas Wallace at 6/7/2016 9:35:05 PM: 100% replaced 250W hps lamp. front 16-00536374-the light directly in front of this address keeps going off and on all night long. A request was put in confirmation # 16-00519074 but its still going out and on cw | High Pressure Sodium | 38.84973980000 | -76.98397493000
6/6/16 | 1187198 | 0000 | BENNING RD | NE | 6/7/16 | 70022 | 7A061 | (Light out) | Thomas Wallace at 6/6/2016 10:02:51 PM: 100% complete replaced 2-400w HPS lamp and 400w POWERDOOR | High Pressure Sodium | 38.88979475000 | -76.93755144000
6/6/16 | 1187195 | 1200 | 11TH ST | SE | 7/2/16 | 67740 | 6L938 | (Light out) | Cristian-7-2-2016-100 % made splices in a manhole , replace 400 W bulb and photocell Jose Mancia at 6/30/2016 1:06:19 PM: upon arrival at this location have MH on middle of the street we need proper MOT Jose Aguilar at 6/11/2016 2:43:11 AM: no cur | High Pressure Sodium | 38.87633690000 | -76.99165150000
6/6/16 | 1187156 | 5900 | EAST CAPITOL ST | NE | 6/7/16 | 73559 | 73559DC | (Light out) | Thomas Wallace at 6/6/2016 10:15:37 PM: 100% Complete replaced 1-250w HPS lamp | High Pressure Sodium | 38.88964122000 | -76.91459774000
6/3/16 | 1187038 | 809 | INTERSTATE 295 | NE | 6/8/16 | 79474 | 7A138 | (Light out) | Jose Malpartida at 6/8/2016 7:23:31 PM: replaced 150 watts light bulb 100 % 16-00533036- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.88176234000 | -76.96414383000
6/3/16 | 1186993 | 3227 | STANTON RD | SE | 6/3/16 | 81725 | 88002 | (Light out) | TONY-06/02/2016-REPLACED LAMP AND PC | High Pressure Sodium | 38.84896255000 | -76.98141403000
6/3/16 | 1186987 | 1524 | TANNER CT | SE | 6/3/16 | 81771 | 88048 | (Light out) | TONY-06/02/2016-REPLACED LAMP | High Pressure Sodium | 38.84771521000 | -76.98170485000
6/3/16 | 1186986 | 1517 | TUBMAN RD | SE | 6/3/16 | 81742 | 88019 | (Light out) | TONY-06/02/2016-REPLACED LAMP AND PC | High Pressure Sodium | 38.84803068000 | -76.98185340000
6/3/16 | 1186985 | 3261 | STANTON RD | SE | 6/3/16 | 81745 | 88022 | (Light out) | TONY-06/02/2016-REPLACED LAMP AND PC | High Pressure Sodium | 38.84770266000 | -76.98109122000
6/3/16 | 1186984 | 1546 | ALABAMA AVE | SE | 6/3/16 | 81747 | 88024 | (Light out) | TONY-06/02/2016-REPLACED LAMP ,PC AND POWERDOOR | High Pressure Sodium | 38.84710965000 | -76.98107212000
6/3/16 | 1186983 | 3268 | 15TH PL | SE | 6/3/16 | 81752 | 88029 | (Light out) | TONY-06/02/2016-REPLACED LAMP AND PC | High Pressure Sodium | 38.84704825000 | -76.98234714000
6/1/16 | 1186784 | 819 | 6TH ST | NW | 6/1/16 | 60541 | 6M706 | (Light out) | Tony A 5-31-16-Replaced 250watt HPS | High Pressure Sodium | 38.90043550000 | -77.01979597000
5/27/16 | 1186598 | 815 | 6TH ST | NW | 6/1/16 | 60542 | 6M707 | (Light out) | Frank Smith at 6/1/2016 3:01:23 AM: 100% replaced 250W HPS bulb two of the 3 street lights in front of 809 6th street are out. 16-00523822-The street light in front of 809 6th street and the street light in front of 813 6th street are out. they have | High Pressure Sodium | 38.90031850000 | -77.01979505000
5/26/16 | 1186353 | 815 | 6TH ST | NW | 6/1/16 | 60542 | 6M707 | (Light out) | Frank Smith at 6/1/2016 1:44:44 AM: 100% done replaced 250 watts HPS bulb ALLEY003 16-00521780-missing globe cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.90031850000 | -77.01979505000
| 1186234 | 1534 | TANNER ST | SE | 6/3/16 | 81769 | 88046 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO Michae | High Pressure Sodium | 38.84740623000 | -76.98158821000
5/25/16 | 1186217 | 1507 | TANNER ST | SE | 6/3/16 | 81774 | 88051 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO | High Pressure Sodium | 38.84738481000 | -76.98202940000
5/25/16 | 1186216 | 1500 | TANNER CT | SE | 6/3/16 | 81772 | 88049 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO | High Pressure Sodium | 38.84759651000 | -76.98189288000
5/25/16 | 1186215 | 1524 | TANNER CT | SE | 6/3/16 | 81771 | 88048 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. | High Pressure Sodium | 38.84771521000 | -76.98170485000
5/25/16 | 1186214 | 1530 | TANNER CT | SE | 6/3/16 | 81770 | 88047 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO | High Pressure Sodium | 38.84763364000 | -76.98153866000
5/25/16 | 1186213 | 1534 | TANNER ST | SE | 6/3/16 | 81769 | 88046 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. ose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO | High Pressure Sodium | 38.84740623000 | -76.98158821000
5/25/16 | 1186212 | 1534 | TANNER ST | SE | 6/3/16 | 81768 | 88045 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO | High Pressure Sodium | 38.84738657000 | -76.98124742000
5/25/16 | 1186211 | 3261 | STANTON RD | SE | 6/3/16 | 81745 | 88022 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO | High Pressure Sodium | 38.84770266000 | -76.98109122000
5/25/16 | 1186210 | 3249 | STANTON RD | SE | 6/1/16 | 81744 | 88021 | (No current) | Duplicate to WO#1186024.. | High Pressure Sodium | 38.84797185000 | -76.98118967000
5/25/16 | 1186209 | 1525 | TUBMAN RD | SE | 6/3/16 | 81743 | 88020 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. | High Pressure Sodium | 38.84806394000 | -76.98142985000
5/25/16 | 1186208 | 1509 | TUBMAN RD | SE | 6/3/16 | 81741 | 88018 | (No current) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO | High Pressure Sodium | 38.84803773000 | -76.98221565000
5/24/16 | 1186150 | 1400 | ROBINSON ST | SE | 5/26/16 | 81739 | 88016 | (Light out) | Michael Hamilton at 5/26/2016 12:59:43 AM: 100% -150w HPS lamp FRONT 16-00519074- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84974214000 | -76.98458609000
5/24/16 | 1186132 | 5019 | F ST | SE | 5/26/16 | 70038 | 7A005 | (Light out) | Michael Hamilton at 5/26/2016 2:42:51 AM: 100% changed 250 watt HPS lightbulb 16-00518464-multiple streetlights out, 3 streetlights out(estimate) please repair asap cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88184129000 | -76.93031372000
5/23/16 | 1186024 | 3249 | STANTON RD | SE | 6/3/16 | 81744 | 88021 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Duplicate to WO#1186024.. Michael Hamilton at 5/24/2016 11:51:02 PM: N/C underground | High Pressure Sodium | 38.84797185000 | -76.98118967000
| 1186010 | 1520 | ALABAMA AVE | SE | 6/3/16 | 81749 | 88026 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Jose Mancia at 5/26/2016 12:31:11 PM: upon arrival have no current on B feeder, refer to PEPCO Michael Hamilton at 5/24/2016 11:56:59 PM: N/C | High Pressure Sodium | 38.84689369000 | -76.98188151000
5/20/16 | 1185881 | 1534 | TANNER ST | SE | 6/3/16 | 81768 | 88045 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO Michae | High Pressure Sodium | 38.84738657000 | -76.98124742000
5/20/16 | 1185875 | 1546 | ALABAMA AVE | SE | 6/3/16 | 81747 | 88024 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Jose Mancia at 5/26/2016 12:33:33 PM: upon arrival have no current on B feeder, refer to PEPCO Michael Hamilton at 5/24/2016 11:55:55 PM: N/C | High Pressure Sodium | 38.84710965000 | -76.98107212000
5/20/16 | 1185873 | 5022 | F ST | SE | 5/25/16 | 70037 | 7A006 | (Light out) | Michael Hamilton at 5/25/2016 1:51:07 AM: 100% -250w HPS lamp 16-00513758-the caller states that the light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88178017000 | -76.93059465000
5/18/16 | 1185616 | 1515 | SHIPPEN LN | SE | 5/19/16 | 81765 | 88042 | (Light out) | Michael Hamilton at 5/19/2016 3:11:13 AM: 100% 250w HPS lamp 16-00509356-caller is reporting streetlight out in front of address listed, caller also requesting brighter light bulbs on the rest of the streetlights. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84917089000 | -76.98166563000
5/17/16 | 1185542 | 1534 | TANNER ST | SE | 6/3/16 | 81769 | 88046 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO Michael | High Pressure Sodium | 38.84740623000 | -76.98158821000
5/17/16 | 1185430 | 1520 | ALABAMA AVE | SE | 6/3/16 | 81749 | 88026 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO Michael | High Pressure Sodium | 38.84689369000 | -76.98188151000
5/17/16 | 1185429 | 1534 | TANNER ST | SE | 6/3/16 | 81769 | 88046 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO Michael | High Pressure Sodium | 38.84740623000 | -76.98158821000
| 1185424 | 3268 | 15TH PL | SE | 6/3/16 | 81752 | 88029 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase. Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO Michael | High Pressure Sodium | 38.84704825000 | -76.98234714000
| 1185412 | 1530 | TANNER CT | SE | 6/3/16 | 81770 | 88047 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO Michael H | High Pressure Sodium | 38.84763364000 | -76.98153866000
| 1184813 | 1534 | TANNER ST | SE | 6/3/16 | 81769 | 88046 | (Light out) | Jose Mancia at 6/2/2016 3:51:45 PM: 100% Pepco ran new feeder to SL Feed. made final splice on Red phase Jose Mancia at 5/26/2016 11:36:18 AM: upon arrival have wires burned up, B fase and neutral wire melted in to the pipe refer to PEPCO Jose Mancia | High Pressure Sodium | 38.84740623000 | -76.98158821000
4/27/16 | 1183737 | 3022 | BLADENSBURG RD | NE | 4/27/16 | 51233DC | 5A129DC | (Light out) | Tony A 4-26-16-replaced 250w HPS lamp | High Pressure Sodium | 38.92821043000 | -76.96163692000
4/24/16 | 1183395 | 5128 | SOUTHERN AVE | SE | 4/28/16 | 75493 | 75493DC | (Light out) | Michael Hamilton at 4/28/2016 10:29:23 PM: 100% 150w HPS lamp 16-00474802- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.87806339000 | -76.92900695000
4/23/16 | 1183376 | 0 | CONNECTICUT AVE | NW | 5/10/16 | 38584 | 3E026 | (Light out) | Juan Escobar at 5/9/2016 10:40:24 AM: 100%. Spliced bad connection in MH Ronald Keith at 4/27/2016 9:13:15 PM: no current there is construction at this location they have a ditch dug for conduit 16-00474 | High Pressure Sodium | 38.94397582000 | -77.06352631000
4/22/16 | 1183304 | 0 | KENILWORTH AVE | SE | 4/22/16 | 79497 | 7A150 | (Light out) | Cristian 4-21-16-Installed 120ft of number 10 cable and 400w HPS lamp | High Pressure Sodium | 38.88456308000 | -76.96344581000
4/20/16 | 1183111 | 2911 | RHODE ISLAND AVE | NE | 5/9/16 | 52505DC | 5A166DC | (Light out) | Cristian Hudisteanu at 5/9/2016 11:44:48 AM: 100% REPLACED 40' CABLE / 400 CUTOFF FIXTURE/ 400w HPS LAMP/ TLPC and made splices. Jose Aguilar at 4/21/2016 2:26:12 AM: no current over head RON K-04/19/2016-400W HPS- NEEDS NEW FIXTURE AND WIRE | High Pressure Sodium | 38.93345368000 | -76.96676649000
4/18/16 | 1182742 | 0 | EAST CAPITOL ST | NE | 4/18/16 | 63629 | 6M837 | (Light out) | Tony A 4-17-16-400w HPS bulb | High Pressure Sodium | 38.88956256000 | -76.97418443000
4/18/16 | 1182724 | 908 | EASTERN AVE | NE | 4/18/16 | 79483 | 7A152 | (Light out) | Tony A 4-17-16-250watt hps bulb and tlpc | High Pressure Sodium | 38.88978699000 | -76.95795735000
4/15/16 | 1182610 | 44 | H ST | NW | 4/15/16 | 60389 | 6A223 | (Light out) | MIKE H-04/14/2106-CLEANED LENS | High Pressure Sodium | 38.90031219000 | -77.01173524000
4/12/16 | 1182436 | 1519 | SHIPPEN LN | SE | 4/14/16 | 81797 | 88074 | (Light out) | Michael Hamilton at 4/14/2016 12:14:48 AM: 100% 250w HPS lamp in front of 1519 shippen lane 16-00456675- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84912604000 | -76.98110955000
| 1182437 | 1417 | TOBIAS DR | SE | 4/14/16 | 81786 | 88063 | (Light out) | Michael Hamilton at 4/14/2016 12:20:41 AM: 100% 250w HPS lamp to the right of 1417 tobias drive 16-00456683-this light will not stay on keeps going out. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85034189000 | -76.98345161000
4/8/16 | 1182038 | 0000 | ROBINSON ST | SE | 4/9/16 | 81755 | 88032 | (Light out) | Michael Hamilton at 4/9/2016 12:38:27 AM: 100% 400w HPS lamp Front 16-00450285-Streetlight burnt out at Lebaum St SE and Mellon St SE cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84999945000 | -76.98436010000
| 1181956 | 3402 | 15TH ST | NE | 4/10/16 | 51213DC | 5A102DC | (Light out) | Jose Aguilar at 4/9/2016 10:11:40 PM: 100% done replaced photocell and 150 watts hps bulb 16-00449546- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93214204000 | -76.98444256000
4/1/16 | 1181291 | 1147 | CONNECTICUT AVE | NW | 4/7/16 | 27220 | 2U544 | (Light out) | Michael Hamilton at 4/6/2016 11:49:40 PM: 100% -400w HPS lamp 16-00442934-On L Street side of property cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90537241000 | -77.04079316000
3/28/16 | 1180824 | 501 | NEW YORK AVE | NE | 4/19/16 | 56842 | 5A430 | (Light out) | Juan Escobar at 4/15/2016 8:24:22 AM: 100% POLE LOCATED INSIDE CONSTRUCTION SITE. BUT A TEMPORARY 400W MH FIXTURE HAS BEEN INSTALLED ON POLE. TEMPORARY LIGHT IS WORKING PROPERLY. Tony A 3-26-16-no current underground | High Pressure Sodium | 38.91132939000 | -76.99721837000
3/23/16 | 1180556 | 1443 | LAWRENCE ST | NE | 3/29/16 | 52488DC | 5A159DC | (Light out) | Michael Hamilton at 3/29/2016 2:57:53 AM: 100% 150w HPS lamp Between 1443 and 1445 Lawrence Street 16-00433970- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93180662000 | -76.98505493000
3/23/16 | 1180307 | 1211 | 7TH ST | NW | 3/24/16 | 25661 | 6A790 | (Light out) | Michael Hamilton at 3/24/2016 1:19:15 AM: 100% -250w HPS lamp | High Pressure Sodium | 38.90712952000 | -77.02201691000
3/23/16 | 1180306 | 1300 | N ST | NW | 4/8/16 | 25599 | 6A792 | (Light out) | Alexander Portales at 4/8/2016 10:35:03 AM: 100% replaced 120' # 10 cable Michael Hamilton at 3/24/2016 12:43:54 AM: N/C underground | High Pressure Sodium | 38.90730081000 | -77.02210992000
3/23/16 | 1180296 | 1301 | 20TH ST | NW | 3/25/16 | 24830 | 2A017 | (Light out) | BCM - PEPCO MADE REPAIRS. 100%...Michael Hamilton at 3/23/2016 11:59:12 PM: N/C underground | High Pressure Sodium | 38.90756285000 | -77.04480461000
3/16/16 | 1179856 | 5524 | SOUTHERN AVE | SE | 3/30/16 | 75510 | 75510DC | (Light out) | : Naji Carson at 3/30/2016 2:36:50 PM: 100% REPLACED 400w HPS fixture | High Pressure Sodium | 38.88359254000 | -76.92141921000
3/16/16 | 1179848 | 5033 | IVORY WALTERS LN | SE | 3/18/16 | 70063 | 7A045 | (Light out) | floyd bailey at 3/18/2016 2:15:44 PM: 100%. changed 250W HPS | High Pressure Sodium | 38.88116944000 | -76.93003787000
3/16/16 | 1179847 | 5027 | IVORY WALTERS LN | SE | 3/18/16 | 70064 | 7A046 | (Light out) | floyd bailey at 3/18/2016 2:21:58 PM: 100%. changed 250W hps | High Pressure Sodium | 38.88124484000 | -76.93027898000
3/16/16 | 1179846 | 5007 | IVORY WALTERS LN | SE | 3/18/16 | 70067 | 7A049 | (Light out) | floyd bailey at 3/18/2016 2:26:07 PM: 100%. changed 250W hps | High Pressure Sodium | 38.88135413000 | -76.93103891000
3/16/16 | 1179844 | 4479 | F ST | SE | 3/18/16 | 75749 | 75749DC | (Light out) | floyd bailey at 3/18/2016 12:47:13 PM: 100%. replaced 250W HPS & TLPC | High Pressure Sodium | 38.88184868000 | -76.93731162000
3/16/16 | 1179841 | 5000 | F ST | SE | 4/5/16 | 70043 | 7A033 | (Light out) | Jose Mancia at 4/5/2016 11:33:27 AM: 100% REPLACED 250w HPS conversion kit Michael Hamilton at 3/22/2016 12:11:10 AM: N/C underground | High Pressure Sodium | 38.88170872000 | -76.92934821000
3/16/16 | 1179840 | 5000 | F ST | SE | 3/17/16 | 70042 | 7A001 | (Light out) | Jose Mancia at 3/17/2016 3:29:14 PM: 100% REPLACED 118 GLOBE and 250w HPS lamp | High Pressure Sodium | 38.88163766000 | -76.92955610000
3/16/16 | 1179836 | 5412 | E ST | SE | 3/29/16 | 75501 | 75501DC | (Light out) | Jose Mancia at 3/29/2016 10:37:15 AM: 100% REPAIRED BREAK IN OVERHEAD WIRED. floyd bailey at 3/18/2016 11:33:34 AM: no current, low voltage | High Pressure Sodium | 38.88126024000 | -76.92504376000
3/8/16 | 1178990 | 1301 | 20TH ST | NW | 3/25/16 | 24830 | 2A017 | (Light out) | Alexander Portales at 3/15/2016 8:36:34 AM: REFER TO PEPCO NO POWER IN MANHOLE AND FEED HAS NO PIG TAILS. : Michael Hamilton at 3/10/2016 12:05:03 AM: N/C underground 16-00419701-in the middle of the block cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90756285000 | -77.04480461000
3/7/16 | 1178887 | 1423 | ROBINSON ST | SE | 3/8/16 | 81736 | 88013 | (Light out) | Michael Hamilton at 3/8/2016 12:43:06 AM: 100% -150w HPS lamp 16-00418102-This is my second attempt to notify DC government to repair the light in the alley that has been out for month. It's a safety matter which the residents feel not safe to walk a | High Pressure Sodium | 38.84912960000 | -76.98365616000
2/22/16 | 1177585 | 1517 | 17TH ST | NW | 2/22/16 | 26707 | 2M071 | (Light out) | CRISTIAN REPLACED 400W POWER DOOR, 400W BULB AND PHOTOCELL | High Pressure Sodium | 38.91030935000 | -77.03857764000
2/22/16 | 1177582 | 1517 | 17TH ST | NW | 2/22/16 | 26707 | 2M071 | (Light off/on) | CRISTIAN REPLACED 400W BULB | High Pressure Sodium | 38.91030935000 | -77.03857764000
2/22/16 | 1177516 | 0 | WISCONSIN AVE | NW | 2/26/16 | 30134 | 3G003 | (Light out) | Ronald Keith at 2/26/2016 12:09:11 PM: 100% replaced t base door See west side of Wisconsin Avenue NW south of Mass. Ave NW by Alban Towers, mid block | High Pressure Sodium | 38.92806668000 | -77.07330376000
2/22/16 | 1177434 | 0 | H ST | NE | 2/23/16 | 68250DC | 68520 | (Light out) | Jose Mancia at 2/22/2016 10:58:51 PM:100% Replaced 400w HPS lamp | High Pressure Sodium | 38.87458286000 | -77.00571187000
2/20/16 | 1177393 | 1900 | 37TH ST | NW | 2/22/16 | 36891 | 30482 | (Light off/on) | Julio Canales at 2/22/2016 8:20:41 PM: 100% replaced a 150w HPS lamp | High Pressure Sodium | 38.91672906000 | -77.07292654000
2/17/16 | 1177113 | 100 | 3RD ST | SE | 2/17/16 | 6A002 | 6A002 | (Light out) | TONY A-02/16/16-REPLACED LAMP | Incandescent | 38.87703665000 | -77.00445216000
2/17/16 | 1176953 | 0000 | OVERLOOK AVE | SW | 2/17/16 | 81836 | 88097 | (Light out) | Christian. 02/12/2016. Replaced 250 watt lamp and 250 watt ballast. 100%. | High Pressure Sodium | 38.83334467000 | -77.01372200000
2/17/16 | 1176950 | 0 | ANACOSTIA FWY | SE | 2/17/16 | 79469 | 7A133 | (Light out) | Christian. 02/12/2016. Replaced 400 watt lamp and 400 watt power door. 100%. | High Pressure Sodium | 38.88182711000 | -76.96446211000
2/17/16 | 1176949 | 0 | ANACOSTIA FWY | NE | 2/17/16 | 79490 | 7A159 | (Light out) | Christian. 02/12/2016. Replaced 400 watt lamp. 100%. | High Pressure Sodium | 38.88986353000 | -76.95869496000
2/11/16 | 1176680 | 0401 | 51ST ST | SE | 2/11/16 | 70047 | 7A030 | (Light out) | Naji Carson at 2/11/2016 10:27:22 PM: 100% Issue resolved 16-00396517-rear please repair three alleylight that are out cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.88219594000 | -76.92932412000
2/8/16 | 1176374 | 331 | 1ST ST | NW | 2/8/16 | 60984 | 68291 | (Light out) | Naji Carson 2-8-16-250w HPS lamp | High Pressure Sodium | 38.89378061000 | -77.01208981000
2/6/16 | 1176245 | 0 | ANACOSTIA FWY | SE | 2/6/16 | 79468 | 7A132 | (Light out) | CHRISTIAN-02/05/16-replaced lamp | High Pressure Sodium | 38.88252291000 | -76.96415772000
2/1/16 | 1175745 | 0000 | SUITLAND PKY | SE | 2/10/16 | 83281 | 82381 | (Light out) | Jose Aguilar at 2/10/2016 4:11:15 PM: 100% upon investigation I found the hot wire was burned up in the manhole . I made new connections Cristian H 1/30/2016 no current on poles 83281,83282,83283,83284, temp | High Pressure Sodium | 38.86351812000 | -77.00055997000
2/1/16 | 1175705 | 0 | KENILWORTH AVE | SE | 2/10/16 | 79492 | 7A161 | (Light out) | ose Aguilar at 2/10/2016 4:13:26 PM: 100% found bad spot on the hot wire . cut the bad spot and made new splices CHRISTIAN NO CURRENT | High Pressure Sodium | 38.88905101000 | -76.96038452000
2/1/16 | 1175704 | 0 | KENILWORTH AVE | NE | 2/1/16 | 79462 | 7A126 | (Light out) | CHRISTIAN REPLACED 400 WATT HPS BULB | High Pressure Sodium | 38.89001850000 | -76.95803705000
2/1/16 | 1175690 | 0000 | OVERLOOK AVE | SW | 2/1/16 | 81834 | 88095 | (Light out) | CHRISTIAN - 01/29/2016 - REPLACED LAMP | High Pressure Sodium | 38.83393831000 | -77.01328820000
2/1/16 | 1175689 | 0000 | OVERLOOK AVE | SE | 2/1/16 | 81810 | 88084 | (Light out) | CHRISTIAN - 01/29/2016 - REPLACED LAMP | High Pressure Sodium | 38.83021266000 | -77.01638931000
2/1/16 | 1175679 | 0 | OVERLOOK AVE | SE | 2/1/16 | 81813 | 88087 | (Light out) | CHRISTIAN - 01/29/2016 - REPLACED LAMP | High Pressure Sodium | 38.83101830000 | -77.01553587000
2/1/16 | 1175667 | 809 | INTERSTATE 295 | NE | 2/12/16 | 79474 | 7A138 | (Light out) | Jose Aguilar at 2/12/2016 4:21:36 PM: 100% installed arm , fixture and 50' of #10 wire Jose Aguilar at 2/11/2016 11:29:08 AM: aRM AND FIXTURE FELL 295 NORTH BOUND CLOSE TO EAST CAPITALCHRISTIAN NO CURRENT | High Pressure Sodium | 38.88176234000 | -76.96414383000
| 1175348 | 0 | 9TH ST | NE | 1/28/16 | 52560 | 5M022 | (Light out) | Naji Carson at 1/28/2016 3:45:57 AM: 100% replaced 100W HPS lamp and TLPC front of address 16-00369821- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91125364000 | -76.99254153000
1/8/16 | 1174303 | 815 | 6TH ST | NW | 1/8/16 | 60542 | 6M707 | (Light out) | Cristian 1-7-2016-replaced photocell and 250w lamp | High Pressure Sodium | 38.90031850000 | -77.01979505000
1/7/16 | 1174195 | 819 | 6TH ST | NW | 1/8/16 | 60541 | 6M706 | (Light out) | Jose Mancia at 1/7/2016 11:27:06 PM: 100% replaced 250W HPS lamp and night watchman photocell Street side 16-00355216-Streetlight Repair Investigation Light out, Chinatown fixture near 817 6th St NW Additional details and/or comments at http://s | High Pressure Sodium | 38.90043550000 | -77.01979597000
12/18/15 | 1172924 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79481 | 7A145 | (No current) | Brian Maynard at 1/6/2016 12:36:40 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88647157000 | -76.96221690000
12/18/15 | 1172923 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79480 | 7A144 | (No current) | Brian Maynard at 1/6/2016 12:36:18 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88580800000 | -76.96248765000
12/18/15 | 1172922 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79479 | 7A143 | (No current) | Brian Maynard at 1/6/2016 12:36:25 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88513632000 | -76.96276237000
12/18/15 | 1172920 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79478 | 7A142 | (No current) | Brian Maynard at 1/6/2016 12:37:03 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88446501000 | -76.96303530000
12/18/15 | 1172919 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79477 | 7A141 | (No current) | Brian Maynard at 1/6/2016 12:36:47 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88375073000 | -76.96332098000
12/18/15 | 1172918 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79476 | 7A140 | (No current) | Brian Maynard at 1/6/2016 12:36:33 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88303360000 | -76.96361101000
12/18/15 | 1172916 | 809 | EASTERN AVE | NE | 1/6/16 | 79475 | 7A139 | (No current) | Brian Maynard at 1/6/2016 12:35:14 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88244563000 | -76.96384495000
12/18/15 | 1172915 | 809 | INTERSTATE 295 | NE | 1/6/16 | 79474 | 7A138 | (No current) | Brian Maynard at 1/6/2016 12:34:52 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88176234000 | -76.96414383000
12/18/15 | 1172914 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79473 | 7A137 | (No current) | Brian Maynard at 1/6/2016 12:36:55 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88109425000 | -76.96448919000
12/18/15 | 1172913 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79472 | 7A136 | (No current) | Brian Maynard at 1/6/2016 12:36:11 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88045569000 | -76.96488247000
12/18/15 | 1172911 | 803 | EASTERN AVE | NE | 1/6/16 | 79471 | 7A135 | (No current) | Brian Maynard at 1/6/2016 12:34:45 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88055222000 | -76.96517808000
12/18/15 | 1172910 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79470 | 7A134 | (No current) | Brian Maynard at 1/6/2016 12:35:22 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88120301000 | -76.96478109000
12/18/15 | 1172909 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79469 | 7A133 | (No current) | Brian Maynard at 1/6/2016 12:35:45 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88182711000 | -76.96446211000
12/18/15 | 1172907 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79468 | 7A132 | (No current) | Brian Maynard at 1/6/2016 12:35:52 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88252291000 | -76.96415772000
12/18/15 | 1172906 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79467 | 7A131 | (No current) | Brian Maynard at 1/6/2016 12:35:30 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88310417000 | -76.96392124000
12/18/15 | 1172904 | 0 | ANACOSTIA FWY | SE | 1/12/16 | 79466 | 7A130 | (No current) | Jose Aguilar at 1/12/2016 3:57:25 PM: >>>>>100%<<<<< found the bad spot on the wire and made the proper repair and now the lights are back on pOLE # 'S 79466-79481 AND 79494-79497 NO CURRENT with cut | High Pressure Sodium | 38.88384591000 | -76.96362320000
12/18/15 | 1172903 | 0 | KENILWORTH AVE | SE | 1/6/16 | 79497 | 7A150 | (No current) | Brian Maynard at 1/6/2016 12:34:33 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88456308000 | -76.96344581000
12/18/15 | 1172901 | 0 | KENILWORTH AVE | SE | 1/6/16 | 79496 | 7A149 | (No current) | Brian Maynard at 1/6/2016 12:35:00 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88522570000 | -76.96311007000
12/18/15 | 1172900 | 0 | KENILWORTH AVE | SE | 1/6/16 | 79495 | 7A148 | (No current) | Brian Maynard at 1/6/2016 12:35:07 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88589091000 | -76.96283495000
12/18/15 | 1172898 | 0 | ANACOSTIA FWY | SE | 1/6/16 | 79494 | 7A147 | (No current) | Brian Maynard at 1/6/2016 12:35:37 PM: 100% DUPLICATE TO WO# 1172904 | High Pressure Sodium | 38.88656390000 | -76.96255943000
12/18/15 | 1172885 | 0 | CHILLUM PL | NE | 12/21/15 | 4P513DC | 4U169 | (Light out) | Naji Carson at 12/21/2015 12:45:36 AM: 100% Replaced 400w HPS lamp. | High Pressure Sodium | 38.95927698000 | -77.00253696000
12/17/15 | 1172817 | 1516 | TUBMAN RD | SE | 12/17/15 | 81723 | 88000 | (Light off/on) | NAJI CARSON-12/16/15-100% REPLACED LAMP | High Pressure Sodium | 38.84867470000 | -76.98179245000
12/17/15 | 1172816 | 1516 | TUBMAN RD | SE | 12/17/15 | 81723 | 88000 | (Light off/on) | NAJI CARSON-12/16/15-100% REPLACED LAMP | High Pressure Sodium | 38.84867470000 | -76.98179245000
| 1172510 | 3233 | STANTON RD | SE | 12/16/15 | 81724 | 88001 | (Light out) | Alexander Portales at 12/16/2015 10:00:36 PM: 100% Replaced 150w lamp and TLPC ALLEY003 15-00337891- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84869935000 | -76.98144585000
12/14/15 | 1172388 | 0 | ANACOSTIA FWY | SE | 12/14/15 | 79464 | 7A128 | (Light off/on) | Naji Carson-replaced 400hps lamp | High Pressure Sodium | 38.88945734000 | -76.95919436000
| 1172359 | 3402 | 15TH ST | NE | 12/15/15 | 51213DC | 5A102DC | (Light out) | Jose Malpartida at 12/15/2015 7:54:43 PM: 100 % done replaced 150 w bulb HPS front 15-00336986- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93214204000 | -76.98444256000
12/11/15 | 1172187 | 2800 | BLADENSBURG RD | NE | 12/14/15 | 50092 | 5A078 | (Light out) | Alexander Portales at 12/14/2015 4:14:36 AM: 100% Replaced 250w HPS lamp and TLPC. 15-00336102- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92548918000 | -76.96461140000
12/8/15 | 1171886 | 0000 | MILITARY RD | NW | 12/15/15 | 4A001 | 4R210 | (Light out) | Charles Mcdermott at 12/15/2015 2:27:37 PM: 100%-- RESPLICED BROKEN FEED @ MH Alexander Portales at 12/11/2015 2:31:16 AM: NO CURRENT UNDERGROUND. Correct pole #4A001. Cristian Hudisteanu at 12/8/2015 11:47:15 PM: we have not pole number for this | High Pressure Sodium | 38.94895547000 | -77.02961274000
| 1171672 | 1240 | UPSHUR ST | NW | 12/15/15 | 4R783 | 4R791 | (Light out) | Charles Mcdermott at 12/15/2015 12:51:41 PM: 100%-- CLEARED SHORT TO NEUTRAL / REPLACED 250w HPS FIXTURE Ismael Hernandez at 12/7/2015 12:29:58 AM: LOW VOLTAGE DAY CREW REQUIRED 94 volts 4-783 15-00330405-1240B upshur st nw...burned out light acros | High Pressure Sodium | 38.94192475000 | -77.02807960000
12/1/15 | 1171391 | 4608 | EASY PL | SE | 12/5/15 | 75826 | 75826DC | (Light out) | Dan. 12/04/2015. 10:10pm. Replaced T/L photocell and fixture. 100%. Ismael Hernandez at 12/3/2015 3:31:23 AM: NO POLE TAG CANT FIND CORRECT LOCATION BECAUSE THERE IS NO POLE TAG Clarence 11-30-2015-repalced twist lock | Incandescent | 38.87603875000 | -76.93343049000
| 1171350 | 0000 | MONTANA AVE | NE | 12/5/15 | 50075 | 5A060 | (Light out) | Alexander Portales at 12/5/2015 4:39:37 AM: 100% replaced 400W HPS LAMP 15-00326949-Streetlight Repair Investigation The light in the Montana Ave Circle from Montana Ave towards New York Ave is out. This pole also has a yield sign on it. No pole n | High Pressure Sodium | 38.91680835000 | -76.97824997000
11/30/15 | 1171341 | 1350 | CONNECTICUT AVE | NW | 12/2/15 | 24527 | 2U491 | (Light out) | Ismael Hernandez at 12/1/2015 11:40:18 PM: 100% changed 70 hps lamp & tlpc 15-00326812-Alleylight Repair Investigation In alley between 1500 block of S and 1500 block is Swann - light goes on and off all night - thanks! Additional details and/or | High Pressure Sodium | 38.90838138000 | -77.04291014000
11/25/15 | 1171126 | 0 | NEW YORK AVE | NE | 12/3/15 | 56832 | 5M053 | (Light out) | BCM - POLE DOES NOT EXIST ANYMORE...NEW T-20 POLES ARE AT THIS LOCATION..Alexander Portales at 12/3/2015 12:48:01 AM: Bad Address | High Pressure Sodium | 38.91324438000 | -76.99169504000
11/25/15 | 1171116 | 0000 | BLADENSBURG RD | NE | 12/2/15 | 51242DC | 5A138DC | (Light out) | Dan Artenie 12/1/2015 (D)5:25 pm (A)5:35 pm (C)5:45 pm 100% light is working properly. Replaced 1 250 w hps bulb. | High Pressure Sodium | 38.92577932000 | -76.96462091000
11/25/15 | 1171115 | 0000 | BLADENSBURG RD | NE | 12/2/15 | 51242DC | 5A138DC | (Light out) | Dan Artenie 12/1/2015 (D)5:25 pm (A)5:35 pm (C)5:45 pm 100% same pole as wo#1171116 | High Pressure Sodium | 38.92577932000 | -76.96462091000
11/24/15 | 1171038 | 1225 | 18TH ST | NW | 11/24/15 | 26763 | 2U514 | (Light out) |  | High Pressure Sodium | 38.90700407000 | -77.04161752000
11/24/15 | 1171037 | 1225 | 18TH ST | NW | 11/25/15 | 26763 | 2U514 | (Light out) | Ismael Hernandez at 11/24/2015 11:33:02 PM: 100% changed IGN/CAPACITOR COMBO ,400w hps lamp ,TLPC | High Pressure Sodium | 38.90700407000 | -77.04161752000
11/24/15 | 1171036 | 1225 | 18TH ST | NW | 11/25/15 | 26763 | 2U514 | (Light out) | Ismael Hernandez at 11/24/2015 8:40:27 PM: 100% Replaced 400w HPS lamp | High Pressure Sodium | 38.90700407000 | -77.04161752000
| 1170763 | 2450 | 37TH ST | NW | 11/24/15 | 36869 | 3G057 | (Light out) | Alexander Portales at 11/24/2015 1:16:30 AM: 100% REPLACED 200W INC Lamp 15-00320803-Streetlight Repair Investigation streetlight burnt out in alley behind (to south of) 2037 huidekoper place nw Additional details and/or comments at http://seec | High Pressure Sodium | 38.92247432000 | -77.07310675000
11/19/15 | 1170710 | 0 | P ST | NW | 11/20/15 | 25805 | 6A807 | (Light out) | Pedro Cruz at 11/20/2015 7:31:39 PM: 100% replaced 400W hps lamp, T/L photocell. | High Pressure Sodium | 38.90960205000 | -77.02177585000
11/18/15 | 1170647 | 2800 | BLADENSBURG RD | NE | 11/24/15 | 50092 | 5A078 | (Light out) | Ismael Hernandez at 11/23/2015 11:15:07 PM: 100% changed 400w hps lamp& tlpc ALLEY003 15-00319690-Alleylight Repair Investigation Alley light out. Additional details and/or comments at http://seeclickfix.com/issues/2036612. cwDesc: ALLEYLIGHT RE | High Pressure Sodium | 38.92548918000 | -76.96461140000
| 1170355 | 236 | RHODE ISLAND AVE | NW | 11/23/15 | 59993 | 5A185 | (Light out) | Jose Aguilar at 11/23/2015 6:27:28 PM: 100% this light was on when we arrived but we replaced the 400W HPS lamp On the southeast corner of 3rd and Rhode Island Ave NW. Pole number 59993 15-00317107-Street light is out...PREVIOUS SR CLOSED AND LIGHT IS | High Pressure Sodium | 38.91439745000 | -77.01561600000
11/12/15 | 1170056 | 236 | RHODE ISLAND AVE | NW | 11/14/15 | 59993 | 5A185 | (Light out) | Charles Mcdermott at 11/14/2015 2:45:25 AM: 100%-- REPLACED 400w HPS LAMP On the southeast corner of 3rd and Rhode Island Ave NW. Pole number 59993 15-00314050-Street light is out. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91439745000 | -77.01561600000
11/10/15 | 1169975 | 0 | 11TH ST | NW | 11/19/15 | 23373 | 2L038 | (Light out) | Ismael Hernandez at 11/19/2015 3:06:28 AM: 100% changed 400w hps lamp front 15-00313429- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90224189000 | -77.02690683000
11/9/15 | 1169885 | 0000 | LAWRENCE ST | NE | 11/15/15 | 52490DC | 5A161DC | (Light out) | Ismael Hernandez at 11/15/2015 1:04:48 AM: 100% changed 150W HPS lamp, TLPC | High Pressure Sodium | 38.93183623000 | -76.98442682000
| 1169843 | 0 | BROAD BRANCH TER | NW | 11/20/15 | 34711DC | 34730DC | (Light out) | Naji Carson at 11/20/2015 9:25:07 AM: 100% Installed 120FT OF #6 wire. Lights working properly in alley. Jose Aguilar at 11/11/2015 11:05:07 PM: no power overhead feed the entire alley is out pole numbers are 34726DC 34727DC , 34728DC 34729DC AND 347 | High Pressure Sodium | 38.95576043000 | -77.06567453000
11/3/15 | 1169406 | 1616 | 18TH ST | NW | 11/5/15 | 26775 | 2M138 | (Light out) | Clarence Wilkerson at 11/5/2015 4:10:47 AM: 100% 400W HPS LAMP front 15-00308189-about 4 lights out on the block cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91224399000 | -77.04173823000
| 1169104 | 1400 | SHIPPEN LN | SE | 11/2/15 | 81733 | 88010 | (Light out) | floyd bailey at 11/1/2015 11:14:28 PM: 100% changed 150w HPS lamp & tlpc 15-00304848-ALLEY LIGHT OUT cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84898543000 | -76.98275634000
10/21/15 | 1168229 | 0000 | H ST | NE | 10/26/15 | 68260DC | 68260 | (Light out) | FLOYD BAILEY-10/20/15-100% | High Pressure Sodium | 38.90032135000 | -77.00885912000
10/16/15 | 1167916 | 777 | NORTH CAPITOL ST | NE | 10/20/15 | 68241DC | 68241 | (Light out) | floyd bailey at 10/20/2015 3:29:37 AM: 100% upon arrival changed 400w hps lamp and TLPC On the conner of North capital & H Street NE 15-00294089- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90010486000 | -77.00885876000
10/14/15 | 1167624 | 0 | KENILWORTH AVE | SE | 10/14/15 | 79492 | 7A161 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88905101000 | -76.96038452000
10/14/15 | 1167623 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79491 | 7A160 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88928656000 | -76.95990942000
10/14/15 | 1167622 | 0 | ANACOSTIA FWY | NE | 10/14/15 | 79490 | 7A159 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88986353000 | -76.95869496000
10/14/15 | 1167621 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79465 | 7A129 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88861563000 | -76.96080132000
10/14/15 | 1167620 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79464 | 7A128 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88945734000 | -76.95919436000
10/14/15 | 1167619 | 0 | KENILWORTH AVE | NE | 10/14/15 | 79463 | 7A127 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88994563000 | -76.95813630000
10/14/15 | 1167618 | 0 | KENILWORTH AVE | NE | 10/14/15 | 79462 | 7A126 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.89001850000 | -76.95803705000
10/14/15 | 1167617 | 0 | KENILWORTH AVE | NE | 10/14/15 | 79461 | 7A125 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.89037514000 | -76.95748332000
10/14/15 | 1167612 | 908 | EASTERN AVE | NE | 10/14/15 | 79483 | 7A152 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88978699000 | -76.95795735000
10/14/15 | 1167611 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79482 | 7A151 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88927741000 | -76.95876088000
10/14/15 | 1167598 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79481 | 7A145 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88647157000 | -76.96221690000
10/14/15 | 1167597 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79480 | 7A144 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88580800000 | -76.96248765000
10/14/15 | 1167596 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79479 | 7A143 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88513632000 | -76.96276237000
10/14/15 | 1167594 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79478 | 7A142 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88446501000 | -76.96303530000
10/14/15 | 1167593 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79477 | 7A141 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88375073000 | -76.96332098000
10/14/15 | 1167592 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79476 | 7A140 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88303360000 | -76.96361101000
10/14/15 | 1167591 | 809 | EASTERN AVE | NE | 10/14/15 | 79475 | 7A139 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88244563000 | -76.96384495000
10/14/15 | 1167590 | 809 | INTERSTATE 295 | NE | 10/14/15 | 79474 | 7A138 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88176234000 | -76.96414383000
10/14/15 | 1167589 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79473 | 7A137 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88109425000 | -76.96448919000
10/14/15 | 1167588 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79472 | 7A136 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88045569000 | -76.96488247000
10/14/15 | 1167587 | 803 | EASTERN AVE | NE | 10/14/15 | 79471 | 7A135 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88055222000 | -76.96517808000
10/14/15 | 1167586 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79470 | 7A134 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88120301000 | -76.96478109000
10/14/15 | 1167584 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79469 | 7A133 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88182711000 | -76.96446211000
10/14/15 | 1167583 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79468 | 7A132 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88252291000 | -76.96415772000
10/14/15 | 1167582 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79467 | 7A131 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88310417000 | -76.96392124000
10/14/15 | 1167581 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79466 | 7A130 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88384591000 | -76.96362320000
10/14/15 | 1167580 | 0 | KENILWORTH AVE | SE | 10/14/15 | 79497 | 7A150 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88456308000 | -76.96344581000
10/14/15 | 1167579 | 0 | KENILWORTH AVE | SE | 10/14/15 | 79496 | 7A149 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88522570000 | -76.96311007000
10/14/15 | 1167578 | 0 | KENILWORTH AVE | SE | 10/14/15 | 79495 | 7A148 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88589091000 | -76.96283495000
10/14/15 | 1167577 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79494 | 7A147 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88656390000 | -76.96255943000
10/14/15 | 1167576 | 0 | ANACOSTIA FWY | SE | 10/14/15 | 79493 | 7A146 | (Light out) | BCM - PEPCO MADE REPAIRS ON 10-13-2015 100%. BCM 10-6-2015: 40+ Lights Out on I295 and East Capitol Ramps to I295 | High Pressure Sodium | 38.88732787000 | -76.96219078000
10/14/15 | 1167546 | 1111 | 14TH ST | NW | 10/14/15 | 27350 | 2M423 | (Light out) | Tony A-10-12-2015-400w hps lamp, 400w hps lamp and t/l photocell | High Pressure Sodium | 38.90469050000 | -77.03208800000
10/5/15 | 1166716 | 1134 | 11TH ST | NW | 10/5/15 | 25277 | 2M260 | (Light out) | Jose Aguilar at 10/5/2015 11:18:03 PM: 100% replaced 100W HPS lamp and TL photocell 15-00282721-Streetlight Repair Investigation Light #25878is out Additional details and/or comments at http://seeclickfix.com/issues/1955609. cwDesc: STREETLIGHT | High Pressure Sodium | 38.90554744000 | -77.02715436000
| 1166705 | 3258 | 15TH PL | SE | 10/6/15 | 81753 | 88030 | (Light out) | Alexander Portales at 10/6/2015 1:15:26 AM: 100% All Alley light work Properly ALLEY003 15-00282668-All of the lights are out in this alley please repair. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84756122000 | -76.98229152000
9/29/15 | 1166265 | 5524 | SOUTHERN AVE | SE | 9/29/15 | 75510 | 75510DC | (Light out) | JOSE M-09/28/2015-REPLACED LAMP | High Pressure Sodium | 38.88359254000 | -76.92141921000
9/25/15 | 1166072 | 0400 | TAYLOR ST | NE | 9/25/15 | 50086 | 5A067 | (Light out) | ISMAEL H- 09/23/15- REPLACED LAMP AND PC | High Pressure Sodium | 38.94068754000 | -77.00205144000
9/25/15 | 1166071 | 0 | NEW YORK AVE | NE | 9/25/15 | 50012 | 5A046 | (Light out) | ISMAEL H- 09/23/15- REPLACED LAMP | High Pressure Sodium | 38.91703724000 | -76.96344782000
9/25/15 | 1166070 | 0 | NEW YORK AVE | NE | 9/25/15 | 50008 | 5A042 | (Light out) | ISMAEL H- 09/23/15- REPLACED LAMP AND PC | High Pressure Sodium | 38.91724347000 | -76.96648514000
9/23/15 | 1165862 | 4604 | IOWA AVE | NW | 9/23/15 | 4K465DC | 4U133 | (Light out) | Michael Hampton. 09/18/2015. 100%. Installed 250 watt HPS lamp. | High Pressure Sodium | 38.94554728000 | -77.02962114000
9/17/15 | 1165500 | 0 | KENNEDY ST | NW | 9/20/15 | 4M070 | 4M070DC | (Light out) | Michael Hamilton at 9/20/2015 12:54:48 AM: 100% -250w HPS lamp -T/L -starter | High Pressure Sodium | 38.95645469000 | -77.02220865000
9/17/15 | 1165499 | 929 | KENNEDY ST | NW | 9/20/15 | 4M084 | 4M084DC | (Light out) | Michael Hamilton at 9/20/2015 12:28:25 AM: 100% replaced 250W HPS lamp, 200-400W hps starter, T/L photocell & capacitor. | High Pressure Sodium | 38.95631296000 | -77.02698538000
9/16/15 | 1165267 | 0 | RICHARDSON PL | NW | 9/22/15 | 59924 | 5A412 | (Light out) | Michael Hamilton at 9/22/2015 1:30:46 AM: 100% replaced 150W hps lamp FRONT003 15-00264976-Alleylight Repair Investigation Street light was observed being removed by construction workers at 410 Richardson place NW. Pole appears to have been discar | High Pressure Sodium | 38.91306930000 | -77.01662788000
9/11/15 | 1164924 | 0 | EAST CAPITOL ST | NE | 9/15/15 | 63629 | 6M837 | (Light out) | JUAN ESCOBAR 9/15/2015 POLE# 63629 "100%" REPLACED 400W HPS LAMP. | High Pressure Sodium | 38.88956256000 | -76.97418443000
9/11/15 | 1164871 | 0 | NEW YORK AVE | NE | 9/24/15 | 50004 | 5A038 | (Light out) | Michael Hamilton at 9/24/2015 1:20:02 AM: 100% -400w hps lamp -T/L Michael Hamilton at 9/20/2015 4:26:13 AM: need crash truck 3 Lights out in the Center Island on New York Ave between Bladensburg Road and the Washington Times building. | High Pressure Sodium | 38.91736785000 | -76.96929432000
| 1163847 | 236 | RHODE ISLAND AVE | NW | 8/28/15 | 59993 | 5A185 | (Light out) | Alexander Portales at 8/28/2015 12:31:11 AM: 100% 150W HPS LAMP AND T/L ALLEY003 15-00236836- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.91439745000 | -77.01561600000
| 1163834 | 0 | VERMONT AVE | NW | 8/28/15 | 25343 | 27068 | (Light out) | Alexander Portales at 8/27/2015 11:33:18 PM: 100% 400W HPS LAMP 15-00236479-Streetlight Repair Investigation Light has been out for a while now. Top globe has '40' on it. Additional details and/or comments at http://seeclickfix.com/issues/1861741. | High Pressure Sodium | 38.90628334000 | -77.03176584000
| 1163750 | 200 | RIGGS RD | NW | 8/25/15 | 4A002 | 4J683 | (Light out) | Michael Hamilton at 8/25/2015 12:01:06 AM: 100% replaced 400W hps power door, 400w hps lamp& T/l photocell. 15-00233335-The streetlight side by side on the opposite side of this address closest to the metro station cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93966490000 | -77.03282752000
| 1163446 | 0 | BUCHANAN ST | NW | 8/26/15 | 4K034 | 4U127 | (Light out) | 100% I was able to connect the feed to another manhole closer to the light there were 2 lights affected by this issue Michael Hamilton at 8/19/2015 12:54:43 AM: No current underground. front 15-00225810- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94618430000 | -77.02981335000
8/4/15 | 1161499 | 3033 | BLADENSBURG RD | NE | 8/4/15 | 58720DC | 5A172DC | (Light out) | Jose Mancia at 8/4/2015 9:59:30 PM: 100% replaced 200W incandescent bulb 15-00205229-Alleylight burnt out. cwDesc: ALLEYLIGHT REPAIR | Incandescent | 38.92960546000 | -76.95868010000
7/28/15 | 1160883 | 0 | CARROLL ST | NW | 7/28/15 | 4H569DC | 4H569 | (Light out) | Jose Rodriguez. 06/12. 12:46am. 100% Installed 250 watt HPS lamp. | High Pressure Sodium | 38.97497351000 | -77.01515190000
7/27/15 | 1160754 | 3222 | 14TH ST | NE | 7/31/15 | 51220DC | 5A114DC | (Light out) | Michael Hamilton at 7/31/2015 3:38:11 AM: 100% Replaced 300w incandescent lamp. 15-00189230-THE STREETLIGHT IS OUT AT THIS LOCATION cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93068379000 | -76.98625793000
7/14/15 | 1160067 | 0000 | ROBINSON ST | SE | 7/19/15 | 81756 | 88033 | (Light out) | Jose Mancia at 7/18/2015 11:18:01 PM: 100% complete replaced 250 hps lamp 15-00178694-This light was suppose had been fix last week and then 2wks before that and it is still out. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84997435000 | -76.98416955000
| 1159888 | 0 | SEDGWICK ST | NW | 7/10/15 | 30008DC | 3A368DC | (Light out) | Jose Rodriguez at 7/10/2015 3:12:01 AM: 100%. Replaced 300w inc lamp 15-00174773- cwDesc: STREETLIGHT REPAIR | Incandescent | 38.94040143000 | -77.09254074000
| 1159847 | 5019 | IVORY WALTERS LN | SE | 7/14/15 | 70065 | 7A047 | (Light out) | Jose Mancia at 7/13/2015 11:34:54 PM: 100% replaced 250W HPS Lamp 15-00173810-2 lights out.. 1 on each side of the street cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88118082000 | -76.93060620000
7/7/15 | 1159699 | 1110 | H ST | NE | 7/8/15 | 62335 | 6S172 | (Light out) | Timothy Brooke at 7/8/2015 2:15:09 AM: 100% complete replaced 400 hps powerdoor | High Pressure Sodium | 38.90029780000 | -76.99103957000
7/6/15 | 1159649 | 0 | ANACOSTIA FWY | SE | 7/14/15 | 79491 | 7A160 | (Light out) | Jose Aguilar at 7/7/2015 9:52:40 AM: 100% Installed light fixture, 250w power door, 250w lamp, and twist lock photocell. NEED 400W HPS FIXTURE, LAMP , AND PC. TONY REMOVED FIXTURE | High Pressure Sodium | 38.88928656000 | -76.95990942000
7/5/15 | 1159584 | 1418 | SHIPPEN LN | SE | 7/9/15 | 81758 | 88035 | (Light out) | Timothy Brooke at 7/9/2015 1:40:34 AM: 100% replaced 250w hps lamp 15-00169735-lot of vandalism in this area by teens. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84969312000 | -76.98374846000
7/5/15 | 1159583 | 1400 | SHIPPEN LN | SE | 7/9/15 | 81762 | 88039 | (Light out) | Timothy Brooke at 7/9/2015 1:19:37 AM: 100% 250w hps lamp replaced Timothy Brooke at 7/9/2015 1:15:10 AM: 100% 250w hps lamp replaced 15-00169732-This light was just fixed about 2wks ago. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84933747000 | -76.98284884000
7/1/15 | 1159478 | 0 | 12TH ST EXPY | SW | 7/3/15 | 28751 | 68647 | (Light out) | Jose Rodriguez at 7/3/2015 2:13:12 AM: 100%. Replaced 400w HPS lamp 15-00167927-Streetlight Repair Investigation 1722 5th St NW, Washington, District of Columbia Streetlight in front of 1722 5th St NW goes on and off. Please repair even if it is on | High Pressure Sodium | 38.88545359000 | -77.02690394000
| 1159391 | 0000 | TAYLOR ST | NE | 7/2/15 | 50085 | 5A066 | (Light out) | Jose Aguilar at 7/2/2015 4:50:39 AM: 100% complete replaced 400hps lamp 15-00165275-Streetlight Repair Investigation 301-399 Taylor St NE, Washington, District of Columbia Street light out. Metal pole 50085 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94068784000 | -77.00284881000
| 1159389 | 0400 | TAYLOR ST | NE | 8/12/15 | 50088 | 5A069 | (Light out) | C Wilkinson at 7/31/2015 5:28:07 PM Installed arm, fixture, and Tbase. . Alexander Portales at 7/9/2015 5:28:07 PM:28' GREY POLE NEEDS A NEW T-BASE, 8' GREY ARM, GREY POLE CAP, 400W HPS FIXTURE, LAMP AND T/L PHOTO | High Pressure Sodium | 38.94068397000 | -77.00029052000
6/23/15 | 1159117 | 1933 | 18TH ST | NW | 7/1/15 | 26784 | 21410 | (Light out) | Timothy Brooke at 6/30/2015 10:51:30 PM: 100% 150w hps lamp replaced | High Pressure Sodium | 38.91663347000 | -77.04174081000
6/19/15 | 1158899 | 1936 | EAST CAPITOL ST | NE | 6/21/15 | 63721 | 6M804 | (Light off/on) | Timothy Brooke at 6/21/2015 2:01:00 AM: 100% complete replaced starter | High Pressure Sodium | 38.88960987000 | -76.97672435000
6/18/15 | 1158824 | 0 | CARROLL ST | NW | 6/18/15 | 4H569DC | 4H569 | (Light out) | Jose R-6-12-2015-250 w hps lamp. 100% | High Pressure Sodium | 38.97497351000 | -77.01515190000
| 1158702 | 1428 | TOBIAS DR | SE | 6/24/15 | 81783 | 88060 | (Light out) | Timothy Brooke at 6/24/2015 12:36:44 AM: 100% replaced 250w hps kit Alexander Portales at 6/18/2015 11:54:53 PM: Need 250w hps conversion kit 15-00152649- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85014068000 | -76.98274637000
| 1158700 | 1400 | SHIPPEN LN | SE | 6/19/15 | 81735 | 88012 | (Light out) | Alexander Portales at 6/18/2015 11:43:25 PM: 100% Replaced 150w hps lamp. 15-00152646- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
6/16/15 | 1158696 | 1428 | TOBIAS DR | SE | 6/24/15 | 81783 | 88060 | (Light out) | Timothy Brooke at 6/24/2015 12:34:03 AM: 100% complete replaced 250 hps lamp Alexander Portales at 6/18/2015 11:53:10 PM: Need 250w hps conversion kit. 15-00152641-This light has been out for 2wks. There is an handicap person that lives next to this add | High Pressure Sodium | 38.85014068000 | -76.98274637000
6/15/15 | 1158623 | 3400 | 14TH ST | NW | 6/18/15 | 13680 | 1G081 | (Light out) | Alexander Portales at 6/18/2015 4:15:17 AM: 100% starter 15-00151136-Streetlight Repair Investigation 1431 Parkwood Place Northwest, Washington, DC 20010, USA Street light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93204150000 | -77.03266569000
6/14/15 | 1158567 | 0400 | TAYLOR ST | NE | 7/14/15 | 50088 | 5A069 | (Light out) | Timothy Brooke at 6/16/2015 11:01:28 PM: close w.o open up installation w.o.......no arm or fixture on this pole. need 8ft gray arm and 400w fixture. near Hawaii av and Taylor at inetersection. pole 50088. 15-00149927-Streetlight Repair Investigation | High Pressure Sodium | 38.94068397000 | -77.00029052000
6/10/15 | 1158429 | 254 | CARROLL ST | NW | 6/13/15 | 4H567DC | 4H567 | (Light out) | Jose Rodriguez at 6/13/2015 12:35:43 AM: 100%. Replaced 250w light fixture / 250w PWR DOOR / 250w HPS lamp / TLPC | High Pressure Sodium | 38.97501539000 | -77.01564228000
6/10/15 | 1158423 | 0 | CHILLUM PL | NE | 6/12/15 | 4P469DC | 4U154 | (Light out) | Jose Rodriguez at 6/12/2015 10:16:31 PM: 100%. Replaced 400w HPS lamp | High Pressure Sodium | 38.95926271000 | -77.00275729000
6/8/15 | 1158301 | 0 | CANAL RD | NW | 9/18/15 | 35452 | 29783 | (Light out) | Jose Rodriguez at 6/10/2015 3:49:53 AM: REFER TO DDOT THIS IS A 200w INCANDESCENT FIXTURE, CUSTOMER IS REQUESTING A LIGHT FIXTURE WITH COVER. THIS LIGHT WAS FUNCTIONING AT ARRIVAL 15-00144086-we have reported this problem SEVERAL times. | High Pressure Sodium | 38.90598666000 | -77.07852914000
6/1/15 | 1157930 | 1500 | TANNER CT | SE | 6/1/15 | 81772 | 88049 | (Light out) | TIM BROOKE-05/16/15-REPLACED LAMP. 100% | High Pressure Sodium | 38.84759651000 | -76.98189288000
5/28/15 | 1157741 | 3884 | PENNSYLVANIA AVE | SE | 5/29/15 | 77877DC | 7E015 | (Light out) | Timothy Brooke at 5/29/2015 4:44:12 AM: 100% 400w HPS lamp | High Pressure Sodium | 38.86571914000 | -76.95138037000
5/20/15 | 1157320 | 3033 | BLADENSBURG RD | NE | 5/22/15 | 58720DC | 5A172DC | (Light out) | Alexander Portales at 5/21/2015 10:05:06 PM: 100% Replaced 200 incandescent lamp. 15-00125901-2 lights in the alley cwDesc: ALLEYLIGHT REPAIR | Incandescent | 38.92960546000 | -76.95868010000
5/15/15 | 1157112 | 1534 | TANNER ST | SE | 5/16/15 | 81769 | 88046 | (Light out) | Timothy Brooke at 5/16/2015 3:04:03 AM: 100% 250w hps lamp 15-00121720-Caller reporting streetlights out on metal pole all through out the block. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84740623000 | -76.98158821000
5/14/15 | 1157052 | 1403 | KEARNEY ST | NW | 5/16/15 | 59990 | 5A182 | (Light out) | Timothy Brooke at 5/15/2015 9:17:20 PM: 100% 300w incandescent 15-00121292- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91424947000 | -77.01606264000
5/12/15 | 1156858 | 0000 | ROBINSON ST | SE | 5/15/15 | 81756 | 88033 | (Light out) | Timothy Brooke at 5/15/2015 2:05:02 AM: 100% Replaced N/W Photocell & 250W HPS Lamp 15-00118164-The light pole was hit by a stolen car. Now the light does not work it is very dark at this location. Recently there have been car window broken at night an | High Pressure Sodium | 38.84997435000 | -76.98416955000
5/11/15 | 1156739 | 0000 | H ST | NE | 5/11/15 | 68252DC | 68252 | (Light out) | TIM BROOKE-REPLACED PC AND LAMP. 100% | High Pressure Sodium | 38.90032915000 | -77.00287599000
5/11/15 | 1156738 | 0000 | H ST | NE | 5/11/15 | 68244DC | 68244 | (Light out) | TIM BROOKE-REPLACED PC. 100% | High Pressure Sodium | 38.90006002000 | -77.00655445000
5/11/15 | 1156737 | 0000 | H ST | NE | 5/11/15 | 68255DC | 68255 | (Light out) | TIM BROOKE-REPLACED PC. 100% | High Pressure Sodium | 38.90037863000 | -77.00528191000
5/8/15 | 1156711 | 2801 | ALLENDALE PL | NW | 5/11/15 | 30002DC | 3A363DC | (Light out) | Anibal Portillo at 5/11/2015 12:35:07 AM: 100%--Replaced 70 w HPS lamp 15-00115645-AT THE CORNER OF 2833 ALLENDALE PLACE cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.94875166000 | -77.05505542000
5/7/15 | 1156652 | 3310 | 15TH ST | NE | 5/7/15 | 51221DC | 5A117DC | (Light out) | Timothy Brooke at 5/7/2015 9:48:59 PM: 100% 300W incandescent Lamp 15-00113740-street light on the left hand side of 3315 15th st, ne (left hand side going toward Kearny st) on streetlight next to pole#: 51220d, 804399-340890. please repair ASAP. cwD | Incandescent | 38.93137950000 | -76.98438250000
5/5/15 | 1156551 | 0 | INTERSTATE 695 | SE | 5/5/15 | 695-001W-9 | 695W613 | (Overhead guide sign no current) | Jose Aguilar at 5/5/2015 9:52:21 AM: 100% upon investigation I found out that the hot leg was cut in the pull box due to ground fault ..... I spliced it and the lights are now back on Jose Aguilar at 4/29/2015 3:29:12 PM: no current to over head sign . | High Pressure Sodium | 38.88110666000 | -77.00656804000
5/1/15 | 1156396 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:26:31 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
5/1/15 | 1156393 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:25:52 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
| 1156394 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:25:04 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
| 1156395 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:23:15 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
5/1/15 | 1156391 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:23:43 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
| 1156392 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:25:26 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
5/1/15 | 1156388 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:22:11 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
| 1156389 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:30:38 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
5/1/15 | 1156386 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:27:09 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
| 1156387 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:29:28 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
5/1/15 | 1156383 | 1423 | ROBINSON ST | SE | 5/5/15 | 81736 | 88013 | (Light out) | Timothy Brooke at 5/4/2015 9:28:42 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84912960000 | -76.98365616000
| 1156384 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:22:41 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
| 1156385 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:26:12 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
5/1/15 | 1156380 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:24:31 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
| 1156381 | 1423 | ROBINSON ST | SE | 5/5/15 | 81736 | 88013 | (Light out) | Timothy Brooke at 5/4/2015 9:29:03 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84912960000 | -76.98365616000
| 1156382 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:26:49 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
5/1/15 | 1156378 | 1423 | ROBINSON ST | SE | 5/5/15 | 81736 | 88013 | (Light out) | Timothy Brooke at 5/4/2015 9:27:52 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84912960000 | -76.98365616000
| 1156379 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:31:14 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
5/1/15 | 1156376 | 1400 | SHIPPEN LN | SE | 5/5/15 | 81735 | 88012 | (Light out) | Timothy Brooke at 5/4/2015 9:27:29 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84900988000 | -76.98347646000
| 1156377 | 1423 | ROBINSON ST | SE | 5/5/15 | 81736 | 88013 | (Light out) | Timothy Brooke at 5/4/2015 9:28:17 PM: clear location. we have checked the front and back of this location thoroughly and there is not any lights out around this area 15-00109459- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84912960000 | -76.98365616000
4/28/15 | 1156242 | 5022 | F ST | SE | 4/29/15 | 70037 | 7A006 | (Light out) | Anibal Portillo at 4/29/2015 12:09:52 AM: 100% 250W HPS LAMP AND 118 GLOBE 15-00105510 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88178017000 | -76.93059465000
4/28/15 | 1156217 | 0 | INTERSTATE 695 | SE |  | 695-001W-9 | 695W613 | (Overhead guide sign light out) | Jose Aguilar at 4/29/2015 3:29:12 PM: no current to over head sign .... | High Pressure Sodium | 38.88110666000 | -77.00656804000
4/24/15 | 1156111 | 2327 | 33RD ST | SE | 4/27/15 | 74832DC | 7A095DC | (Light out) | Timothy Brooke at 4/27/2015 11:39:13 PM: 100% replaced photocell 15-00101634- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86054874000 | -76.96053965000
4/24/15 | 1156074 | 0 | CONNECTICUT AVE | NW | 5/12/15 | 38585 | 3E024 | (Light out) | s: Alexander Portales at 5/12/2015 12:36:55 PM: 100% replaced 70' # 10. light work properly Jose Aguilar at 5/6/2015 3:12:43 PM: upon arrival I had to pump the water out the manhole to check inside ..... when I got in the manhole I didn't see any str | High Pressure Sodium | 38.94350522000 | -77.06325010000
4/14/15 | 1155455 | 5005 | IVORY WALTERS LN | SE | 4/15/15 | 70068 | 7A050 | (Light out) | Alexander Portales at 4/15/2015 1:48:13 AM: 100% 250W HPS Lamp | High Pressure Sodium | 38.88142209000 | -76.93123721000
4/14/15 | 1155451 | 4651 | BENNING RD | SE | 4/15/15 | 75822 | 75822DC | (Light out) | Alexander Portales at 4/15/2015 2:53:46 AM: 100% 400W HPS Lamp & Starter | High Pressure Sodium | 38.87611644000 | -76.93130301000
| 1154805 | 1625 | NEW YORK AVE | NE | 4/27/15 | 50062 | 5A053 | (Light out) | Jose Aguilar at 4/27/2015 7:58:51 AM: 100% installed 28' pole , 250W cut off fixture and 90' of #10 AWG WIRE. Brian Maynard at 4/16/2015 7:34:39 AM: Alfaro 4-15-15 Foundation Complete\ Jose Aguilar at 4/3/2015 10:45:06 AM: 100% removed 28' pole t-base | High Pressure Sodium | 38.91708690000 | -76.98011488000
4/1/15 | 1154769 | 3204 | 15TH PL | SE | 4/1/15 | 81716 | 87993 | (Light off/on) | Alexander Portales at 4/1/2015 10:23:16 PM: 100% 150W hps lamp T/L photo cell Please ask your staff to return to rear of 3204 15th Place, SE tonight to make a thorough repair. The resident said the light is still going off/on. This is a crime issue. | High Pressure Sodium | 38.84976378000 | -76.98203464000
3/31/15 | 1154681 | 0 | 8TH ST | NW | 4/3/15 | 25202 | 6A829 | (Light out) | Charles Mcdermott at 4/2/2015 10:48:59 PM: 100%--replaced 400w HPS lamp /TLPC | High Pressure Sodium | 38.91242134000 | -77.02206576000
3/31/15 | 1154680 | 1604 | 7TH ST | NW | 4/3/15 | 25653 | 6A819 | (Light out) | Charles Mcdermott at 4/2/2015 11:08:56 PM: 100%-- replaced 400w HPS lamp/TLPC | High Pressure Sodium | 38.91140348000 | -77.02202187000
3/30/15 | 1154573 | 0 | NEW YORK AVE | NE | 3/31/15 | 50011 | 5A045 | (Bridge light out) | Michael Hamilton at 3/31/2015 12:14:38 PM: 100%- light is working -system needs 2-3 days of sunlight to recharge the 24 volt system to 25.6v before allowing the light to come on at night. -also tightened fixture to arm | High Pressure Sodium | 38.91707776000 | -76.96424700000
3/30/15 | 1154572 | 0 | NEW YORK AVE | NE | 3/31/15 | 50007 | 5A041 | (Bridge light out) | Michael Hamilton at 3/31/2015 12:13:53 PM: 100%- light is working -system needs 2-3 days of sunlight to recharge the 24 volt system to 25.6v before allowing the light to come on at night. -also tightened fixture to arm | High Pressure Sodium | 38.91727852000 | -76.96718437000
3/30/15 | 1154570 | 0 | NEW YORK AVE | NE | 3/31/15 | 50006 | 5A040 | (Bridge light out) | Michael Hamilton at 3/31/2015 11:51:20 AM: 100%- light is working -system needs 2-3 days of sunlight to recharge the 24 volt system to 25.6v before allowing the light to come on at night. -also tightened fixture to arm | High Pressure Sodium | 38.91731218000 | -76.96789154000
3/30/15 | 1154569 | 0 | NEW YORK AVE | NE | 3/31/15 | 50005 | 5A039 | (Bridge light out) | Michael Hamilton at 3/31/2015 11:41:54 AM: 100%- light is working -system needs 2-3 days of sunlight to recharge the 24 volt system to 25.6v before allowing the light to come on at night. -also tightened fixture to arm | High Pressure Sodium | 38.91734425000 | -76.96859446000
3/30/15 | 1154507 | 0 | MASSACHUSETTS AVE | NW | 4/8/15 | 25938 | 2L555 | (Light out) | Anibal Portillo at 4/8/2015 12:09:36 AM: 100% 400W HPS LAMP BCM - Pole is on Mass. Ave but located NWC of Mass/9th | High Pressure Sodium | 38.90304936000 | -77.02416740000
3/29/15 | 1154490 | 0 | 8TH ST | NW | 4/3/15 | 25202 | 6A829 | (Light out) | Charles Mcdermott at 4/3/2015 1:38:58 AM: 100%--Replaced 400w HPS/ TLPC/ Located @ 7th& Rhode Island/ Repeat WO#1154681 C | High Pressure Sodium | 38.91242134000 | -77.02206576000
3/26/15 | 1154157 | 3722 | HAYES ST | NE | 3/31/15 | 72374DC | 7A503 | (Light out) | Joshwa Ashby at 3/31/2015 10:56:14 PM: 100% 400W HPS LAMP AND T/L | High Pressure Sodium | 38.90352892000 | -76.95082496000
3/26/15 | 1154154 | 705 | ANACOSTIA AVE | NE | 4/3/15 | 72356DC | 7A478 | (Light out) | Joshwa Ashby at 4/2/2015 9:58:16 PM: 100% Repair Pole ID# 72356 DC Joshwa Ashby at 3/31/2015 11:25:52 PM: 100% 400W HPS LAMP | High Pressure Sodium | 38.90141616000 | -76.95127149000
3/24/15 | 1154039 | 2121 | WISCONSIN AVE | NW | 3/26/15 | 30156 | 3G105 | (Light out) | Charles Mcdermott at 3/26/2015 1:29:27 AM: 100% 400W HPS LAMP AND PHOTOCELL | High Pressure Sodium | 38.91797218000 | -77.06970643000
3/14/15 | 1153543 | 0 | CONNECTICUT AVE | NW | 4/17/15 | 38585 | 3E024 | (Light out) | Jose Aguilar at 4/17/2015 1:42:23 PM: 100% wires were burned up .... I pulled 550' 2 legs of #6 AWG AND 1 leg of #8 bare ground . also I made up all the splices in the manholes . Timothy Brooke at 2/5/2015 6:56:07 AM: PEPCO REFER - SEVERAL MANHOLES CABLE | High Pressure Sodium | 38.94350522000 | -77.06325010000
| 1153544 | 0 | CONNECTICUT AVE | NW | 4/17/15 | 38585 | 3E024 | (Light out) | Jose Aguilar at 4/17/2015 1:43:19 PM: 100% wires were burned up .... I pulled 550' 2 legs of #6 AWG AND 1 leg of #8 bare ground . also I made up all the splices in the manholes .. Timothy Brooke at 2/5/2015 6:56:07 AM: PEPCO REFER - SEVERAL MANHOLES C | High Pressure Sodium | 38.94350522000 | -77.06325010000
3/13/15 | 1153416 | 5077 | KIMI GRAY CT | SE | 3/17/15 | 70034 | 7A025 | (Light out) | Joshwa Ashby at 3/16/2015 11:25:14 PM: everything on light fixture was installed last week light is working properly Jose Mancia at 3/13/2015 5:36:23 PM: 100% Replaced lamp,photocell,and conversion kit because light was not working. Secured globe. | High Pressure Sodium | 38.88231618000 | -76.92941922000
3/12/15 | 1153321 | 501 | NEW YORK AVE | NE |  | 56842 | 5A430 | (Light out) | ichael Hamilton at 3/27/2015 8:19:51 AM: Refer to DDot- I spoke to Dan Poole, Assistant Project Manager from Scheibel Construction. I explained him that our light is not working because of the work inside of their staging area. Please contact him. Dan Poo | High Pressure Sodium | 38.91132939000 | -76.99721837000
3/10/15 | 1153194 | 3204 | 15TH PL | SE | 3/10/15 | 81716 | 87993 | (Light out) | Charles Mcdermott at 3/10/2015 8:47:46 PM: 100% PHOTOCELL 15-00052653-light goes off and on cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84976378000 | -76.98203464000
| 1153195 | 1506 | TOBIAS DR | SE | 3/10/15 | 81795 | 88072 | (Light out) | Charles Mcdermott at 3/10/2015 8:51:09 PM: 100% -- Replaced TLPC 15-00052656-light out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85006986000 | -76.98182599000
2/26/15 | 1152867 | 400 | RHODE ISLAND AVE | NW | 3/19/15 | 59987 | 5A178 | (Light out) | Michael Hamilton at 3/19/2015 2:33:05 PM: 100% -ran 160ft #10 -light working 03/18/15-REPAIR 30'-2" CONDUIT 9'X3' PCC SIDEWALK Michael Hamilton at 3/12/2015 6:31:06 PM: N/C with cut break down Jose Aguilar at 3/10/2015 11:37:32 AM: location will rema | High Pressure Sodium | 38.91400893000 | -77.01743154000
2/26/15 | 1152806 | 0 | INTERSTATE 395 | SW | 3/2/15 | 395-008N-2 | 395N616 | (Overhead guide sign light out) | Jose Aguilar at 3/2/2015 12:36:24 PM: 100% found a broken splice at the photocell ... also I replaced all 3 lamps 400W MH now all the lights are working fine ... ALL OUT | High Pressure Sodium | 38.88218760000 | -77.02743713000
2/26/15 | 1152805 | 0 | INTERSTATE 395 | SW | 3/2/15 | 395-020W-3 | 395S615 | (Overhead guide sign light out) | ose Aguilar at 3/2/2015 11:02:07 AM: 100% replaced 100W hps lamps to light 1 and 2 #1 and 2 OUT | High Pressure Sodium | 38.88257008000 | -77.02132351000
2/26/15 | 1152804 | 0 | INTERSTATE 395 | SW | 3/2/15 | 395-019W-8 | 395S617 | (Overhead guide sign light out) | Jose Aguilar at 3/2/2015 11:04:11 AM: 100% replaced 3 100W hps lamps #1 and 2 OUT #1 and 2 OUT | High Pressure Sodium | 38.88266839000 | -77.02310233000
2/26/15 | 1152803 | 0 | INTERSTATE 695 | SE | 3/9/15 | 695-005E-3 | 695E614 | (Overhead guide sign light out) | Jose Aguilar at 3/9/2015 12:30:59 PM: 100% upon inspection I found out that the terminal lug was damaged inside the disconnect ....I used another lug and now the problem is fixed Jose Aguilar at 3/2/2015 1:59:56 PM: OVERHEAD GUIDE SIGN nO cURRENT....l | High Pressure Sodium | 38.88084110000 | -77.00451005000
2/12/15 | 1152161 | 300 | 3RD ST | SW | 2/25/15 | 21551 | 6A351 | (Light out) | Timothy Brooke at 2/25/2015 2:22:35 PM: 100% working upon arrival BCM - Need daytime SURVEY>>> Jose Aguilar at 2/13/2015 11:20:58 PM: NO CURRENT/Refer DDOT/ Major Construction @ Location Pole#: 21551/22553 | High Pressure Sodium | 38.88562094000 | -77.01510801000
2/12/15 | 1152144 | 0000 | 15TH PL | SE | 2/18/15 | 81780 | 88057 | (Light out) | Charles Mcdermott at 2/17/2015 9:11:41 PM: 100--Replaced 250HPS Bulb/ Removed Ice From Fixture/ Reseated Globe 15-00033552-3200 block of 15th Pl SE the caller said that the light globe is about to fall off and she is afraid that the light will fall a | High Pressure Sodium | 38.84932860000 | -76.98242224000
2/12/15 | 1152141 | 0000 | 15TH PL | SE | 2/18/15 | 81780 | 88057 | (Light out) | Charles Mcdermott at 2/17/2015 9:13:23 PM: 100%--Repeat of WO#1152144 15-00033546-one light stays on all day, and another light the bulb is hanging off the pole. please repair cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84932860000 | -76.98242224000
2/6/15 | 1151892 | 0 | INTERSTATE 695 | SE | 2/13/15 | 695-003W-5 | 695E612 | (Overhead guide sign light out) | ose Aguilar at 2/13/2015 4:12:47 PM: 100% we got the power back on NO CURRENT - MAYBE ASSOCIATE WITH UNDERPASS AT NJ AVE | High Pressure Sodium | 38.88055777000 | -77.00245051000
2/3/15 | 1151685 | 4829 | NORTH CAPITOL ST | NW | 2/5/15 | 4R750 | 4A791 | (Light out) | Charles Mcdermott at 2/5/2015 10:52:46 PM: 100%--Replaced 400w HPS Bulb/ PC 15-00026538-Please the streetlight is located on the pole on the west side of street. Please repair. Thanks cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94981176000 | -77.00891482000
1/31/15 | 1151416 | 0 | FERN PL | NW | 2/4/15 | 4D591DC | 4D891DC | (Light out) | oshwa Ashby at 2/3/2015 11:57:55 PM: 100% 300W incandescent lamp | Incandescent | 38.97836028000 | -77.02202042000
1/29/15 | 1151307 | 0 | EAST CAPITOL ST | NE | 2/2/15 | 73562 | 73562DC | (Light out) | Alexander Portales at 2/1/2015 11:13:24 PM: 100% 250W hps lamp photo cell | High Pressure Sodium | 38.88964380000 | -76.91556114000
1/28/15 | 1151250 | 0 | CECIL PL | NW | 3/11/15 | 21193 | 2H002 | (Light out) | Michael Hamilton at 2/28/2015 9:56:14 AM: 100% installed 100 w HPS kit with 100 w lamp . also installed 60 ft total of #10 wire. ,made connections in manhole and terminated kit. tested light and is now working properly Alexander Portales at 2/25/2015 9 | Incandescent | 38.90349703000 | -77.06387013000
1/19/15 | 1150848 | 206 | RHODE ISLAND AVE | NW | 1/20/15 | 59996 | 5A188 | (Light out) | Joshwa Ashby at 1/20/2015 4:38:33 AM: 100% 300W incandescent lamp 15-00014232- cwDesc: STREETLIGHT REPAIR | Incandescent | 38.91473859000 | -77.01463730000
1/15/15 | 1150657 | 2218 | WISCONSIN AVE | NW | 3/25/15 | 30161 | 3G086 | (Light out) | Jose Aguilar at 3/25/2015 10:03:46 AM: >>>>>>>>. 100%. <<<<<<<<< installed 35' of #10 AWG ..... light is now working 100% 3-24-2015 Repair breakdown 25'-2'conduit and 10'x3' pcc sidewalk. WAINTING ON RED LINE DRAWINGS.....ose Aguilar at 1/22/2015 1 | High Pressure Sodium | 38.91961236000 | -77.07085524000
1/14/15 | 1150633 | 2912 | BLADENSBURG RD | NE | 1/15/15 | 51235DC | 5A131DC | (Light out) | Luis Quijada at 1/15/2015 7:48:17 PM: 100% PHOTOCELL 15-00010701- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92770962000 | -76.96225165000
1/13/15 | 1150450 | 1401 | 7TH ST | NW | 1/14/15 | 25699 | 6A805 | (Light out) | Luis Quijada at 1/14/2015 1:45:33 AM: 100% 400W HPS LAMP 15-00007488-Streetlight Repair Investigation 1401 7th Street Northwest, Washington, District of Columbia This issue has an image. You can view it here http://seeclickfix.com/issues/1436414 . | High Pressure Sodium | 38.90896734000 | -77.02182266000
1/13/15 | 1150349 | 0000 | SUITLAND PKY | SE | 1/13/15 | 83281 | 82381 | (Light out) | LUIS Q-1/12/15-REPLACED LAMP AND PHOTOCELL | High Pressure Sodium | 38.86351812000 | -77.00055997000
1/13/15 | 1150322 | 0 | WHITNEY M YOUNG BRG | SE | 1/15/15 | 295-033E-5 | ECSE705 | (Overhead guide sign light out) | Jose Aguilar at 1/15/2015 4:38:54 PM: >>>>>>>>>>>>>> 100% <<<<<<<<<<<<<<< after doing all the necessary searching I found out that the Hotwire feeding The lights and The sign was cut in one of the pulled boxes due to corrosion ...I spliced the wires back | High Pressure Sodium | 38.88972513000 | -76.96245405000
1/9/15 | 1150277 | 0 | INTERSTATE 295 | SE | 1/13/15 | 86495 | 8A074 | (Light out) | Jose Aguilar at 1/13/2015 4:51:24 PM: 100% replaced 400 W hps lamp | High Pressure Sodium | 38.84532586000 | -77.00708398000
12/23/14 | 1149725 | 0 | IOWA AVE | NW | 1/2/15 | 4K496 | 4U128 | (Light out) | Naji Carson at 1/2/2015 12:41:37 PM: 100% Jose Aguilar at 12/26/2014 9:49:22 PM: NO CURRENT 0 VOLTS. DAY TIME CREW REQUIRED... | High Pressure Sodium | 38.94605354000 | -77.02957834000
12/22/14 | 1149699 | 1240 | UPSHUR ST | NW | 12/24/14 | 4R784 | 4R792 | (Light dim) | Alexander Portales at 12/24/2014 1:06:25 AM: changed 250w HPS now 100% Alexander Portales at 12/24/2014 1:05:48 AM: changed 250 HPS lamp now 100% | High Pressure Sodium | 38.94192309000 | -77.02764852000
12/22/14 | 1149684 | 0 | 7TH ST | NW | 12/24/14 | 22409 | 6M688 | (Light out) | Trang Huynh at 12/24/2014 1:50:20 AM: 100% 250W HPS LAMP | High Pressure Sodium | 38.90199325000 | -77.02201951000
12/15/14 | 1149332 | 0 | C ST | SW | 12/16/14 | 21788 | 6A353 | (Light out) | Trang Huynh at 12/15/2014 11:21:44 PM: 100% 250W HPS LAMP | High Pressure Sodium | 38.88598753000 | -77.01505038000
12/10/14 | 1148979 | 0 | INTERSTATE 695 | SE | 12/12/14 | 695-001W-9 | 695W613 | (Overhead guide sign light out) | lexander Portales at 12/12/2014 12:05:58 PM: 100%. ( 3 ) 100W HPS LAMP #2,3, & 4 LIGHT OUT #2,3, & 4 LIGHT OUT | High Pressure Sodium | 38.88110666000 | -77.00656804000
12/10/14 | 1148977 | 0 | WHITNEY M YOUNG BRG | SE | 12/10/14 | 295-033E-5 | ECSE705 | (Overhead guide sign light out) | Alexander Portales at 12/10/2014 11:10:44 AM: 100%.100W HPS LAMP #4 OUT #4 OUT | High Pressure Sodium | 38.88972513000 | -76.96245405000
12/9/14 | 1148937 | 0 | MACARTHUR BLVD | NW | 12/11/14 | 33891 | 3A375 | (Light out) | Jose Aguilar at 12/11/2014 4:23:50 AM: 100% 250 W hps lamp | High Pressure Sodium | 38.92881945000 | -77.10590630000
12/6/14 | 1148827 | 0000 | OVERLOOK AVE | SE | 12/6/14 | 81806 | 85793 | (Light out) | Jose Aguilar at 12/6/2014 10:00:37 PM: 100% replaced 400 W hps lamp | High Pressure Sodium | 38.82907587000 | -77.01730772000
11/21/14 | 1147962 | 2914 | BLADENSBURG RD | NE | 11/22/14 | 50101 | 5A087 | (Light out) | Ronald Keith at 11/22/2014 12:05:54 AM: 100% 400w HPS lamp Ronald Keith at 11/22/2014 12:01:12 AM: 100% 400w HPS lamp | High Pressure Sodium | 38.92776425000 | -76.96181488000
11/21/14 | 1147949 | 1475 | BRUCE PL | SE | 11/22/14 | 81731 | 88008 | (Light out) | Trang Huynh at 11/22/2014 9:50:03 PM: 100% 150W HPS LAMP AND P/C | High Pressure Sodium | 38.85043302000 | -76.98303184000
11/21/14 | 1147948 | 1500 | TANNER ST | SE | 11/24/14 | 81773 | 88050 | (Light out) | Trang Huynh at 11/22/2014 9:43:01 PM: 100% 250W HPS LAMP | High Pressure Sodium | 38.84729389000 | -76.98176920000
11/21/14 | 1147943 | 0 | SHERIDAN RD | SE | 11/24/14 | 81363DC | 8M047 | (Light out) | Trang Huynh at 11/24/2014 8:41:18 PM: 100% SAME WO# 1147940 | High Pressure Sodium | 38.85928023000 | -76.99335324000
11/21/14 | 1147940 | 0 | SHERIDAN RD | SE | 11/24/14 | 81363DC | 8M047 | (Light out) | Trang Huynh at 11/24/2014 8:39:53 PM: 100% 400W CUTOFF FIXTURE, 400W HPS POWER DOOR, 400W HPS LAMP AND P/C | High Pressure Sodium | 38.85928023000 | -76.99335324000
11/20/14 | 1147894 | 0000 | INTERSTATE 395 | SW | 11/25/14 | 395-003S-4 | 395S235 | (Overhead guide sign light out) | Alexander Portales at 11/25/2014 3:11:05 PM: 100%. 400W MH LAMP 395-003S #2 LO | High Pressure Sodium | 38.87847753000 | -77.03939283000
11/20/14 | 1147893 | 0 | INTERSTATE 695 | SE | 11/24/14 | 695-001W-9 | 695W613 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88110666000 | -77.00656804000
11/19/14 | 1147846 | 625 | BURNS ST | SE | 11/25/14 | 76071 | 76071DC | (Light out) | Timothy Brooke at 11/25/2014 12:28:31 PM: 100% installed 180 ft of quad plex cable between poles 76071dc and 76072dc. terminated both ends and terminated at source .tested all remainder lights on circuit . all alley lights working properly now : Tran | High Pressure Sodium | 38.88020983000 | -76.94386284000
11/17/14 | 1147656 | 3222 | 14TH ST | NE | 11/19/14 | 51220DC | 5A114DC | (Light out) | Trang Huynh at 11/19/2014 1:59:59 AM: 100% PHOTOCELL | High Pressure Sodium | 38.93068379000 | -76.98625793000
11/11/14 | 1147389 | 1508 | 17TH ST | NW | 11/18/14 | 26732 | 2M073 | (Light out) | Ronald Keith at 11/17/2014 4:18:06 AM; INSTALLED STARTER, 7-W LAMP, AND tlpc. 100%>>>Ronald Keith at 11/15/2014 3:18:26 AM: request van 70w HPS alley pole under ground feed 14-00310108- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.91000204000 | -77.03857883000
11/7/14 | 1147177 | 0 | CANAL RD | NW | 11/8/14 | 21171 | 29774 | (Light out) | Ronald Keith at 11/8/2014 3:40:06 AM: 100% 200w incandescent lamp Ronald Keith at 11/7/2014 8:15:59 PM: 100% 200w incandescent lamp | High Pressure Sodium | 38.90551232000 | -77.07477025000
11/6/14 | 1147062 | 0 | INTERSTATE 695 | SE | 11/7/14 | 695-005E-3 | 695E614 | (Overhead guide sign light out) | Jose Aguilar at 11/7/2014 4:05:32 PM: No current Bad disconnect and also one of the phaces is out . more time is required to complete this job ... | High Pressure Sodium | 38.88084110000 | -77.00451005000
11/6/14 | 1147059 | 300 | NEW YORK AVE | NW | 11/7/14 | 395-052W-3 | NYAW604 | (Overhead guide sign light out) | Jose Aguilar at 11/7/2014 4:32:46 PM: 100% replaced 150W HPS lamp | High Pressure Sodium | 38.90536765000 | -77.01505349000
11/6/14 | 1147058 | 307 | NEW YORK AVE | NW | 11/7/14 | 395-051W-4 | NYAW602 | (Overhead guide sign light out) | Jose Aguilar at 11/7/2014 4:59:51 PM: 100% replaced 4- 400W MH LAMPS | High Pressure Sodium | 38.90508373000 | -77.01589183000
11/6/14 | 1147057 | 0 | WHITNEY M YOUNG BRG | SE | 11/7/14 | 295-033E-5 | ECSE705 | (Overhead guide sign light out) | Jose Aguilar at 11/7/2014 10:54:55 AM: 100% Replaced 3 100Watts HPS lamps | High Pressure Sodium | 38.88972513000 | -76.96245405000
11/6/14 | 1147056 | 0000 | EAST CAPITOL ST | SE | 11/8/14 | 295-031E-5 | ECSE701 | (Overhead guide sign light out) | jose Aguilar at 11/8/2014 11:24:25 AM: 100% for one of the lights I replaced 100W HPS ballast and the lamp... and the other light fixed the push bottom switch | High Pressure Sodium | 38.88974086000 | -76.96696532000
11/6/14 | 1147033 | 0 | INTERSTATE 695 | SE | 11/24/14 | 695-001W-9 | 695W613 | (Overhead guide sign light out) | Jose Aguilar at 11/7/2014 3:26:05 PM: no current to overhead guide sign 695-001W-9 - ALL OUT | High Pressure Sodium | 38.88110666000 | -77.00656804000
11/6/14 | 1147032 | 0 | INTERSTATE 695 | SE | 11/6/14 | 695-002W-6 | 695W611 | (Overhead guide sign light out) | Jose Aguilar at 11/6/2014 2:08:29 PM: 100% replaced 150W hps lamp #5 LO 695-002W-6 #5 LO 695-002W-6 | High Pressure Sodium | 38.88104238000 | -77.00567540000
11/6/14 | 1147031 | 0 | INTERSTATE 695 | SE | 11/6/14 | 695-003W-5 | 695E612 | (Overhead guide sign light out) | Jose Aguilar at 11/6/2014 2:09:15 PM: 100% replaced 150 W hps lamp #1 LO 695-003W-5 #1 LO 695-003W-5 | High Pressure Sodium | 38.88055777000 | -77.00245051000
11/5/14 | 1147028 | 0 | CANAL RD | NW | 11/7/14 | 21171 | 29774 | (Light out) | WRONG LOCATION GIVEN BY DDOT | High Pressure Sodium | 38.90551232000 | -77.07477025000
11/1/14 | 1146634 | 3408 | 15TH ST | NE | 11/4/14 | 51212DC | 5A101DC | (Light out) | Trang Huynh at 11/4/2014 3:39:43 AM: 100% PHOTO CELL 14-00303412-Second Band on Pole 804400-170200 cwDesc: STREETLIGHT REPAIR | Incandescent | 38.93231561000 | -76.98445505000
10/31/14 | 1146581 | 0000 | NEW YORK AVE | NE | 11/5/14 | 50076 | 5A061 | (Light out) | Trang Huynh at 11/5/2014 2:20:38 AM: 100% 400W HPS LAMP & P/C | High Pressure Sodium | 38.91712421000 | -76.97842805000
10/31/14 | 1146577 | 408 | RHODE ISLAND AVE | NW | 11/4/14 | 59989 | 5A181 | (Light out) | Ronald Keith at 11/4/2014 9:44:02 PM: 100% 400w HPS lamp | High Pressure Sodium | 38.91392931000 | -77.01700898000
10/26/14 | 1146000 | 1512 | TOBIAS DR | SE | 10/29/14 | 81714 | 87991 | (Light out) | Alexander Portales at 10/28/2014 9:31:45 PM: 100%. 150W HPS LAMP, 150W HPS P/D and T/L 14-00298382- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.85019660000 | -76.98144001000
| 1145944 | 1507 | TANNER ST | SE | 10/29/14 | 81774 | 88051 | (Light out) | Alexander Portales at 10/28/2014 10:02:11 PM: 100%. W/M AND 250W HPS LAMP 14-00297567-Streetlight 1507 Tanner St SE, Washington, District of Columbia Streetlight stays on 24x7. Does nit turnoff during the day. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84738481000 | -76.98202940000
10/24/14 | 1145934 | 1500 | TANNER ST | SE | 10/29/14 | 81767 | 88044 | (Light out) | Alexander Portales at 10/28/2014 9:43:20 PM: 100%. 250W HPS LAMP 14-00297307- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84754661000 | -76.98099415000
10/24/14 | 1145897 | 0 | INTERSTATE 395 | NW | 10/29/14 | 395-005N-4 | 395N234 | (Overhead guide sign light out) | Jose Aguilar at 10/29/2014 11:16:58 AM: 100% replaced 400 W MH lamp HOV - 1 LIGHT OUT | High Pressure Sodium | 38.87624339000 | -77.04138535000
10/24/14 | 1145896 | 0 | INTERSTATE 395 | SW | 10/29/14 | 395-006S-6 | 395S233 | (Overhead guide sign light out) | Jose Aguilar at 10/29/2014 10:18:29 AM: 100% replaced 400 W MH LAMP 1 light out | Mercury Vapor | 38.87915645000 | -77.03882245000
10/24/14 | 1145892 | 0000 | INTERSTATE 395 | SW | 10/28/14 | 395-012S-8 | 395S229 | (Overhead guide sign light out) | Jose Aguilar at 10/28/2014 11:06:54 AM: replaced 400w MH LAMP. 100% 1 LIGHT OUT | High Pressure Sodium | 38.87944884000 | -77.03283901000
10/24/14 | 1145887 | 0 | INTERSTATE 395 | SW | 11/26/14 | 395-019W-8 | 395S617 | (Overhead guide sign light out) | Jose Aguilar at 11/23/2014 1:22:13 PM: rEPLAXCED 3 LAMPS . 100% Jose Aguilar at 10/30/2014 1:22:23 PM: No current to over head sign 1,4, & 5 LO | High Pressure Sodium | 38.88266839000 | -77.02310233000
10/24/14 | 1145886 | 0000 | INTERSTATE 295 | SE | 10/30/14 | 395-040N-4 | SCSN608 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88206202000 | -77.00983105000
10/23/14 | 1145854 | 1541 | 7TH ST | NW | 10/29/14 | 25702 | 6A814 | (Light out) | Alexander Portales at 10/29/2014 3:24:39 AM: 100%. 400W HPS LAMP, T/L AND 400W HPS P/D | High Pressure Sodium | 38.91080483000 | -77.02182504000
10/17/14 | 1145390 | 0000 | FRANKLIN ST | NE | 11/14/14 | 50066 | 5A057 | (Light out) | Alexander Portales at 10/17/2014 10:25:42 PM: 28' POLE ON TEMPORARY T-BASE SHOULD BE TRANSFERED TO PERMANENT FOUNDATION. 14-00292075-intersection of Franklin and Lincoln Street NE. Making a later tune from Lincoln to Frankli | High Pressure Sodium | 38.92553854000 | -77.00229041000
10/10/14 | 1144952 | 0211 | NEW YORK AVE | NW | 10/15/14 | 395-053W-3 | NYAW606 | (Overhead guide sign light out) | Alexander Portales at 10/15/2014 3:06:45 AM: 100%. (1) 100W HPS LAMP ON FIRST LIGHT LEFT TO THE RIGHT | High Pressure Sodium | 38.90568335000 | -77.01410935000
10/10/14 | 1144935 | 0000 | OVERLOOK AVE | SE | 10/14/14 | 81812 | 88086 | (Light out) | Alexander Portales at 10/13/2014 11:38:00 PM: 100% 250 W HPS LAMP & T/L P/C POLE 81812 | High Pressure Sodium | 38.83074514000 | -77.01582193000
10/10/14 | 1144934 | 0000 | OVERLOOK AVE | SW | 10/15/14 | 81838 | 88099 | (Light out) | Alexander Portales at 10/15/2014 12:08:23 AM: 100%. 250W HPS LAMP AND T/L POLE 81838 Alexander Portales at 10/14/2014 4:26:00 AM: NEED MAP. | High Pressure Sodium | 38.83275193000 | -77.01416044000
| 1144887 | 1520 | ALABAMA AVE | SE | 10/10/14 | 81749 | 88026 | (Light out) | Alexander Portales at 10/9/2014 11:18:52 PM: 100% 150 W HPS LAMP 14-00286207- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84689369000 | -76.98188151000
10/7/14 | 1144762 | 0 | 3RD ST | NW | 10/8/14 | 59991 | 5A184 | (Light out) | lexander Portales at 10/8/2014 2:38:58 AM: 100% 150 W POWER DOOR AND 150 W HPS LAMP POLE 59991 | High Pressure Sodium | 38.91407956000 | -77.01569433000
10/3/14 | 1144559 | 501 | NEW YORK AVE | NE |  | 56842 | 5A430 | (Light out) | BCM - REFER TO DDOT - IN CONSTRUCTION AREA>>>Jose Aguilar at 10/7/2014 4:18:08 PM: BRAKE DOWN There is a brake down between the manhole and the light # 56842. I pushed the rodder from the base and it stops at 30' and from MH it stops at 165' the total dis | High Pressure Sodium | 38.91132939000 | -76.99721837000
10/2/14 | 1144534 | 236 | RHODE ISLAND AVE | NW | 10/8/14 | 59993 | 5A185 | (Light out) | Alexander Portales at 10/8/2014 2:43:02 AM: 100% 300 W INCANDESCENT LAMP POLE 59993 14-00281387-Thank you! Please call me with any questions! cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91439745000 | -77.01561600000
9/26/14 | 1144163 | 1300 | UPSHUR ST | NW | 9/30/14 | 4J795 | 4U152 | (Light out) | Ronald Keith at 9/30/2014 3:48:43 AM: 100% 400w hps lamp 14-00275360-Streetlight Repair 931-1299 Upshur Street Northwest, Washington, DC 20011, USA Red light bulb is burned-out on light on NW corner of Upshur and 13th St NW. cwDesc: STREETLIGHT REP | High Pressure Sodium | 38.94192828000 | -77.02984643000
9/24/14 | 1143947 | 1900 | 37TH ST | NW | 9/30/14 | 36891 | 30482 | (Light out) | Alexander Portales at 9/29/2014 11:21:34 PM: 100% -150w hps lamp Ronald Keith at 9/26/2014 11:29:23 PM: temp needs a 150w lamp | High Pressure Sodium | 38.91672906000 | -77.07292654000
| 1143918 | 1435 | NEWTON ST | NW | 9/23/14 | 13913 | 1G072 | (Light out) | Ronald Keith at 9/23/2014 10:47:29 PM: 100% 400w HPS lamp 14-00272700-Streetlight Repair 1435 Newton NW, Washington, District of Columbia Between 14th and 16th St., street light goes out at night. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93143118000 | -77.03279918000
9/19/14 | 1143711 | 0 | 7TH ST | NW | 9/19/14 | 25703 | 6A818 | (Light out) | Alex. 09/19/2014. 4:40am. Installed 400 watt HPS lamp. | High Pressure Sodium | 38.91121698000 | -77.02181678000
9/19/14 | 1143708 | 1401 | 7TH ST | NW | 10/22/14 | 25699 | 6A805 | (Light out) | William Day at 9/30/2014 3:38:41 PM: 100% Installed 400 Watt HPS Lamp and Twist Lock Photo Cell. Missing a T Base Cover Alex. 09/19/2014. 4:35am. No current. | High Pressure Sodium | 38.90896734000 | -77.02182266000
| 1143389 | 400 | RHODE ISLAND AVE | NW | 9/17/14 | 59987 | 5A178 | (Light out) | Ronald Keith at 9/17/2014 3:19:22 AM: 100% 300w incandescent lamp pole 59987 14-00263117- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91400893000 | -77.01743154000
9/11/14 | 1143223 | 1423 | SHIPPEN LN | SE | 9/17/14 | 81759 | 88036 | (Light out) | Michael Hamilton at 9/17/2014 12:03:26 AM: 100% -all light found working fine -& no lights are on metal poles pole 81759 400 - 538 BLOCK OF LEBAUM STREET SE 14-00261394-2 stretlight poles are out on metal pole are busted out the globe and the ligh | High Pressure Sodium | 38.84947902000 | -76.98358734000
| 1142894 | 3740 | KANAWHA ST | NW | 9/15/14 | 32724DC | 3E012 | (Light out) | Timothy Brooke at 9/15/2014 3:05:22 PM: 100% upon arrival there was no neutral wire. installed 15 ft of #10 wire from secondary to light , also replaced 100 w hps power door. Ron Keith-Jose Mancia at 9/12/2014 1:20:43am: temp no current. 100w hps fixt | High Pressure Sodium | 38.96036130000 | -77.07215925000
9/3/14 | 1142665 | 1400 | SHIPPEN LN | SE | 9/4/14 | 81734 | 88011 | (Light out) | MIKE H-9/3/2014-10:25PM-100%-150W HPS AND T/L. 14-00253049-Behind Shippen line alleylight repair cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84897224000 | -76.98310254000
9/2/14 | 1142601 | 719 | 15TH ST | SE | 9/4/14 | 64363DC | 6A053 | (Light out) | MIKE H-9/4/2014-3:25AM-100%-2 LIGHTS OUT IN ALLEY-2T/L-2 200W INC LAMPS. FOR POLES 6A053 AND 64363DC 14-00251412-IN THE MIDDLE OF THE ALLEY cwDesc: ALLEYLIGHT REPAIR | Incandescent | 38.88032991000 | -76.98412324000
8/27/14 | 1142453 | 1713 | 7TH ST | NW | 8/29/14 | 25650 | 6A833 | (Light out) | Ronald Keith at 8/29/2014 5:07:35 AM: 400wpower door , p/c. 100% | High Pressure Sodium | 38.91300300000 | -77.02201369000
8/26/14 | 1142401 | 3412 | 15TH ST | NE | 8/28/14 | 51211DC | 5A100DC | (Light out) | Ronald Keith at 8/27/2014 9:42:33 PM: changed 300w incandescent 14-00247049- cwDesc: STREETLIGHT REPAIR | Incandescent | 38.93257808000 | -76.98447612000
8/26/14 | 1142348 | 0 | SHERIDAN RD | SE | 8/27/14 | 81353DC | 8U654 | (Light out) | Michael Hamilton at 8/27/2014 3:04:28 AM: 100% -400w HPS lamp -T/L Michael Hamilton at 8/27/2014 3:04:28 AM: 100% -400w HPS lamp -T/L | High Pressure Sodium | 38.85641207000 | -76.99331957000
8/22/14 | 1142241 | 0 | INTERSTATE 295 | SE | 8/23/14 | 82155 | 8L759 | (Light out) | Mike Hamilton at 8/23/2014 12:33:07 AM: Replaced 250w HPS LAMP- T/L PC 14-00243175-2 "lamp posts" are out. One in front of yellow house, possibly 827 G St., NE...2nd light is out at corner of 9th and G St., NE cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86418702000 | -76.99473194000
8/20/14 | 1142128 | 0 | K ST | SE | 8/21/14 | 67672 | 6A855 | (Light out) | MIKE H-8/21/2014-1:16AM-100%. 400 W HPS LAMP AND T/L. | High Pressure Sodium | 38.87836203000 | -77.00649464000
| 1142016 | 0 | RICHARDSON PL | NW | 8/23/14 | 59924 | 5A412 | (Light out) | DA 8-22-14 - Replaced Photo cell and 150w HPS lamp... MIKE H-8/20/2014-12:16AM-NEED VAN 14-00238676-STREET LIGHT BULB IS OUT. 14-00238676-Street light bulb is out. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91306930000 | -77.01662788000
8/14/14 | 1141799 | 2800 | LINCOLN RD | NE | 8/16/14 | 50065 | 5A056 | (Light out) | Alberto Campbell at 8/16/2014 10:29:34 AM: change twist lock photocell checked light.light working 100% no fixture neededMIKE H-8/14/2014-10:20-10:30-NEW 400 HPS FIXTURE IS NEEDED | High Pressure Sodium | 38.92549974000 | -77.00275988000
8/13/14 | 1141771 | 0 | BLADENSBURG RD | NE | 8/14/14 | 59569 | 5B253 | (Light out) | Michael Hamilton at 8/13/2014 11:26:24 PM: 100% -100w HPS lamp 14-00232969- cwDesc: ALLEYLIGHT REPAIR MIKE H-8/13/2014-11:20PM-11:25-REPLACED 100 W HPS LAMP. 100% | High Pressure Sodium | 38.90642019000 | -76.97915220000
8/10/14 | 1141635 | 1225 | 18TH ST | NW |  | 26763 | 2U514 | (Light out) | MIKE H-8/12/2014-12:40;12:45-LIGHT WORKING. 100% 14-00229597-Please fix immediately. A work request was submitted over 30 days ago, and MC Dean normally responds within 48 hours, not 30 + days. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90700407000 | -77.04161752000
8/7/14 | 1141517 | 0 | PENNSYLVANIA AVE | NW | 8/12/14 | 28039 | 2G694 | (Light out) | DH-08/07/14-REPLACED LAMP AND PHOTOCELL. NOI CURRENT UNDERGROUND | High Pressure Sodium | 38.90227133000 | -77.04894911000
8/6/14 | 1141483 | 0 | K ST | NW | 8/12/14 | 24677 | 2G692 | (Light out) | Jose Aguilar at 8/11/2014 3:21:03 PM: upon arrival I checked for power .. I noticed that this intersection was under construction by Chasepicke and the lights are not working because they will be removed and they already have the new lights operating .,, | High Pressure Sodium | 38.90236272000 | -77.04868832000
8/6/14 | 1141482 | 0 | PENNSYLVANIA AVE | NW | 8/12/14 | 28039 | 2G694 | (Light out) | Jose Aguilar at 8/11/2014 3:23:38 PM: feed for this light has been cut, because it will be removed .. the new light is already installed and operating DENO HEBRON-4:11AM;4:13AM;4:18AM-N/C UNDERGROUND | High Pressure Sodium | 38.90227133000 | -77.04894911000
7/28/14 | 1141159 | 643 | BARNES ST | NE | 7/29/14 | 72469 | 7U750 | (Light out) | 14-00216687-Streetlight Repair 600 Barnes Street Northeast, Washington, District of Columbia Streetlight lens is loose and hanging off the light pole. Otherwise appears intact. cwDesc: STREETLIGHT REPAIR MH- CLOSED LENS COVER. 100%. | High Pressure Sodium | 38.90075954000 | -76.95122635000
| 1141112 | 408 | RHODE ISLAND AVE | NW | 7/29/14 | 59989 | 5A181 | (Light out) | PL-07/29/14-4:30AM- REPLACED PHOTOCELL. COMPLETE SNW 14-00215259- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91392931000 | -77.01700898000
7/21/14 | 1140953 | 408 | RHODE ISLAND AVE | NW | 7/25/14 | 59989 | 5A181 | (Light out) | Mike H. 07/25/2014. Installed 300watt lamp and PhotoCell for pole 59989. 100% Complete. 14-00209449-2 lights are out on this block cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91392931000 | -77.01700898000
7/20/14 | 1140910 | 3261 | STANTON RD | SE | 8/16/14 | 81745 | 88022 | (Light out) | PL-08/08/14-NEED 8X4 COVER DAY CREW PL-08/05/14-INSTALL GLOBE/LENS MH-NEED T-BASE COVER PLATE. 14-00208042-Light pole doesn't have a cover which the wires are exposed cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84770266000 | -76.98109122000
7/18/14 | 1140843 | 1713 | 7TH ST | NW | 7/18/14 | 25650 | 6A833 | (Light out) | LM 7/18/14 Greg installed a TLPC & 400 lamp installed | High Pressure Sodium | 38.91300300000 | -77.02201369000
7/17/14 | 1140802 | 0400 | TAYLOR ST | NE | 7/30/14 | 50084 | 5A065 | (Light out) | JE-07/27/14-4:30AM-NEED 400W POWER DOOR PAT LUPINO-7/30-4:15AM;4:23AM. REPLACED POWER DOOR. 100% COMPLETE. | High Pressure Sodium | 38.94081181000 | -77.00160841000
7/1/14 | 1140367 | 1211 | 7TH ST | NW | 7/1/14 | 25661 | 6A790 | (Light out) | DA 7/01/14 @ 250am A Buige / J Brucksch repaired pole 25661 | High Pressure Sodium | 38.90712952000 | -77.02201691000
7/1/14 | 1140364 | 0 | NEW YORK AVE | NW | 8/2/14 | 25924 | 6A530 | (Light out) | Timothy Brooke at 8/2/2014 7:49:34 AM: upon arrival light was working properly. 100%LM 7/7/14 Adric found Wire has been pulled out of the PVC pipe due to near by construction. 1145am DA 7/01/14 @ 140am A Buige / J Brucksch pole 25924 - NC Underground ref | High Pressure Sodium | 38.90430311000 | -77.01816812000
6/25/14 | 1140127 | 1000 | 4TH ST | SE | 6/25/14 | 67544 | 6A436 | (Light out) | DA 6/25/14 @ 310am J Brucksch / S Peters repaired pole 67544- muse 15410 - complete | High Pressure Sodium | 38.87791653000 | -77.00064890000
6/25/14 | 1140118 | 2406 | 18TH ST | NW | 6/25/14 | 11532 | 1G489 | (Light out) | DA 6/25/14 R Fell / R Bush repaired pole 11532 muse 15279 - complete | High Pressure Sodium | 38.92086253000 | -77.04217175000
6/24/14 | 1140031 | 0 | 14TH ST | NW | 6/24/14 | 19990 | 11795 | (Light out) | DA 6/24/14 @ 105am K Dunton / M Brown repaired pole 19990 - muse 15407 installed T Base door complete | High Pressure Sodium | 38.91820164000 | -77.03182708000
6/24/14 | 1140024 | 1100 | 11TH ST | SE | 6/25/14 | 67614 | 6L993 | (Light out) | DA 6/24/14 @ 205am J Brucksch / S Peters pole 67614 - Muse 15424 -needs 400 powerdoor | High Pressure Sodium | 38.87689854000 | -76.99165831000
6/24/14 | 1140005 | 0 | BANGOR ST | SE | 6/24/14 | 74833DC | 7A096DC | (Light out) | DA 6/24/14 @ 215am M Craig / J Peck repaired pole 74833dc - MUSE 14974 | High Pressure Sodium | 38.86055117000 | -76.96088105000
6/23/14 | 1139891 | 921 | 4TH ST | NE | 6/23/14 | 61438 | 6A299 | (Light out) | DA 6/22/14 @ 935pm S Peters / J Brucksch repaired pole 61438 no muse - repaired photocell adapter | High Pressure Sodium | 38.90192178000 | -77.00064462000
6/19/14 | 1139762 | 508 | MELLON ST | SE | 6/19/14 | 86496 | 8A358 | (Light out) | LM 6/19/14 Adric made splice in the T-Base & Installed a TLPC. 3pm | High Pressure Sodium | 38.86233552000 | -77.00031519000
6/19/14 | 1139727 | 3217 | CONNECTICUT AVE | NW | 6/19/14 | 30100 | 30427 | (Light out) | DA 6/19/14 @ 310am R Fell / R Bush pole 30100 - muse 14840 -light dound on and working | High Pressure Sodium | 38.93294186000 | -77.05685295000
6/18/14 | 1139629 | 1403 | MONROE ST | NE | 6/18/14 | 51215DC | 5A105DC | (Light out) | DA 6/18/14 @ 215am J Brucksch / S Peters repaired pole 51215dc - muse 14367 - complete | High Pressure Sodium | 38.93275065000 | -76.98602999000
6/18/14 | 1139575 | 0 | E ST | SW | 6/18/14 | 21609 | 6A340 | (Light out) | DA 6/17/14 @ 930pm A Buige / S Manning pole 21609 - muse 14652 -pole not at location possibly removed due to construction | High Pressure Sodium | 38.88331015000 | -77.01862717000
6/17/14 | 1139547 | 2318 | 32ND ST | SE | 6/18/14 | 74839DC | 7A103DC | (Light out) | DA 6/17/14 R Fells / R Bush repaired pole 74839dc muse 13552 - complete | High Pressure Sodium | 38.86076984000 | -76.96087210000
6/17/14 | 1139520 | 5309 | B ST | SE | 12/17/14 | 75568 | 75568DC | (Light out) | DA 6/19/14 R Fell / S Manning repaired pole 75568 - Needs Tree Trimmed 14-00173927- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.88611178000 | -76.92542926000
6/17/14 | 1139513 | 0 | INTERSTATE 395 | SW | 6/19/14 | 395-022N-9 | 395N612 | (Overhead guide sign no current) | LM 6/19/14 Anthony Checked out the circuit & found a bad fuse. Replaced the fuse and light is now working fine. 1030am | High Pressure Sodium | 38.88233608000 | -77.01846985000
6/17/14 | 1139464 | 0000 | MICHIGAN AVE | NE | 6/17/14 | 50072 | 2A059 | (Light out) | DA 6/17/14 @ 130am J Brucksch / S Peters repaired pole 50072 - Muse 14647 - complete | High Pressure Sodium | 38.90029467000 | -77.03972470000
6/16/14 | 1139449 | 2 | MASSACHUSETTS AVE | NE | 6/17/14 | 60928 | 6U602 | (Light out) | DA 6/16/14 @ 1117pm A Buige / S Manning pole 60928 - MUSE 14003 - complete | High Pressure Sodium | 38.89801466000 | -77.00755371000
6/16/14 | 1139448 | 600 | 1ST ST | NE | 6/17/14 | 60927 | 6U601 | (Light out) | DA 6/16/14 @ 1110pm A Buige / S Manning pole 60327 - MUSE 14002 - complete | High Pressure Sodium | 38.89824861000 | -77.00746947000
6/12/14 | 1139209 | 206 | D ST | SE | 8/3/14 | 65644 | 65618 | (Light out) | Jose Aguilar at 8/2/2014 10:55:43 AM: Wires from the MH to the T base were deteriorated and when they shorted out the wire broke. so, I installed new #10 wire from the MH to the light ... total light is 60' 2 # and 1 #8 ground ... I also installed a new | High Pressure Sodium | 38.88502510000 | -77.00336540000
6/12/14 | 1139197 | 136 | RHODE ISLAND AVE | NW | 7/1/14 | 59999 | 5A191 | (Light out) | LM 7/1/14 Rob made a splice in the manhole. light now working. 1030am LM 6/20/14 Rob found that the Manhole has too much trash & junk inside. It can not be accessed until manhole is cleaned. 945am DA 6/16/14 @ 1020pm J Brucksch / S Peters pole 59999 - | High Pressure Sodium | 38.91513978000 | -77.01349288000
6/12/14 | 1139190 | 717 | BARNES ST | NE | 6/16/14 | 72462DC | 7A473 | (Light out) | DA 6/15/14 @ 845pm R Bush / M Brown reattached shield screws were missing - muse 14501 - complete 14-00169741-Cover of light is flapping. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90163933000 | -76.95010523000
6/12/14 | 1139130 | 1000 | NEW YORK AVE | NW | 6/12/14 | 22948 | 2L032 | (Light out) | DA 6/11/14 @ 233am A Buige / A Diaz pole 22978 - MUSE 12721 - light found on and working | High Pressure Sodium | 38.90132896000 | -77.02684244000
6/12/14 | 1139093 | 0 | 7TH ST | NW | 6/12/14 | 25654 | 6A815 | (Light out) | DA 6/12/14 @ 210am J Brucksch / S Peters repaired pole 25654 - complete | High Pressure Sodium | 38.91104528000 | -77.02202690000
6/10/14 | 1138879 | 0 | CAMDEN ST | SE | 6/10/14 | 74750DC | 7A064DC | (Light out) | DA 6/10/14 @ 312am R Bush / M Brown repaired pole 74750dc MUSE 13551 | High Pressure Sodium | 38.85948091000 | -76.96189661000
6/9/14 | 1138743 | 0 | WISCONSIN AVE | NW | 6/9/14 | 3A061DC | 3A061 | (Light out) | DA 6/8/14 R Fells / R Douglas repaired pole 3a061dc muse 13335 - complete | High Pressure Sodium | 38.94998940000 | -77.08058258000
6/6/14 | 1138611 | 1100 | 11TH ST | SE | 6/8/14 | 67614 | 6L993 | (Light out) | DA 6/6/14 @ 330am J Brucksch / S Peters pole 67614 MUSE 13135 - needs 400 powerdoor | High Pressure Sodium | 38.87689854000 | -76.99165831000
6/6/14 | 1138577 | 714 | 21ST ST | NW | 6/6/14 | 28278 | 2L389 | (Light out) | DA 6/5/14 @ 1122pm A Buige / A Diaz pole 28278 - MUSE 13376- can not access light due to construction behind fence | High Pressure Sodium | 38.89893750000 | -77.04659509000
6/5/14 | 1138510 | 0 | GARFIELD ST | NW | 6/9/14 | 35100 | 3A377 | (Light out) | DA 6/8/14 R Fells / R Douglas repaired pole 35100 muse 13614 - complete | High Pressure Sodium | 38.92674181000 | -77.05525746000
6/4/14 | 1138288 | 5600 | 3RD ST | NE | 6/5/14 | 4P471DC | 4U158 | (Light out) | DA 6/3/14 @ 930pm M Craig / J Peck pole 4p471dc needs 400 powerdoor | High Pressure Sodium | 38.95858464000 | -77.00292664000
6/3/14 | 1138190 | 0 | 33RD PL | NW | 6/3/14 | 37335 | 37735 | (Light out) | DA 6/3/14 R Fells repaired pole 37335 Muse 12987 | High Pressure Sodium | 38.93133051000 | -77.06519402000
6/3/14 | 1138157 | 0 | 14TH ST | NW | 6/3/14 | 14568 | 1G558 | (Light out) | DA 6/3/14 @ 1247am M Craig / J Peck repaired pole 14568 MUSE 12718 | High Pressure Sodium | 38.91881236000 | -77.03182667000
5/30/14 | 1137998 | 917 | U ST | NW | 5/30/14 | 14405 | 1G555 | (Light out) | DA 5/30/14 @ 139am R Bush / M Brown repaired pole 14405 - MUSE 11740 | High Pressure Sodium | 38.91709088000 | -77.02460528000
5/30/14 | 1137996 | 0 | IRVING ST | NW | 5/30/14 | 12743 | 1G024 | (Light out) | DA 5/30/14 @ 1213am R Bush / M Brown pole 12743 light is on and working - MUSE 11713 | High Pressure Sodium | 38.92879140000 | -77.03335110000
5/29/14 | 1137937 | 0 | 14TH ST | NW | 6/2/14 | 14568 | 1G558 | (Light out) | DA 6/2/14 @ 130am R Bush / M Brown repaired pole 14568 - MUSE 12718 - complete | High Pressure Sodium | 38.91881236000 | -77.03182667000
5/29/14 | 1137789 | 0000 | FRANKLIN ST | NE | 5/29/14 | 50066 | 5A057 | (Light out) | DA 5/29/14 @ 1215am S Manning / D Northcraft pole 50066 - MUSE 10462 - Needs 400 powerdoor | High Pressure Sodium | 38.92553854000 | -77.00229041000
5/27/14 | 1137574 | 919 | T ST | NW | 5/27/14 | 13451 | 1L370 | (Light out) | DA 5/27/14 @ 1245am K Dunton / R Douglas repaired pole 13451 | High Pressure Sodium | 38.91563328000 | -77.02474424000
5/27/14 | 1137559 | 0 | SUNDERLAND PL | NW | 5/27/14 | 24522 | 2G779 | (Light out) | LM 5/27/14 Adric found New pole has been installed 4 feet from 24522 which has now been abandoned. Pole must be removed by contractor. 1050am DA 5/27/14 @ 245am A Buige pole 24522 No feed from underground to base refer to fault crew | High Pressure Sodium | 38.90796596000 | -77.04475549000
5/27/14 | 1137531 | 0 | ALLISON ST | NW | 5/27/14 | 4K101DC | 4U136DC | (Light out) | DA 5/26/14 @ 9345pm M Craig / J Peck repaired pole 4k101dc | High Pressure Sodium | 38.94511734000 | -77.02981962000
5/23/14 | 1137383 | 705 | ANACOSTIA AVE | NE | 5/23/14 | 72357DC | 7A480 | (Light out) | DA 5/23/14 @ 240am R Bush / M Brown repaired pole 72357dc - MUSE 11960 | High Pressure Sodium | 38.90177755000 | -76.95081946000
5/23/14 | 1137361 | 425 | I ST | NW | 5/23/14 | 60476 | 6B414 | (Light out) | DA 5/23/14 @ 110am J Brucksch / S Peters repaired pole 60476 repaired damaged wire in kit | High Pressure Sodium | 38.90138391000 | -77.01760653000
5/22/14 | 1137264 | 0 | M ST | NW | 5/28/14 | 23728 | 2U535 | (Light out) | DA 5/27/14 @ 1040pm J Brucksch / S Peters repaired pole 23728 - repaired wire in fixture complete | High Pressure Sodium | 38.90574873000 | -77.04183268000
5/22/14 | 1137177 | 0 | ALLISON ST | NW | 5/22/14 | 4K101DC | 4U136DC | (Light out) | DA 5/22/14 @ 115am M Criag / J Peck repaired pole 4k101dc | High Pressure Sodium | 38.94511734000 | -77.02981962000
5/22/14 | 1137113 | 3249 | STANTON RD | SE | 5/22/14 | 81744 | 88021 | (Light out) | DA 5/21/14 @ 1035pm R Douglas / K Dunton repaired pole 81744 | High Pressure Sodium | 38.84797185000 | -76.98118967000
5/22/14 | 1137111 | 0000 | OVERLOOK AVE | SW | 5/22/14 | 81839 | 88100 | (Light out) | DA 5/21/14 @ 10pm R Douglas / K Dunton repaired pole 81839 | High Pressure Sodium | 38.83246279000 | -77.01439370000
5/22/14 | 1137110 | 0000 | OVERLOOK AVE | SW | 5/22/14 | 81837 | 88098 | (Light out) | DA 5/21/14 @ 950pm R Douglas / K Dunton repaired pole 81837 | High Pressure Sodium | 38.83304530000 | -77.01393197000
5/22/14 | 1137096 | 0 | PATTERSON ST | NE | 5/22/14 | 61114 | 6U242 | (Light out) | DA 5/21/14 @ 940pm J Brucksch / S Peters repaired pole 61114 | High Pressure Sodium | 38.90641074000 | -77.00882448000
5/21/14 | 1137006 | 0 | ALLISON ST | NW | 5/21/14 | 4K101DC | 4U136DC | (Light out) | DA 5/21/14 @ 200am M Craig/ J Peck repaired pole 4k101dc | High Pressure Sodium | 38.94511734000 | -77.02981962000
5/19/14 | 1136847 | 1500 | TOBIAS DR | SE | 5/19/14 | 81710 | 87987 | (Light out) | DA 5/19/14 @ 945pm R Douglas / K Dunton inspected and tightend lamp pole 81710 - light on and working | High Pressure Sodium | 38.85014923000 | -76.98199197000
5/19/14 | 1136846 | 1424 | TOBIAS DR | SE | 5/19/14 | 81784 | 88061 | (Light out) | DA 5/19/14 @ 930pm R Douglas / K Dunton repaired pole 81784 | High Pressure Sodium | 38.85006791000 | -76.98302786000
5/19/14 | 1136822 | 0 | RICHARDSON PL | NW | 5/22/14 | 59924 | 5A412 | (Light out) | DA 5/21/14 @ 840pm R Bush / M Brown repaired pole 59924 DA 5/21/14 @ 125am S Manning / D Northcraft needs van - 14-00143725-The street light bulb was just replaced on May 10th and it worked up until the May 17th when it did not come on all night on th | High Pressure Sodium | 38.91306930000 | -77.01662788000
5/19/14 | 1136808 | 0000 | BLADENSBURG RD | NE | 5/20/14 | 50091 | 5M218 | (Light out) | DA 5/20/14 @ 151am S Manning / D Northcraft repaired pole 50091 | High Pressure Sodium | 38.92522195000 | -76.96493267000
5/16/14 | 1136503 | 705 | ANACOSTIA AVE | NE | 5/16/14 | 72357DC | 7A480 | (Light out) | DA 5/16/14 @ 106am R Bush / M Brown pole 72357dc - needs 400 fixture | High Pressure Sodium | 38.90177755000 | -76.95081946000
5/15/14 | 1136418 | 0 | PATTERSON ST | NE | 5/15/14 | 61114 | 6U242 | (Light out) | DA 5/15/14 @ 310am J Brucksch / S Peters pole 61114 | High Pressure Sodium | 38.90641074000 | -77.00882448000
5/14/14 | 1136217 | 1900 | 37TH ST | NW | 5/14/14 | 36891 | 30482 | (Light out) | DA 5/14/15 M Criag / J Peck repaired pole 36891 | High Pressure Sodium | 38.91672906000 | -77.07292654000
5/13/14 | 1136058 | 508 | MELLON ST | SE | 6/19/14 | 86496 | 8A358 | (Light out) | LM 6/19/14 Lloyd Pulled 40 feet 2" PVC, 300 feet of #8 wire, made splices in T-base & manhole. Pole is hot to the T-base but someone will have to energize the pole. 12pm. LM 5/20/14 Anthony found Break in duct. Tried in both directions multiple times. Re | High Pressure Sodium | 38.86233552000 | -77.00031519000
5/9/14 | 1135890 | 0 | INTERSTATE 395 | SW | 5/9/14 | 395-022N-9 | 395N612 | (Overhead guide sign light out) | LM 5/9/14 Keith REFER TO WO #113559 / MUSE #10229 | High Pressure Sodium | 38.88233608000 | -77.01846985000
5/9/14 | 1135822 | 3136 | 15TH PL | SE | 5/13/14 | 81712 | 87989 | (Light out) | DA 5/13/14 @ 1230am R Douglas / K Dunton repaired pole 81712 | High Pressure Sodium | 38.85063867000 | -76.98193762000
5/9/14 | 1135821 | 1500 | TOBIAS DR | SE | 5/13/14 | 81710 | 87987 | (Light out) | DA 5/13/14 @ 1220am R Douglas / K Dunton repaired pole 81710 | High Pressure Sodium | 38.85014923000 | -76.98199197000
5/9/14 | 1135788 | 4469 | WISCONSIN AVE | NW | 5/9/14 | 30131 | 3L465 | (Light out) | DA 5/9/14 R Fells repaired 30131 - complete | High Pressure Sodium | 38.94724720000 | -77.06516811000
5/8/14 | 1135704 | 0000 | MICHIGAN AVE | NE | 5/12/14 | 50071 | 2A058 | (Light out) | LM 5/1214 Rob Ran wire, 40 feet of #10 from manhole to the light. Made splices in manhole & T-base. Light now working 1255pm DA 5/11/14 @ 955pm S Manning / D Northcraft pole 50071 -NC @ Base refer to fault crew | High Pressure Sodium | 38.90029517000 | -77.03986681000
5/8/14 | 1135685 | 0 | KENILWORTH AVE | NE | 5/8/14 | 79489 | 7A158 | (Light out) | DA 5/7/14 J Brucksch/A Buige / S Peters - MOT -repaired pole 79489 - complete | High Pressure Sodium | 38.89044233000 | -76.95766327000
5/8/14 | 1135678 | 809 | EASTERN AVE | NE | 5/8/14 | 79475 | 7A139 | (Light out) | DA 5/7/14 J Brucksch/A Buige / S Peters - MOT -repaired pole 79475- complete | High Pressure Sodium | 38.88244563000 | -76.96384495000
5/8/14 | 1135622 | 0509 | 51ST ST | SE | 5/8/14 | 70072 | 7A054 | (Light out) | DA 5/8/14 R Bush / M Brown repaired pole 70072 | High Pressure Sodium | 38.88134505000 | -76.92951520000
5/8/14 | 1135577 | 2318 | 32ND ST | SE | 5/8/14 | 74838DC | 7A102DC | (Light out) | DA 5/8/14 @ 1002pm R Bush/ M Brown pole 74838dc light found on and working | High Pressure Sodium | 38.86110733000 | -76.96087329000
5/6/14 | 1135382 | 3200 | WISCONSIN AVE | NW | 5/7/14 | 38774 | 3U388 | (Light out) | DA 5/7/14 R Fell repaired pole 38774 - complete DA 5/6/14 R Fells pole 38774 - needs 400 powerdoor | High Pressure Sodium | 38.93433690000 | -77.07255580000
5/6/14 | 1135379 | 4469 | WISCONSIN AVE | NW | 5/6/14 | 30131 | 3L465 | (Light out) | DA 5/6/14 R Fells repaired pole 30131 - complete | High Pressure Sodium | 38.94724720000 | -77.06516811000
5/6/14 | 1135374 | 2001 | 20TH ST | NW | 5/6/14 | 23846 | 2A072 | (Light out) | DA 5/6/14 @ 142am A Buige repaired pole 23846 installed 400hps lamp | High Pressure Sodium | 38.90640579000 | -77.04498110000
5/5/14 | 1135333 | 0000 | UPSHUR ST | NW | 5/6/14 | 4R787 | 4G314 | (Light out) | DA 5/5/14 M Craig / J Peck repaired pole 4r787 14-00126820- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.94192544000 | -77.02607074000
5/2/14 | 1135101 | 0000 | NANNIE HELEN BURROUGHS AVE | NE | 5/2/14 | 70029 | 7A059 | (Light out) | DA 5/2/14 @ 210am R Douglas / K Dunton repaired pole 70029 | High Pressure Sodium | 38.89830988000 | -76.91657202000
5/1/14 | 1135056 | 1300 | BRENTWOOD RD | NE | 5/2/14 | 51354 | 5A258 | (Light out) | DA 5/1/14 @ 1103pm R Bush / M Brown repaired pole 51354 | High Pressure Sodium | 38.92186515000 | -76.98853396000
4/29/14 | 1134876 | 1331 | CONNECTICUT AVE | NW | 4/29/14 | 24528 | 2U495 | (Light out) | DA 4/29/14 @ 1255am J Brucksch / S Peters repaired pole 24528 - complete | High Pressure Sodium | 38.90805642000 | -77.04271948000
4/29/14 | 1134848 | 0 | 7TH ST | NW | 4/29/14 | 25659 | 6A800 | (Light out) | DA 4/28/14 J Brucksch / S Peters repaired pole 25659 - complete | High Pressure Sodium | 38.90822210000 | -77.02201697000
4/29/14 | 1134847 | 1300 | N ST | NW | 4/29/14 | 25599 | 6A792 | (Light out) | DA 4/28/14 J Brucksch / S Peters repaired pole 25599 - complete | High Pressure Sodium | 38.90730081000 | -77.02210992000
4/28/14 | 1134813 | 501 | NEW YORK AVE | NE | 4/28/14 | 56842 | 5A430 | (No current) |  | High Pressure Sodium | 38.91132939000 | -76.99721837000
4/28/14 | 1134812 | 515 | NEW YORK AVE | NE | 4/28/14 | 56841 | 5A428 | (No current) |  | High Pressure Sodium | 38.91151960000 | -76.99667276000
4/25/14 | 1134630 | 5220 | WISCONSIN AVE | NW | 4/25/14 | 3A084DC | 3A084 | (Light out) | DA 4/25/14 R Fell Repaired pole 3a084dc - complete | High Pressure Sodium | 38.95810245000 | -77.08423960000
4/22/14 | 1134252 | 4010 | SHEPHERD ST | NE | 4/23/14 | 51206DC | 52006DC | (Light out) | DA 4/23/14 @ 125am S Manning / D Northcraft repaired pole 51206dc | High Pressure Sodium | 38.93996002000 | -76.97564051000
4/18/14 | 1133904 | 0000 | TOBIAS DR | SE | 4/18/14 | 81793 | 88070 | (Light out) | DA 4/18/14 @ 320am R Douglas / K Dunton repaired pole 81793 | High Pressure Sodium | 38.85003251000 | -76.98126336000
4/18/14 | 1133903 | 3201 | STANTON RD | SE | 4/18/14 | 81792 | 88069 | (Light out) | DA 4/18/14 @ 250am R Douglas / K Dunton repaired pole 81792 | High Pressure Sodium | 38.84992639000 | -76.98111740000
| 1133814 | 401 | 51ST ST | SE | 4/18/14 | 70046 | 7A029 | (Light out) | DA4/17/14 @ 916pm R Bush / M Brown repaired pole 70046 secured globe 14-00105452-in the alley behind this address lamp light fixture is hanging dangerously cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.88264938000 | -76.92923070000
4/16/14 | 1133691 | 4611 | NORTH CAPITOL ST | NE | 4/17/14 | 4R755 | 4A796 | (No Current to Over Head) | LM 4/17/14 Damien Installed 200 feet of #6 Triplex cable, made 4 splices and all lights working LM 4/17/14 POLE #s are actually 4R754DC & 4R755DC | High Pressure Sodium | 38.94780081000 | -77.00876904000
4/15/14 | 1133606 | 3464 | DIX ST | NE | 4/16/14 | 70020 | 7A023 | (Light out) | DA 4/16/14 @ 145am R Bush / M Brown repaired pole 70020 installed 250hps lamp - complete | High Pressure Sodium | 38.89482319000 | -76.95519656000
4/15/14 | 1133538 | 1300 | BRENTWOOD RD | NE | 4/16/14 | 51354 | 5A258 | (Light out) | DA 4/15/14 Craig/ Peck repaired pole 51354 | High Pressure Sodium | 38.92186515000 | -76.98853396000
4/15/14 | 1133537 | 1300 | BRENTWOOD RD | NE | 4/17/14 | 51354 | 5A258 | (Light out) | DA 4/16/14 @ 1124pm S Manning / M Tomlin repaired pole 51354 installed 250hps lamp - complete | High Pressure Sodium | 38.92186515000 | -76.98853396000
4/15/14 | 1133536 | 1300 | BRENTWOOD RD | NE | 4/18/14 | 51354 | 5A258 | (Light out) | DA 7/17/14 W Black pole 51354 previously repaired refer to wo 1133537 | High Pressure Sodium | 38.92186515000 | -76.98853396000
4/15/14 | 1133524 | 0 | K ST | NE | 4/20/14 | 62263 | 6S399 | (Light out) | LM 4/18/14 Al Young found New construction that is incomplete in area (Traffic pole) poles aren't ready yet. DA 4/16/14 @ 10pm J Brucksch / S Peters pole 62263 -NC Underground - refer to fault crew | High Pressure Sodium | 38.90260245000 | -77.00544206000
4/14/14 | 1133408 | 3217 | CONNECTICUT AVE | NW | 4/15/14 | 30100 | 30427 | (Light out) | DA 4/15/14 @ 145am J Brucksch / S Peters can not locate pole number at lhis location request for map | High Pressure Sodium | 38.93294186000 | -77.05685295000
4/10/14 | 1133126 | 0 | SAYLES PL | SE | 4/14/14 | 81374DC | 88115 | (Light out) | DA 4/13/14 @ 915pm R Douglas / Dunton pole 81374dc this pole has been removed DA 4/11/14 R Douglas / Dunton pole 81374dc could not locate request for map | High Pressure Sodium | 38.86067966000 | -76.99269860000
4/9/14 | 1132887 | 314 | ST LOUIS ST | SE | 4/11/14 | 75280 | 75280DC | (Light out) | LM 4/11/14 Anthony found light is Not our pole, it's a temporary pole for construction site. DA 4/9/14 R Douglas / Dunton pole 75280 - NC Underground refer to fault crew | High Pressure Sodium | 38.88545489000 | -76.93271695000
4/9/14 | 1132861 | 0 | SHERIDAN RD | SE | 4/9/14 | 81363DC | 8M047 | (Light out) | DA 4/8/14 R Douglas / Dunton repaired pole 81363dc installed 400hps lamp - complete | High Pressure Sodium | 38.85928023000 | -76.99335324000
4/9/14 | 1132853 | 2022 | 14TH ST | SE | 4/9/14 | 80525 | 80525DC | (Light out) | DA 4/8/14 R Douglas / Dunton repaired pole 80525 installed 150hps lamp - complete | High Pressure Sodium | 38.86531307000 | -76.98537942000
4/8/14 | 1132788 | 1110 | 4TH ST | NW | 4/8/14 | 60423 | 6S485 | (Light out) | DA 4/8/14 @ 205am J Brucksch / S Peters repaired pole 60423 installed 250hps lamp- complete | High Pressure Sodium | 38.90322567000 | -77.01625282000
4/8/14 | 1132737 | 4519 | BENNING RD | NE | 4/8/14 | 77203 | 7A108 | (Light out) | DA 4/8/14 @ 1220am S Manning / M Tommlin repaired pole 77203 tightened lamp | High Pressure Sodium | 38.88952076000 | -76.93756179000
4/8/14 | 1132728 | 3221 | CONNECTICUT AVE | NW | 4/8/14 | 30101 | 30423 | (Light out) | DA 4/8/14 @ 109am M Craig / M Tomlin repaired pole 30101 installed 400hps lamp - complete | High Pressure Sodium | 38.93328522000 | -77.05704960000
4/3/14 | 1132338 | 3375 | WISCONSIN AVE | NW | 4/8/14 | 38775 | 3U386 | (Light out) | LM 4/8/14 Adric Made splice in vault in construction site. Light is working DA 4/3/14 R Fell pole 38775 NC Underground refer to fault crew | High Pressure Sodium | 38.93401705000 | -77.07253869000
4/2/14 | 1132100 | 0 | SHERIDAN RD | SE | 4/2/14 | 81356DC | 8U649 | (Light out) | DA 4/1/14 R Douglas / A Daiz repaired pole 81356dc | High Pressure Sodium | 38.85735331000 | -76.99328092000
4/2/14 | 1132098 | 0 | SHERIDAN RD | SE | 4/2/14 | 81363DC | 8M047 | (Light out) | DA 4/1/14 R Douglas / A Daiz repaired pole 81363dc | High Pressure Sodium | 38.85928023000 | -76.99335324000
4/2/14 | 1132097 | 0 | SHERIDAN RD | SE | 4/2/14 | 81365DC | 8M049 | (Light out) | DA 4/1/14 R Douglas / A Daiz repaired pole 81365dc | High Pressure Sodium | 38.85966279000 | -76.99341499000
4/1/14 | 1131987 | 1500 | KEARNEY ST | NE | 4/1/14 | 59986 | 5A177 | (Light out) | LM 4/1/14 Damien Made splice in manhole | High Pressure Sodium | 38.91401980000 | -77.01759054000
3/29/14 | 1131774 | 0 | BEECHER ST | NW | 3/31/14 | 36776 | 36776DC | (Light out) | DA 3/30/14 R Fell repaired pole 36776 14-00079529-STREET LIGHT ACROSS FROM THIS ADDRESS IS OUT cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92182285000 | -77.07457768000
3/28/14 | 1131700 | 1618 | 7TH ST | NW | 3/28/14 | 25652 | 6A825 | (Light out) | DA 3/27/14 A Buige / R Fike repaired pole 25652 | High Pressure Sodium | 38.91195512000 | -77.02201592000
3/27/14 | 1131580 | 0 | ANACOSTIA FWY | SE | 3/27/14 | 79494 | 7A147 | (Light out) | DA 3/26/14 J Brucksch / S Peters repaired pole 79494 | High Pressure Sodium | 38.88656390000 | -76.96255943000
3/27/14 | 1131579 | 0 | ANACOSTIA FWY | SE | 3/27/14 | 79493 | 7A146 | (Light out) | DA 3/26/14 J Brucksch / S Peters repaired pole 79493 repaired damaged wire in t base | High Pressure Sodium | 38.88732787000 | -76.96219078000
3/27/14 | 1131576 | 0 | KENILWORTH AVE | NE | 3/27/14 | 79463 | 7A127 | (Light out) | DA 3/26/14 J Brucksch / S Peters repaired pole 79463 | High Pressure Sodium | 38.88994563000 | -76.95813630000
3/27/14 | 1131563 | 1936 | EAST CAPITOL ST | NE | 3/27/14 | 63721 | 6M804 | (Light out) | DA 3/26/14 J Brucksch / S Peters repaired pole 63721 secured powerdoor | High Pressure Sodium | 38.88960987000 | -76.97672435000
3/26/14 | 1131515 | 1713 | 7TH ST | NW | 4/2/14 | 25650 | 6A833 | (Light out) | LM 4/2/14 Lloyd reconnected wires from pole in the vault. Used 2 hotlinks & made secondary taps LM 4/1/14 Damien refer to PEPCO>> no tails in PEPCO vault DA 3/27/14 A Buige / R Fike pole 25650 NC Underground refer to fault crew | High Pressure Sodium | 38.91300300000 | -77.02201369000
3/26/14 | 1131512 | 0 | 7TH ST | NW | 3/28/14 | 25698 | 6A803 | (Light off/on) | DA 3/27/14 A Buige / R Fike repaired pole 25698 | High Pressure Sodium | 38.90849059000 | -77.02177122000
3/26/14 | 1131488 | 0 | 33RD PL | NW | 3/31/14 | 37335 | 37735 | (Light out) | DA 3/31/14 R Fell repaired pole 37335 14-00076304-TWO WEEKS OUT cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.93133051000 | -77.06519402000
3/26/14 | 1131348 | 0000 | S ST | NW | 3/26/14 | 14381 | 1G600 | (Light out) | DA 3/26/14 R Bush / M Brown repaired pole 14381 (LED) | High Pressure Sodium | 38.91429425000 | -77.02127001000
3/25/14 | 1131243 | 0000 | S ST | NW | 3/25/14 | 14381 | 1G600 | (Light out) | DA 3/24/14 R Bush / M Brown repaired pole 14381 reset photocell on led | High Pressure Sodium | 38.91429425000 | -77.02127001000
3/23/14 | 1131110 | 5128 | SOUTHERN AVE | SE | 3/24/14 | 75493 | 75493DC | (Light out) | DA 3/23/14 R Douglas / A Diaz repaired pole 75493 14-00072021- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.87806339000 | -76.92900695000
3/23/14 | 1131104 | 900 | U ST | NW | 3/24/14 | 13983 | 1G551 | (Light out) | DA 3/23/14 A Buige / R Fike repaired pole 13983 | High Pressure Sodium | 38.91713116000 | -77.02591861000
3/23/14 | 1131103 | 0 | 12TH ST | NW | 3/24/14 | 13984 | 1G536 | (Light out) | DA 3/23/14 A Buige / R Fike repaired pole 13984 | High Pressure Sodium | 38.91686452000 | -77.02815086000
3/21/14 | 1130984 | 0 | ALLISON ST | NW | 3/21/14 | 4K101DC | 4U136DC | (Light out) | DA 3/20/14 M Craig / J Peck repaired pole 4K101DC | High Pressure Sodium | 38.94511734000 | -77.02981962000
3/16/14 | 1130619 | 1508 | TOBIAS DR | SE | 4/5/14 | 81713 | 87990 | (Light out) | G. Edwards completed on 4/5/14. Installed 15in t-base door. 14-00064410-the pole cover were the wire are at on the ground cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85037486000 | -76.98164018000
3/14/14 | 1130519 | 401 | 51ST ST | SE | 3/18/14 | 70046 | 7A029 | (Light out) | DA 3/18/14 R Douglas / A Diaz repaired pole 70046 | High Pressure Sodium | 38.88264938000 | -76.92923070000
3/14/14 | 1130518 | 5005 | F ST | SE | 3/19/14 | 70041 | 7A002 | (Light out) | DA 3/18/14 @ 1010pm R Douglas / Daiz repaired pole 70041 DA 3/18/14 R Douglas / A Diaz pole 70041 needs 250 hps fixture | High Pressure Sodium | 38.88176434000 | -76.92976826000
3/14/14 | 1130498 | 1154 | SUMNER RD | SE | 3/18/14 | 81566DC | 8A352 | (Light off/on) | DA 3/18/14 M Craig / J Peck repaired pole 81566dc | High Pressure Sodium | 38.86072349000 | -76.99691194000
3/13/14 | 1130424 | 4625 | 13TH ST | NW | 3/19/14 | 4K417 | 4U123 | (Light out) | DA 3/19/14 @ 1225am M Craig / J Peck repaired pole 4k417 14-00061966-Streetlight Repair 1284-1298 Crittenden Street Northwest, Washington, DC 20011, USA cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94669824000 | -77.02961658000
3/12/14 | 1130178 | 3641 | BANGOR ST | SE | 3/13/14 | 74815DC | 7A087DC | (Light out) | DA 3/12/14 Douglas/Diaz repaired pole 74815dc 14-00059342-light goes off and on cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.86030331000 | -76.95456197000
3/7/14 | 1129749 | 0 | GARFIELD ST | NW | 3/10/14 | 35100 | 3A377 | (Light out) | DA 3/9/14 R Fell repaired pole 35100 14-00054486-Streetlight Repair 2807 27th Street Northwest, Washington, DC 20008, USA Light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92674181000 | -77.05525746000
3/6/14 | 1129534 | 1509 | TUBMAN RD | SE | 3/6/14 | 81803 | 88080 | (Light out) | DA 3/5/14 Bush/ Brown repaired pole 81803 tightened lose globe and fixture | High Pressure Sodium | 38.84827859000 | -76.98210715000
3/6/14 | 1129533 | 1501 | TUBMAN RD | SE | 3/6/14 | 81740 | 88017 | (Light out) | DA 3/5/14 Bush/ Brown repaired pole 81740 | High Pressure Sodium | 38.84805233000 | -76.98250059000
2/28/14 | 1129272 | 3156 | BLADENSBURG RD | NE | 3/4/14 | 51231DC | 5A127DC | (Light out) | LM 3/4/14 Anthony installed 250 lamp | High Pressure Sodium | 38.92863144000 | -76.96109161000
2/28/14 | 1129248 | 1306 | L ST | SE | 3/5/14 | 66199 | 6U007 | (Light out) | WBlack on abandoned old 695 freeway and is unreachable due to construction. | High Pressure Sodium | 38.87748181000 | -76.98785343000
2/26/14 | 1129008 | 4400 | GEORGIA AVE | NW | 2/28/14 | 4K024 | 4G309 | (Light out) | DA 2/27/14 M Craig/J Peck repaired pole 4k024 | High Pressure Sodium | 38.94410262000 | -77.02599601000
2/26/14 | 1128869 | 0000 | NANNIE HELEN BURROUGHS AVE | NE | 2/26/14 | 70029 | 7A059 | (Light out) | DA 2/25/14 Douglas repaired pole 70029 | High Pressure Sodium | 38.89830988000 | -76.91657202000
| 1128694 | 1412 | 33RD ST | NW | 2/27/14 | 20731 | 2G186 | (Light out) | DA 2/26/14 T Buige repaired pole 20731repaired shorted wires in powerdoor 14-00043301- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90826387000 | -77.06601588000
2/24/14 | 1128622 | 1700 | 3RD ST | NW | 2/26/14 | 59992 | 5A183 | (Light out) | DA 2/25/14 S Manning/ M Thomas all lights found on and working | High Pressure Sodium | 38.91426862000 | -77.01583923000
2/24/14 | 1128613 | 0 | 7TH ST | NW | 2/24/14 | 22409 | 6M688 | (Light out) | DA 2/23/14 J BRucksch repaired pole 22409 (400 teardrop starter ) | High Pressure Sodium | 38.90199325000 | -77.02201951000
2/24/14 | 1128596 | 803 | EASTERN AVE | NE | 2/24/14 | 79471 | 7A135 | (Light out) | DA 2/23/14 R Fell repaired pole 79471 | High Pressure Sodium | 38.88055222000 | -76.96517808000
2/24/14 | 1128587 | 0 | LEE ST | NE | 2/24/14 | 70327 | 7M082 | (Light out) | DA 2/23/14 R Fell repaired pole 70327 | High Pressure Sodium | 38.90317749000 | -76.94336293000
2/24/14 | 1128584 | 809 | INTERSTATE 295 | NE | 2/24/14 | 79474 | 7A138 | (Light out) | DA 2/23/14 R Fell repaired 79474 | High Pressure Sodium | 38.88176234000 | -76.96414383000
2/24/14 | 1128583 | 809 | EASTERN AVE | NE | 2/24/14 | 79475 | 7A139 | (Light out) | DA 2/23/14 R Fell repaired 79575 | High Pressure Sodium | 38.88244563000 | -76.96384495000
2/20/14 | 1128370 | 0 | 22ND ST | NW | 2/20/14 | 28304 | 2M295 | (Light out) | LM 2/20/14 Damien installed a nightwachman | High Pressure Sodium | 38.90133435000 | -77.04875951000
2/20/14 | 1128287 | 0 | FERN PL | NW | 2/20/14 | 4D591DC | 4D891DC | (Light out) | DA 2/19/14 M Craig repaired pole 4d591dc | Incandescent | 38.97836028000 | -77.02202042000
2/19/14 | 1128172 | 775 | H ST | NE | 2/19/14 | 61991 | 6S197 | (Light out) | DA 2/1914 Busch repaired pole 61991 | High Pressure Sodium | 38.90030060000 | -76.99586046000
2/16/14 | 1127969 | 1900 | 37TH ST | NW | 2/16/14 | 36891 | 30482 | (Light out) | DA 2/16/14 R Fell repaired pole 36891 | High Pressure Sodium | 38.91672906000 | -77.07292654000
2/11/14 | 1127790 | 0 | 13TH ST | NW | 2/11/14 | 4K416DC | 4U119DC | (Light out) | DA 2/10/14 M Craig repaired pole 4K416dc | High Pressure Sodium | 38.94716466000 | -77.02979020000
2/10/14 | 1127750 | 0 | 7TH ST | NW | 2/16/14 | 25706 | 6A832 | (Light out) | DA 2/16/14 J Brucksch repaired pole 25706 | High Pressure Sodium | 38.91270444000 | -77.02180700000
2/7/14 | 1127650 | 600 | 5TH ST | NW | 2/17/14 | 60549 | 6S584 | (Light out) | DA 2/17/14 Fike/Diaz repaired pole 60549 14-00028967-Cobra type cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89787642000 | -77.01979899000
2/7/14 | 1127643 | 0 | NEW YORK AVE | NE | 2/7/14 | 50007 | 5A041 | (Light out) | DA 2/5/14 K Greenfield repaired pole 50007 | High Pressure Sodium | 38.91727852000 | -76.96718437000
2/7/14 | 1127635 | 0 | NEW YORK AVE | NE | 2/7/14 | 50003 | 5A037 | (Light out) | DA 2/5/14 K Greenfield repaired pole 50003 | High Pressure Sodium | 38.91737165000 | -76.96995714000
2/7/14 | 1127631 | 501 | NEW YORK AVE | NE | 2/17/14 | 56842 | 5A430 | (Light out) | See W.O.1126108 (No current surface with cut) 56842 DA 2/5/14 K Greenfield pole 56842 NC Underground | High Pressure Sodium | 38.91132939000 | -76.99721837000
| 1127605 | 0 | SOUTH CAPITOL ST | SE | 2/12/14 | 65304 | 6A046 | (Light out) | DA 2/11/14 Fike/Diaz repaired pole 65304 14-00028883-metal pole cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88155197000 | -77.00892933000
2/1/14 | 1127351 | 3641 | BANGOR ST | SE | 2/4/14 | 74815DC | 7A087DC | (Light out) | DA 1/3/14 K Greenfield repaired pole 74815dc 14-00023802- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86030331000 | -76.95456197000
1/31/14 | 1127350 | 0 | SOUTH DAKOTA AVE | NE | 2/1/14 | 4P562 | 4P566 | (Light out) | DA 1/31/14 Fike/Diaz repaired pole 4p562 complete | High Pressure Sodium | 38.95662010000 | -77.00177320000
1/31/14 | 1127323 | 0 | PATTERSON ST | NE | 2/24/14 | 61261 | 6A274 | (Light out) | LM 2/24/14 Damien Poles are part of an ongoing project, adequate lighting is supplied close out LM 2/19/14 Adric Pole is recessing asfault unable to rod DA 2/16/14 J Brucksch pole 61261 NC Underground refer to fault crew | High Pressure Sodium | 38.90650714000 | -77.00604658000
1/31/14 | 1127322 | 1222 | 1ST ST | NE | 2/19/14 | 61245 | 6A276 | (Light out) | LM 2/19/14 Made splice in T-Base DA 2/17/14 J Burcksch pole 61245 NC Underground refer to fault crew | High Pressure Sodium | 38.90699632000 | -77.00596394000
1/31/14 | 1127250 | 454 | I ST | NW | 2/25/14 | 61059 | 6A740 | (Light out) | LM 2/25/14 Greg insalled base door DA 2/16/14 T Buige repaired pole 61059 missing access cover | High Pressure Sodium | 38.90185344000 | -77.01769222000
1/30/14 | 1127050 | 2601 | BOWEN RD | SE | 2/11/14 | 81362DC | 88102 | (Light out) | DA 2/10/14 K Greenfield repaired pole 81362dc made taps to secondary DA 2/9/14 K Greenfield request for map | High Pressure Sodium | 38.85890249000 | -76.99330089000
| 1126977 | 4500 | EAST CAPITOL ST | SE | 2/24/14 | 70052 | 7A035 | (Light out) | LM 2/24/14 Wayne Installed cable in manhole to T-base 50' #10 EM 2/17/14 Jeremiah Lancaster. Need MOT, manhole in middle of road. DA 1/3/14 K Greenfield pole 70052 NC Underground refer to fault crew - NO CURRENT PENDING 14-00021780- cwDesc: STREETLIGH | High Pressure Sodium | 38.88960932000 | -76.93729068000
1/29/14 | 1126920 | 0 | MARYLAND AVE | NE | 2/12/14 | 59542 | 5M248 | (Light out) | LM 2/12/14 Adric found lights working properly DA 1/31/14 Fike/Diaz pole 59542 has No underground current refer to fault crew- NO CURRENT PENDING 14-00020859-pole is rotten, and light bulb needs to be replaced This pole have been called in before b | High Pressure Sodium | 38.90066776000 | -76.98240388000
1/28/14 | 1126807 | 0 | SEDGWICK ST | NW | 1/31/14 | 30008DC | 3A368DC | (Light out) | DA 1/30/14 R Fells repaired repaired pole 30008dc 14-00020314-Street light is out. Nothing else cwDesc: STREETLIGHT REPAIR | Incandescent | 38.94040143000 | -77.09254074000
1/28/14 | 1126766 | 0 | IOWA AVE | NW | 1/31/14 | 4K496 | 4U128 | (Light out) | DA 1/31/14 Fike/Diaz repaired pole 4k496 14-00019462-PLEASE REPLACE LIGHT BULB. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94605354000 | -77.02957834000
1/28/14 | 1126765 | 0 | 13TH ST | NW | 1/30/14 | 4K432 | 4U146 | (Light out) | DA 1/29/14 Fike/Diaz repaired pole 4k432 complete 14-00019461-PLEASE REPLACE LIGHT BULB. ON WEST SIDE OF STREET cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94308499000 | -77.02978871000
| 1126691 | 1516 | 7TH ST | NW | 2/10/14 | 25655 | 6A524 | (Light out) | DA 2/9/14 T Buige repaired pole 25655 DA 2/3/14 M Craig pole 25655 needs 400 powerdoor 14-00018270- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91044053000 | -77.02202127000
| 1126568 | 45 | L ST | NE | 1/31/14 | 61204 | 6A244 | (Light out) | DA 1/30/14 K Greenfield repaired pole 61204 14-00015334-IN THE REAR OF THE HOUSE THE LIGHT IS OUT. CAME OUT ONCE BUT LIGHT STAYED ON FOR 3 DAYS cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90379039000 | -77.00717091000
1/21/14 | 1126543 | 1530 | 11TH ST | NW | 1/24/14 | 25286 | 2U045 | (Light out) | DA 1/23/14 M Craig repaired pole 25286 - complete 14-00014577-Street light on the SW corner is out. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91105847000 | -77.02715860000
1/18/14 | 1126467 | 4202 | BENNING RD | NE | 2/18/14 | 73867DC | 73867 | (Light out) | DA 2/17/14 K Greenfield repaired pole 73867dc reinstalled teardrop fixture DA 2/16/14 Fike /Diaz teardrop fixture taken back to shop for repairs DA 1/20/14 K Greenfield pole 73867dc and pepco pole #6385278 - both teardrop fixture with high voltage of | High Pressure Sodium | 38.89298310000 | -76.94251439000
1/17/14 | 1126437 | 0000 | OVERLOOK AVE | SW | 1/24/14 | 81834 | 88095 | (Light out) | DA 1/23/14 K Greenfield repaired pole 81834 - complete 14-00013500-streetlights are too dark at night cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.83393831000 | -77.01328820000
1/17/14 | 1126400 | 0 | 7TH ST | NW | 1/24/14 | 25656 | 6U467 | (Light out) | DA 1/23/14 M Craig repaired pole 25656 - complete | High Pressure Sodium | 38.90956587000 | -77.02202768000
| 1126296 | 5127 | H ST | SE | 1/17/14 | 75492 | 75492DC | (Light out) | DA 1/16/14 K Greenfield poles 75492 and 75494 complete Alley 14-00012467-At least 2 alley lights are out. One directly behind this address. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.87810752000 | -76.92948653000
1/16/14 | 1126278 | 0000 | H ST | NE | 1/16/14 | 68255DC | 68255 | (Light out) | DA 1/15/14 J Lancaster pole 48255dc complete | High Pressure Sodium | 38.90037863000 | -77.00528191000
1/16/14 | 1126271 | 0000 | H ST | NE | 1/16/14 | 68246DC | 68246 | (Light out) | DA 1/15/14 J Lancaster pole 48246dc complete | High Pressure Sodium | 38.90004454000 | -77.00552357000
| 1126151 | 1403 | KEARNEY ST | NW | 1/31/14 | 59990 | 5A182 | (Light out) | DA 1/30/14 K Greenfield pole 59990 found okay 14-00010645- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91424947000 | -77.01606264000
1/14/14 | 1126121 | 1457 | BRUCE PL | SE | 1/16/14 | 81728 | 88005 | (Light off/on) | DA 1/15/14 McDuffie pole 81728 complete | High Pressure Sodium | 38.85000110000 | -76.98366929000
1/14/14 | 1126108 | 501 | NEW YORK AVE | NE |  | 56842 | 5A430 | (No current) | LM 2/5/14 Tony breakdown in conduit 31' EAST from the pole #56842 / see attached map LM 2/4/14 Tony Need a plact to determine the direction of the feed into the conduit DA 1/13/14 J Lancaster pole 56842 NC Underground NO CURRENT PENDING | High Pressure Sodium | 38.91132939000 | -76.99721837000
1/14/14 | 1126094 | 0 | NEW YORK AVE | NE | 1/14/14 | 50009 | 5A043 | (Light out) | DA 1/13/14 J Lancaster pole #50009 needs 400 powerdoor | High Pressure Sodium | 38.91719217000 | -76.96575011000
1/13/14 | 1126053 | 1807 | MARTIN LUTHER KING JR AVE | SE | 1/14/14 | 81019 | 8L851 | (Light out) | DA 1/13/14 K GRenfield pole 81019 complete 14-00008953-Replace light bulb cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86789068000 | -76.98847973000
1/9/14 | 1125866 | 5504 | D ST | SE | 1/10/14 | 75506 | 75506DC | (Light out) | DA 1/9/14 K Greenfield repaired pole #75506 | High Pressure Sodium | 38.88245663000 | -76.92287061000
1/9/14 | 1125830 | 0 | D ST | SW | 1/15/14 | 21625 | 6L714 | (Light out) | DA 1/14/14 M Craig pole 21625 complete | High Pressure Sodium | 38.88478652000 | -77.01928219000
| 1125720 | 7051 | SPRING PL | NW | 1/9/14 | 4H522DC | 4H522 | (Light out) | DA 1/8/14 J Lancaster repaired pole #4H522DC and 4H523DC 14-00005098-I'm not sure about the street identifiers requested (quadrant, etc.), but the Blair road address is the front side of the apartment building, but both street lights are out in the bac | Incandescent | 38.97614004000 | -77.01896257000
1/6/14 | 1125576 | 4469 | WISCONSIN AVE | NW | 1/7/14 | 30131 | 3L465 | (Light out) | DA 1/6/14 R Fells repaired pole #30131 14-00002676- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.94724720000 | -77.06516811000
1/2/14 | 1125458 | 206 | RHODE ISLAND AVE | NW | 1/6/14 | 59996 | 5A188 | (Light out) | DA 1/5/14 G McDuffie repaired pole #59996 14-00000316- cwDesc: STREETLIGHT REPAIR | Incandescent | 38.91473859000 | -77.01463730000
12/24/13 | 1125004 | 0 | CAMDEN ST | SE | 12/27/13 | 74758DC | 7A072DC | (Light out) | DA 12/26/13 K Greenfield repaired pole #74758dc 13-00286627-light is on the corner cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85947585000 | -76.95854009000
| 1124955 | 1101 | BRENTWOOD RD | NE | 12/31/13 | 56626DC | 5A242 | (Light out) | DA 12/30/13 G McDuffie repaired pole #56626dc 13-00296500- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91899930000 | -76.99156802000
12/23/13 | 1124882 | 0 | NEW YORK AVE | NE | 1/14/14 | 50006 | 5A040 | (Light out) | DA 1/13/14 J Lancaster light on and working | High Pressure Sodium | 38.91731218000 | -76.96789154000
12/23/13 | 1124881 | 0 | NEW YORK AVE | NE | 1/14/14 | 50003 | 5A037 | (Light out) | DA 1/13/14 J Lancaster light on and working | High Pressure Sodium | 38.91737165000 | -76.96995714000
12/23/13 | 1124861 | 501 | NEW YORK AVE | NE | 1/14/14 | 56842 | 5A430 | (Light out) | DA 1/13/14 J Lancaster light on and working | High Pressure Sodium | 38.91132939000 | -76.99721837000
12/23/13 | 1124851 | 3156 | BLADENSBURG RD | NE | 12/27/13 | 51231DC | 5A127DC | (Light out) | DA 12/26/13 G. McDuffie repaired pole #51231dc | High Pressure Sodium | 38.92863144000 | -76.96109161000
12/17/13 | 1124521 | 0 | KENILWORTH AVE | NE | 12/17/13 | 72418 | 7M094 | (Light out) | RD - Nov. 15, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 72418 | High Pressure Sodium | 38.90197307000 | -76.94478816000
12/17/13 | 1124515 | 0 | KENILWORTH AVE | NE | 12/17/13 | 72424 | 7M100 | (Light out) | MJ - Nov. 15, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 72424 | High Pressure Sodium | 38.90030476000 | -76.94672537000
12/17/13 | 1124504 | 3901 | PENNSYLVANIA AVE | SE | 12/17/13 | 78529DC | 7E130DC | (Light out) | RW - Nov. 15, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 78529DC | High Pressure Sodium | 38.86627511000 | -76.95318058000
12/17/13 | 1124489 | 711 | ANACOSTIA AVE | NE | 12/17/13 | 72358DC | 7A481 | (Light out) | RD - Nov. 15, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 72358DC | High Pressure Sodium | 38.90197539000 | -76.95056600000
12/17/13 | 1124468 | 0000 | OVERLOOK AVE | SE | 12/17/13 | 81815 | 88088 | (Light out) | FT - Nov. 16, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81815 | High Pressure Sodium | 38.83154015000 | -77.01497801000
12/17/13 | 1124466 | 3237 | STANTON RD | SE | 12/17/13 | 81798 | 88075 | (Light out) | MJ - Nov. 16, 2013. Replaced photocell. 100% complete. Repaired pole number 81798 | High Pressure Sodium | 38.84851465000 | -76.98100550000
12/17/13 | 1124434 | 1512 | TOBIAS DR | SE | 12/17/13 | 81714 | 87991 | (Light out) | MJ - Nov. 16, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 81714 | High Pressure Sodium | 38.85019660000 | -76.98144001000
12/17/13 | 1124415 | 1516 | SHIPPEN LN | SE | 12/17/13 | 81718 | 87995 | (Light out) | FT - Nov. 16, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81718 | High Pressure Sodium | 38.84937674000 | -76.98141962000
12/17/13 | 1124353 | 0 | OVERLOOK AVE | SW | 12/17/13 | 82101 | 82091 | (Light out) | FT - Nov. 18, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 82101 | High Pressure Sodium | 38.83804032000 | -77.01026127000
12/17/13 | 1124346 | 0000 | OVERLOOK AVE | SE | 12/17/13 | 81805 | 85792 | (Light out) | RD - Nov. 18, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81805 | High Pressure Sodium | 38.82939638000 | -77.01717209000
12/17/13 | 1124287 | 0000 | ROBINSON ST | SE | 12/17/13 | 81756 | 88033 | (Light out) | RD - Nov. 14, 2106. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81756 | High Pressure Sodium | 38.84997435000 | -76.98416955000
12/17/13 | 1124263 | 0 | INTERSTATE 295 | SE | 12/17/13 | 86521 | 8L857 | (Light out) | MJ - Nov. 14, 2082. Replaced HPS lamp. 100% completed. Repaired pole number 86521 | High Pressure Sodium | 38.86851926000 | -76.98829110000
12/17/13 | 1124259 | 2500 | SHERIDAN RD | SE | 12/17/13 | 81367DC | 8M053 | (Light out) | RW - Nov. 14, 2078. Replaced HPS lamp. 100% completed. Repaired pole number 81367DC | High Pressure Sodium | 38.86029651000 | -76.99351508000
12/17/13 | 1124257 | 3215 | HENSON RD | SE | 12/17/13 | 81791 | 88068 | (Light out) | MJ - Nov. 14, 2076. Replaced photocell. 100% complete. Repaired pole number 81791 | High Pressure Sodium | 38.84953994000 | -76.98294254000
12/16/13 | 1124200 | 1509 | TUBMAN RD | SE | 12/16/13 | 81741 | 88018 | (Light out) | RW - Nov. 14, 2038. Replaced HPS lamp. 100% completed. Repaired pole number 81741 | High Pressure Sodium | 38.84803773000 | -76.98221565000
12/16/13 | 1124165 | 2606 | BOWEN RD | SE | 12/16/13 | 81376DC | 88117 | (Light out) | RD - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81376DC | High Pressure Sodium | 38.86028724000 | -76.99280196000
12/16/13 | 1124131 | 1546 | ALABAMA AVE | SE | 12/16/13 | 81747 | 88024 | (Light out) | RW - Nov. 14, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 81747 | High Pressure Sodium | 38.84710965000 | -76.98107212000
12/16/13 | 1124090 | 0 | SHERIDAN RD | SE | 12/16/13 | 81356DC | 8U649 | (Light out) | RD - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81356DC | High Pressure Sodium | 38.85735331000 | -76.99328092000
12/13/13 | 1124012 | 1230 | SUMNER RD | SE | 12/13/13 | 81565DC | 8A351 | (Light out) | RW - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81565DC | High Pressure Sodium | 38.86063641000 | -76.99700502000
12/13/13 | 1124004 | 0 | SHERIDAN RD | SE | 12/13/13 | 81353DC | 8U654 | (Light out) | RD - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81353DC | High Pressure Sodium | 38.85641207000 | -76.99331957000
12/13/13 | 1123997 | 0 | SAYLES PL | SE | 12/13/13 | 81374DC | 88115 | (Light out) | FT - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81374DC | High Pressure Sodium | 38.86067966000 | -76.99269860000
12/13/13 | 1123969 | 3943 | PENNSYLVANIA AVE | SE | 12/13/13 | 78579DC | 7E003DC | (Light out) | RD - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 78579DC | High Pressure Sodium | 38.86417025000 | -76.94760339000
12/13/13 | 1123898 | 3641 | BANGOR ST | SE | 12/13/13 | 74815DC | 7A087DC | (Light out) | MJ - Nov. 15, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 74815DC | High Pressure Sodium | 38.86030331000 | -76.95456197000
12/13/13 | 1123892 | 625 | BURNS ST | SE | 12/13/13 | 76071 | 76071DC | (Light out) | FT - Nov. 15, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 76071 | High Pressure Sodium | 38.88020983000 | -76.94386284000
12/13/13 | 1123888 | 4000 | SOUTHERN AVE | SE | 12/13/13 | 78576 | 78576DC | (Light out) | RD - Nov. 15, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 78576 | High Pressure Sodium | 38.86379385000 | -76.94657249000
12/13/13 | 1123867 | 300 | EASTERN AVE | NE | 12/13/13 | 70026 | 72855 | (Light out) | RD - Nov. 16, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 70026 | High Pressure Sodium | 38.89394625000 | -76.91101330000
12/13/13 | 1123861 | 5335 | B ST | SE | 12/13/13 | 75564 | 75564DC | (Light out) | FT - Nov. 16, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 75564 | High Pressure Sodium | 38.88622800000 | -76.92459483000
12/13/13 | 1123853 | 5336 | CALL PL | SE | 12/13/13 | 75598 | 75598DC | (Light out) | MJ - Nov. 16, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 75598 | High Pressure Sodium | 38.88354836000 | -76.92520818000
12/13/13 | 1123850 | 4012 | PENNSYLVANIA AVE | SE | 12/13/13 | 78578DC | 7E001DC | (Light out) | RW - Nov. 16, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 78578DC | High Pressure Sodium | 38.86391627000 | -76.94694320000
12/13/13 | 1123830 | 723 | BARNES ST | NE | 12/13/13 | 72463DC | 7A472 | (Light out) | MJ - Nov. 16, 2013. Replaced photocell. 100% complete. Repaired pole number 72463DC | High Pressure Sodium | 38.90181026000 | -76.94988632000
12/12/13 | 1123753 | 4815 | TEXAS AVE | SE | 12/12/13 | 76840 | 76940 | (Light out) | MJ - Nov. 18, 2013. Replaced photocell. 100% complete. Repaired pole number 76840 | High Pressure Sodium | 38.88952535000 | -76.93806998000
12/12/13 | 1123742 | 5901 | CENTRAL AVE | SE | 12/12/13 | 75520 | 75520DC | (Light out) | MJ - Nov. 18, 2013. Replaced photocell. 100% complete. Repaired pole number 75520 | High Pressure Sodium | 38.88563104000 | -76.91846228000
12/12/13 | 1123688 | 2427 | MINNESOTA AVE | SE | 12/12/13 | 70076 | 80098 | (Light out) | MJ - Nov. 18, 2013. Replaced photocell. 100% complete. Repaired pole number 70076 | High Pressure Sodium | 38.87320803000 | -76.97100322000
12/12/13 | 1123620 | 0000 | S ST | NW | 12/19/13 | 14384 | 1G603 | (Light out) | DA 12/19/13 @ 143am G McDuffie/ T Buige repaired pole #14384 | High Pressure Sodium | 38.91499293000 | -77.02126455000
12/12/13 | 1123619 | 0000 | S ST | NW | 12/19/13 | 14383 | 1G602 | (Light out) | DA 12/19/13 @ 139am G McDuffie/ T Buige repaired pole #14383 | High Pressure Sodium | 38.91475323000 | -77.02126679000
12/12/13 | 1123618 | 600 | S ST | NW | 12/19/13 | 14382 | 1G601 | (Light out) | DA 12/19/13 @ 133am G McDuffie/ T Buige repaired pole #14382 | High Pressure Sodium | 38.91444559000 | -77.02127006000
12/12/13 | 1123617 | 0000 | S ST | NW | 12/19/13 | 14381 | 1G600 | (Light out) | DA 12/19/13 @ 133am G McDuffie/ T Buige pole #14381 LED lights on and working | High Pressure Sodium | 38.91429425000 | -77.02127001000
12/10/13 | 1123560 | 1101 | CONNECTICUT AVE | NW | 12/11/13 | 27217 | 2U560 | (Light out) | RW-12/10/13-REPLACED LAMP POLE 27217 | High Pressure Sodium | 38.90409324000 | -77.04001398000
12/10/13 | 1123549 | 0 | 18TH ST | NW | 12/11/13 | 24534 | 2U529 | (Light out) | RW-12/10/13-REPLACED LAMP POLE 24534 | High Pressure Sodium | 38.90591907000 | -77.04143681000
12/10/13 | 1123548 | 0 | M ST | NW | 12/11/13 | 23728 | 2U535 | (Light out) | RW-12/10/13-REPLACED LAMP POLE 23728 | High Pressure Sodium | 38.90574873000 | -77.04183268000
12/10/13 | 1123547 | 1218 | CONNECTICUT AVE | NW | 12/11/13 | 24532 | 2U519 | (Light out) | RW-12/10/13-REPLACED LAMP POLE 24532 | High Pressure Sodium | 38.90651643000 | -77.04185036000
12/10/13 | 1123528 | 1270 | NEW HAMPSHIRE AVE | NW | 1/29/14 | 23873 | 2G758 | (Light out) | RW-12/10/13-NO CURRENT POLE 23873 EM-12/30/13-No current from manhole, added temporaroy light for block | High Pressure Sodium | 38.90672638000 | -77.04606427000
12/10/13 | 1123527 | 1307 | NEW HAMPSHIRE AVE | NW | 12/11/13 | 24481 | 2G770 | (Light out) | RW-12/10/13-REPLACED LAMP POLE 24481 | High Pressure Sodium | 38.90814384000 | -77.04473348000
12/4/13 | 1123389 | 0 | CAMDEN ST | SE | 12/9/13 | 74756DC | 7A070DC | (Light out) | Jose Aguilar at 12/9/2013 12:20:52 PM: replaced 250 W HPS Power door ... now the light works 100% NEED 250W POWER DOOR 13-00284013-The streetlight nearest the alley in the 3300 block of Camden Street, S. E., is out and needs to be replaced. The locat | High Pressure Sodium | 38.85947622000 | -76.95961031000
11/27/13 | 1123041 | 0 | EAST CAPITOL ST | NE | 12/6/13 | 63629 | 6M837 | (Light out) | Kenneth Bryant at 11/30/2013 11:07:28 AM: replace light bulb 400w and photocell 100% | High Pressure Sodium | 38.88956256000 | -76.97418443000
11/26/13 | 1122993 | 775 | H ST | NE | 11/28/13 | 61991 | 6S197 | (Light out) | RODNEY-11-27-2013-9:35-REPLACED 400 HPS LAMP FOR POLE 61991 | High Pressure Sodium | 38.90030060000 | -76.99586046000
| 1122925 | 467 | NEW YORK AVE | NW | 11/30/13 | 25925 | 6A529 | (Light out) | Tony-11-29-2013-11:15pm. Power door is ok. replaced 400 w lamp for pole 25925 RW-11/27/13-NEED 400W POWER DOOR 13-00278899-Streetlight Repair 460 New York Ave. NW 20001 This issue has an image. You can view it here http://seeclickfix.com/issues/83 | High Pressure Sodium | 38.90424380000 | -77.01844811000
| 1122909 | 2800 | BLADENSBURG RD | NE | 11/26/13 | 50098 | 5A084 | (Light out) | RW-11/25/13-REPLACED LAMP POLE 50098 Rear 13-00278759- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.92696727000 | -76.96279437000
11/20/13 | 1122582 | 2311 | 33RD ST | SE | 11/20/13 | 74837DC | 7A101DC | (Light out) | RW - Nov. 14, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 74837DC | High Pressure Sodium | 38.86135172000 | -76.96056260000
11/20/13 | 1122579 | 3407 | MINNESOTA AVE | SE | 11/20/13 | 76578DC | 7S023 | (Light out) | FT - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 76578DC | High Pressure Sodium | 38.88422000000 | -76.95717076000
11/20/13 | 1122558 | 0 | BENNING RD | NE | 11/20/13 | 74692DC | 5M294 | (Light out) | RW - Nov. 14, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 74692DC | High Pressure Sodium | 38.89761355000 | -76.96693872000
11/20/13 | 1122546 | 1000 | KENILWORTH AVE | NE | 11/20/13 | 70324 | 7M023 | (Light out) | FT - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 70324 | High Pressure Sodium | 38.90351786000 | -76.94253181000
11/19/13 | 1122465 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 11/19/13 | 71269 | 7A201 | (Light out) | MJ - Nov. 14, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 71269 | High Pressure Sodium | 38.89826963000 | -76.92624974000
11/19/13 | 1122425 | 0 | KENILWORTH AVE | NE | 11/19/13 | 72427 | 7M104 | (Light out) | MJ - Nov. 14, 2013. Replaced photocell. 100% complete. Repaired pole number 72427 | High Pressure Sodium | 38.89924990000 | -76.94806704000
11/19/13 | 1122392 | 5340 | NANNIE HELEN BURROUGHS AVE | NE | 11/19/13 | 72642DC | 7A193 | (Light out) | FT - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 72642DC | High Pressure Sodium | 38.89843570000 | -76.92357000000
11/19/13 | 1122386 | 0 | KENILWORTH AVE | NE | 11/19/13 | 72420 | 7M096 | (Light out) | RW - Nov. 14, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 72420 | High Pressure Sodium | 38.90152728000 | -76.94525169000
11/19/13 | 1122351 | 926 | T ST | NW | 11/19/13 | 13450 | 1L367 | (Light out) | MJ - Nov. 15, 2013. Replaced photocell. 100% complete. Repaired pole number 13450 | High Pressure Sodium | 38.91552698000 | -77.02529625000
11/19/13 | 1122320 | 1000 | KENYON ST | NW | 11/19/13 | 12866 | 1L266 | (Light out) | RD - Nov. 15, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 12866 | High Pressure Sodium | 38.92984478000 | -77.02653870000
11/19/13 | 1122318 | 334 | OAKDALE PL | NW | 11/19/13 | 14190DC | 14802DC | (Light out) | RW - Nov. 16, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 14190DC | High Pressure Sodium | 38.91817964000 | -77.01706140000
11/19/13 | 1122302 | 0 | SHERMAN AVE | NW | 11/19/13 | 14220 | 1G456 | (Light out) | RW - Nov. 16, 2013. Replaced photocell. 100% complete. Repaired pole number 14220 | High Pressure Sodium | 38.92254478000 | -77.02525138000
11/19/13 | 1122299 | 0 | SEATON ST | NW | 11/19/13 | 11451 | 1A100 | (Light out) | RW - Nov. 16, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 11451 | High Pressure Sodium | 38.91753869000 | -77.04044580000
11/19/13 | 1122289 | 1500 | PARK RD | NW | 11/19/13 | 12703 | 1G369 | (Light out) | FT - Nov. 16, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 12703 | High Pressure Sodium | 38.93118367000 | -77.03534967000
11/19/13 | 1122276 | 1300 | MONROE ST | NW | 11/19/13 | 13676 | 1G086 | (Light out) | MJ - Nov. 16, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 13676 | High Pressure Sodium | 38.93146550000 | -77.03246204000
11/19/13 | 1122269 | 3400 | 14TH ST | NW | 11/19/13 | 13677 | 1G075 | (Light out) | FT - Nov. 16, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 13677 | High Pressure Sodium | 38.93148309000 | -77.03266734000
11/19/13 | 1122265 | 1654 | PARK RD | NW | 11/19/13 | 10111 | 1G344 | (Light out) | RW - Nov. 16, 2013. Replaced HPS lamp. 100% completed. Repaired pole number 10111 | High Pressure Sodium | 38.93223824000 | -77.03782531000
11/19/13 | 1122201 | 2605 | ADAMS MILL RD | NW | 11/19/13 | 10730 | 1A012 | (Light out) | FT - Nov. 18, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 10730 | Incandescent | 38.92353292000 | -77.04371242000
11/19/13 | 1122193 | 3115 | 14TH ST | NW | 11/19/13 | 15013 | 1G057 | (Light out) | FT - Nov. 18, 2013. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 15013 | High Pressure Sodium | 38.93013310000 | -77.03280986000
11/17/13 | 1122081 | 0 | O ST | NW | 11/20/13 | 29268 | 6A852 | (Light out) | RW-11-19-2013-9:25PM. REPLACED 2 200 W INC LAMPS FOR POLES 29268 AND 29270 RW-11/18/13-ALLEY TOO SMALL NEED VAN Alley 13-00273019-Alleylight Repair 1336 8th Street Northwest, Washington, DC 20001, USA This issue has an image. You can view it he | Incandescent | 38.90837595000 | -77.02348678000
11/13/13 | 1121767 | 775 | H ST | NE | 11/14/13 | 61991 | 6S197 | (Light out) | FRED-11-13-2013-REPLACED 150 HPS LAMP FOR POLE 61991 | High Pressure Sodium | 38.90030060000 | -76.99586046000
11/12/13 | 1121722 | 0 | INTERSTATE 295 | SE | 11/20/13 | 86516 | 8L776 | (Light out) | RODNEY-11-20-2013-2:05AM. REPLACED 400 W HPS LAMP FOR POLE 86516 RW - REPLACED LAMP AND PHOTOCELL. 100% 13-00269768- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86724779000 | -76.99038506000
11/12/13 | 1121698 | 1005 | 1ST ST | NE | 11/18/13 | 61231 | 6S439 | (Light out) | Kenneth Bryant at 11/18/2013 10:35:15 AM: Rewired fixture and made splice in MH. 100% FRED-11-12-2013-REPLACED 250 HPS LAMP FOR POLE 61231 13-00269403- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90311217000 | -77.00596908000
11/7/13 | 1121547 | 0 | EAST CAPITOL ST | NE | 11/9/13 | 63621 | 6M831 | (Light out) | FT-11/08/13-REPLACED LAMP. POLE 63621 | High Pressure Sodium | 38.88963634000 | -76.97650063000
| 1121511 | 404 | H ST | NE | 11/9/13 | 61633 | 6S222 | (Light out) | FT-11/08/13-REPLACED LED. POLE 61633 Alley 13-00266448-Alley light doesn't turn on at dark. First light pole when entering alley from 6th st ne. Alley between F stand Acker St. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.90029910000 | -77.00026746000
11/6/13 | 1121505 | 3310 | 15TH ST | NE | 11/8/13 | 51221DC | 5A117DC | (Light out) | RW-11-7-2013-10:30PM. REPLACED 250 W HPS LAMP FOR POLE 51221DC 13-00266413-Streetlight Repair 472-598 Taylor Street Northeast, Washington, DC 20017, USA This issue has an image. You can view it here http://seeclickfix.com/issues/813266 . MBT lig | Incandescent | 38.93137950000 | -76.98438250000
11/6/13 | 1121475 | 0 | WISCONSIN AVE | NW | 11/15/13 | 38770 | 3U406 | (Light out) | RW-11-7-2013-2:15AM-N/C UNDERGROUND FOR POLE Paul Primrose at 11/15/2013 2:23:08 PM: pp 11-15-13 feed broken. ran wire to manhole and connected it. now 100% 38770 | High Pressure Sodium | 38.93584295000 | -77.07318687000
11/4/13 | 1121357 | 1418 | SHIPPEN LN | SE | 11/6/13 | 81758 | 88035 | (Light out) | RW-11/06/13-2:00AM-REPLACED LAMP POLE 81758 13-00263825-METAL POLE LIGHT HAS BEEN OUT SINCE 09-26-13 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84969312000 | -76.98374846000
| 1121074 | 0 | MONTANA AVE | NE | 10/30/13 | 59014DC | 59014 | (Light out) | RW-10/29/13-8:55PM-REPLACED LAMP 59014 13-00258783-3 POLE LIGHTS ARE OUT cwDesc: STREETLIGHT REPAIR | Mercury Vapor | 38.91668894000 | -76.97782076000
10/28/13 | 1121068 | 0 | 13TH ST | NW | 10/31/13 | 4K416DC | 4U119DC | (Light out) | FT-10/31/13- REPLACED LAMP 4K416DC | High Pressure Sodium | 38.94716466000 | -77.02979020000
10/26/13 | 1121009 | 0000 | H ST | NE | 11/9/13 | 68255DC | 68255 | (Light out) |  | High Pressure Sodium | 38.90037863000 | -77.00528191000
10/25/13 | 1120936 | 0 | 13TH ST | NW | 10/28/13 | 4K432 | 4U146 | (Light out) | Jose Aguilar at 10/28/2013 3:04:42 PM: TA 10-28-13 upon arriving we checked for power and found120vac. The light was not working because there was a wire loose at the base of the photocell. We fixed the problem and now the light works.100%...FT-10/26/2013 | High Pressure Sodium | 38.94308499000 | -77.02978871000
10/24/13 | 1120896 | 0 | O ST | NW | 10/25/13 | 29268 | 6A852 | (Light out) | FT-10/24/2013 REPLACED 189 INCANDESCENT BULB. 100% COMPLETE. POLE ID 29268 Alley 13-00255987-ALLEY LIGHTS IN THE BACK OF THIS LOCATION DO NOT COME ON IN THE EVENING. cwDesc: ALLEYLIGHT REPAIR | Incandescent | 38.90837595000 | -77.02348678000
10/24/13 | 1120853 | 1435 | NEWTON ST | NW | 10/26/13 | 13913 | 1G072 | (Light out) | FRED-10/26/2013-REPLACED 400 W HPS LAMP AND PHOTOCELL FOR POLE 13913 | High Pressure Sodium | 38.93143118000 | -77.03279918000
10/23/13 | 1120748 | 0 | RHODE ISLAND AVE | NW | 10/30/13 | 25214 | 2U043 | (Light out) | Jose Aguilar at 10/30/2013 11:34:54 AM: TA 10-30-13 wire was disconnected in the manhole, and the power door was as well. we respliced the feed and plugged in the power door. 100%Fred. 10/23/2013. 11:05pm. Replaced 250 HPS lamp on pole 25214. A power | High Pressure Sodium | 38.91062739000 | -77.02719923000
10/20/13 | 1120581 | 0 | CARROLL ST | NW | 11/7/13 | 4H569DC | 4H569 | (Light out) | Jose Aguilar at 11/7/2013 12:55:04 PM: TA Checked the light .. and we didn't find anything wrong with this light . in fact this is a brand new fixture ... light works 100%RW-10/22/13-10:55PM. NO CURRENT OVERHEAD 4H569DC Alley 13-00252470- cwDesc: ALL | High Pressure Sodium | 38.97497351000 | -77.01515190000
10/18/13 | 1120530 | 100 | STODDERT PL | SE | 10/22/13 | 70028 | 74231 | (Light out) | RW-10/22/13-1:25AM- REPLACED LAMP POLE 70028 13-00251098- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88967004000 | -76.94839956000
10/18/13 | 1120527 | 3718 | 4TH ST | SE | 10/18/13 | 85729 | 8A143 | (Light out) | RD - 41563. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 85729 | High Pressure Sodium | 38.83852517000 | -76.99985248000
10/18/13 | 1120526 | 1105 | STEVENS RD | SE | 10/18/13 | 81584DC | 8A048 | (Light out) | RD - 41563. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 81584DC | High Pressure Sodium | 38.86023686000 | -77.00228963000
10/17/13 | 1120378 | 3425 | 14TH ST | NE | 10/17/13 | 51210DC | 5A099DC | (Light out) | FT - 41563. Replaced HPS lamp. 100% completed. Repaired pole number 51210DC | High Pressure Sodium | 38.93246169000 | -76.98640494000
10/17/13 | 1120374 | 1409 | LAWRENCE ST | NE | 10/17/13 | 52486DC | 5A157DC | (Light out) | FT - 41563. Replaced HPS lamp. 100% completed. Repaired pole number 52486DC | High Pressure Sodium | 38.93177342000 | -76.98574118000
10/17/13 | 1120363 | 600 | MICHIGAN AVE | NE | 10/17/13 | 53646DC | 5U708 | (Light out) | FT - 41563. Replaced HPS lamp and photocell. 100% operational upon departure. Repaired pole number 53646DC | High Pressure Sodium | 38.93303755000 | -76.99623620000
10/17/13 | 1120308 | 0 | 13TH ST | NW | 10/18/13 | 4K415 | 4U118 | (Light out) | FRED-10/18/2013-3:40AM. REPLACED 400 HPS LAMP FOR POLE 4K415 | High Pressure Sodium | 38.94728139000 | -77.02961900000
10/10/13 | 1120031 | 0000 | ROBINSON ST | SE | 10/15/13 | 81756 | 88033 | (Light out) | Kenneth Bryant at 10/15/2013 2:38:19 PM: Changed photocell; lightbulb & installed globe RW-10/10/2013-9:55PM. NEED 150 W KIT AND GLOBE FOR 81756 13-00245677-There is a second street light in the alley behind 1459 Bruce Pl SE. cwDesc: STREETLIGHT REPAI | High Pressure Sodium | 38.84997435000 | -76.98416955000
10/10/13 | 1120011 | 900 | VIRGINIA AVE | SE | 10/10/13 | 67623 | 6L983 | (Light out) | FT - 10/8/2013. Replaced HPS lamp. Operational upon departure. Pole #67623 was repaired. | High Pressure Sodium | 38.87841973000 | -76.99513021000
10/10/13 | 1120002 | 0 | INTERSTATE 295 | SE | 10/10/13 | 68050 | 6L972 | (Light out) | FT - 10/8/2013. Replaced HPS lamp. Operational upon departure. Pole #68050 was repaired. | High Pressure Sodium | 38.87795866000 | -76.99246087000
10/10/13 | 1119978 | 600 | 5TH ST | NW | 10/10/13 | 60570 | 6S531 | (Light out) | FT - 10/8/2013. Replaced HPS Fixture. Pole #60570 was repaired. | High Pressure Sodium | 38.89772251000 | -77.01901849000
10/9/13 | 1119953 | 810 | 5TH ST | NW | 10/9/13 | 60077 | 68300 | (Light out) | FT - 10/8/2013. Replaced HPS lamp. Operational upon departure. Pole #60077 was repaired. | High Pressure Sodium | 38.89994449000 | -77.01884166000
10/9/13 | 1119941 | 1300 | MAINE AVE | SW | 10/9/13 | 66531 | 6M443 | (Light out) | FT - 10/8/2013. replaced HPS Lamp and photocell. Pole #66531 was repaired. | High Pressure Sodium | 38.88186010000 | -77.02828319000
10/8/13 | 1119849 | 0000 | 22ND ST | SE | 10/8/13 | 68332 | 6M820 | (Light out) | RW - 10/7/2013. replaced HPS Lamp and photocell. Pole #68332 was repaired. | High Pressure Sodium | 38.88856033000 | -76.97379932000
10/8/13 | 1119829 | 610 | H ST | NE | 10/8/13 | 61865 | 6S069 | (Light out) | RW - 10/7/2013. replaced HPS Lamp and photocell. Pole #61865 was repaired. | High Pressure Sodium | 38.90012072000 | -76.99763496000
10/8/13 | 1119825 | 0 | INTERSTATE 295 | SE | 10/8/13 | 68020 | 6L997 | (Light out) | RW - 10/7/2013. Replaced photocell. operational upon departure. Pole #68020 was repaired. | High Pressure Sodium | 38.87813114000 | -76.99135936000
10/8/13 | 1119823 | 0 | L ST | NW | 10/8/13 | 60457 | 6A167 | (Light out) | RW - 10/7/2013. Replaced HPS lamp. Operational upon departure. Pole #60457 was repaired. | High Pressure Sodium | 38.90380088000 | -77.01639654000
10/8/13 | 1119817 | 1200 | N ST | SE | 10/8/13 | 67782 | 68578 | (Light out) | RW - 10/7/2013. Replaced HPS Fixture. Pole #67782 was repaired. | High Pressure Sodium | 38.87457240000 | -77.00824641000
10/8/13 | 1119812 | 633 | INDIANA AVE | NW | 10/8/13 | 60665 | 6S565 | (Light out) | RW - 10/7/2013. Replaced power door. operational upon departure. Pole #60665 was repaired. | High Pressure Sodium | 38.89413265000 | -77.02076751000
10/8/13 | 1119793 | 888 | 1ST ST | NE | 10/8/13 | 61222 | 6S502 | (Light out) | RW - 10/7/2013. replaced HPS Lamp and photocell. Pole #61222 was repaired. | High Pressure Sodium | 38.90202513000 | -77.00581170000
10/8/13 | 1119773 | 0000 | H ST | NE | 10/8/13 | 68259DC | 68259 | (Light out) | RW - 10/7/2013. Replaced HPS Fixture. Pole #68259DC was repaired. | High Pressure Sodium | 38.90033650000 | -77.00847314000
10/8/13 | 1119732 | 0 | SHERMAN AVE | NW | 10/8/13 | 12586 | 1G459 | (Light out) | MJ - 10/03/2013. Replaced HPS lamp. Operational upon departure. Pole #12586 was repaired. | High Pressure Sodium | 38.92223537000 | -77.02543083000
10/8/13 | 1119726 | 1419 | CHAPIN ST | NW | 10/8/13 | 14473 | 19998 | (Light out) | MJ - 10/03/2013. Replaced HPS lamp. Operational upon departure. Pole #14473 was repaired. | High Pressure Sodium | 38.92104346000 | -77.03296049000
10/8/13 | 1119621 | 2114 | 18TH ST | NW | 10/8/13 | 11538 | 1G505 | (Light out) |  | High Pressure Sodium | 38.91851092000 | -77.04175253000
10/7/13 | 1119537 | 3400 | SHERMAN AVE | NW | 10/7/13 | 13071 | 1L295 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.93219026000 | -77.02662830000
10/7/13 | 1119486 | 0 | NEW YORK AVE | NE | 10/7/13 | 50010 | 5A044 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.91713437000 | -76.96502016000
10/7/13 | 1119484 | 2531 | BENNING RD | NE | 10/7/13 | 59619DC | 5M304 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.89795698000 | -76.97026345000
| 1119288 | 0 | 7TH ST | NW | 10/5/13 | 25703 | 6A818 | (Light out) | FRED-10/5/2013-5:30AM. REPLACED 400 HPS LAMP 13-00240780- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91121698000 | -77.02181678000
10/2/13 | 1119198 | 4469 | WISCONSIN AVE | NW | 10/3/13 | 30131 | 3L465 | (Light out) | FT-10/3/13-5:10AM- REPLACED PHOTOCELL 13-00239537-Received a complaint from the ANC regarding outage. Potentially burnt out bulb. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94724720000 | -77.06516811000
9/27/13 | 1119001 | 2327 | 33RD ST | SE | 10/2/13 | 74831DC | 79438DC | (Light out) | FRED-10/2/2013-1:50AM. REPLACED 250 HPS LAMP 13-00235721- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86054471000 | -76.95992861000
9/12/13 | 1118265 | 1005 | 1ST ST | NE | 9/17/13 | 61231 | 6S439 | (Light out) | Jose Aguilar at 9/17/2013 2:44:50 PM: This pole has probably been lifted out to make way for construction. There are temporary poles here, and we lost the trail at #61233 in the next block. FRED-9/13/2013-12:45AM. REPLACED 250 HPS LAMP. N/C | High Pressure Sodium | 38.90311217000 | -77.00596908000
9/12/13 | 1118242 | 0 | INTERSTATE 295 | SE | 9/17/13 | 86494 | 8A073 | (Light out) | TA 9-16-13 4:04PM: This problem has been fixed. It needed a new photocell. | High Pressure Sodium | 38.84482511000 | -77.00710099000
9/9/13 | 1118100 | 3254 | 15TH PL | SE | 9/11/13 | 81754 | 88031 | (Light out) | RODNEY-9/11/2013-1:05AM. REPLACED 250 W HPS LAMP. 13-00218732- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84785558000 | -76.98226108000
9/7/13 | 1118067 | 4469 | WISCONSIN AVE | NW | 9/11/13 | 30131 | 3L465 | (Light out) | FT-9/10/13-10:10PM-REPLACED LAMP 13-00217948-There is new construction to start at Van Ness Center....the area on the sidewalk is dark. Don 't know if the street light being out is related to building demo. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94724720000 | -77.06516811000
9/4/13 | 1117956 | 3408 | 15TH ST | NE | 9/6/13 | 51212DC | 5A101DC | (Light out) | FT-09/05/13-8:45PM- REPLACED LAMP 13-00215446- cwDesc: STREETLIGHT REPAIR | Incandescent | 38.93231561000 | -76.98445505000
9/4/13 | 1117937 | 2427 | MINNESOTA AVE | SE | 9/13/13 | 70076 | 80098 | (Light out) | RW-09/04/13-10:05PM- NO CURRENT OVER HEAD. WHOLE ALLEY OUT Alley 13-00214824-the alley light need to be repaired asap, crime has went up in the area. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.87320803000 | -76.97100322000
8/30/13 | 1117826 | 0000 | FRANKLIN ST | NE | 8/30/13 | 50064 | 5A055 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.92554079000 | -77.00303515000
8/30/13 | 1117775 | 0 | MONTANA AVE | NE | 8/30/13 | 59013 | 59013DC | (Light out) | replaced HPS Lamp and photocell | High Pressure Sodium | 38.91653600000 | -76.97768633000
8/30/13 | 1117724 | 1201 | NEW YORK AVE | NE | 8/30/13 | 56829 | 5M061 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.91379829000 | -76.99017687000
8/30/13 | 1117700 | 0 | KENILWORTH AVE | NE | 8/30/13 | 72459DC | 7M113DC | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.90131755000 | -76.94465926000
8/30/13 | 1117688 | 0 | ANACOSTIA FWY | SE | 8/30/13 | 79493 | 7A146 | (Light out) | Replaced photocell. operational upon departure | High Pressure Sodium | 38.88732787000 | -76.96219078000
8/30/13 | 1117668 | 0 | JAY ST | NE | 8/30/13 | 72419 | 7M095 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.90160220000 | -76.94523892000
8/30/13 | 1117653 | 0 | ANACOSTIA FWY | SE | 8/30/13 | 79466 | 7A130 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.88384591000 | -76.96362320000
8/29/13 | 1117436 | 0 | D ST | SW |  | 21625 | 6L714 | (Light out) | RW-9-5-2013-1:45 INSTALLED ONE 400 WATT HPS LAMP 9/4 RD - Installed lamp - 100% | High Pressure Sodium | 38.88478652000 | -77.01928219000
8/28/13 | 1117385 | 1015 | KENILWORTH AVE | NE | 8/28/13 | 71172DC | 7M119 | (Light out) |  | High Pressure Sodium | 38.90271798000 | -76.94306831000
8/28/13 | 1117382 | 3901 | PENNSYLVANIA AVE | SE | 8/28/13 | 78525DC | 7E135DC | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.86569632000 | -76.95176682000
8/28/13 | 1117357 | 4922 | NANNIE HELEN BURROUGHS AVE | NE | 8/28/13 | 71281DC | 7A214 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.89848333000 | -76.93033462000
8/28/13 | 1117344 | 5008 | F ST | SE | 8/28/13 | 70040 | 7A003 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.88168380000 | -76.92989661000
8/28/13 | 1117340 | 0 | KENILWORTH AVE | NE | 8/28/13 | 72458DC | 7M114DC | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.90169265000 | -76.94423992000
8/28/13 | 1117322 | 0 | 13TH ST | NW | 9/6/13 | 4K430 | 4U144 | (Light out) | Jose Aguilar at 9/6/2013 11:27:49 AM: TA 9-6-13 replaced fixture (250w) - 100% Rodney Williams at 8/29/2013 12:13:34 AM: n/c underground | High Pressure Sodium | 38.94357657000 | -77.02978724000
8/27/13 | 1117307 | 4815 | TEXAS AVE | NE | 8/27/13 | 76839 | 76939 | (Light out) | Replaced HPS Fixture | High Pressure Sodium | 38.88961077000 | -76.93822815000
8/27/13 | 1117306 | 3859 | PENNSYLVANIA AVE | SE | 8/27/13 | 77881DC | 7E010 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.86525460000 | -76.95024453000
8/27/13 | 1117302 | 5077 | KIMI GRAY CT | SE | 8/27/13 | 70036 | 7A027 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.88227693000 | -76.92914010000
8/27/13 | 1117299 | 3806 | ALABAMA AVE | SE | 8/27/13 | 77878 | 7E014 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.86565202000 | -76.95107338000
8/27/13 | 1117278 | 0 | CAMDEN ST | SE | 8/27/13 | 74756DC | 7A070DC | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.85947622000 | -76.95961031000
8/27/13 | 1117269 | 5345 | ASTOR PL | SE | 8/27/13 | 75574 | 75574DC | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.88660798000 | -76.92411890000
8/27/13 | 1117263 | 3464 | DIX ST | NE | 8/27/13 | 70020 | 7A023 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.89482319000 | -76.95519656000
8/27/13 | 1117234 | 1109 | KENILWORTH AVE | NE | 8/27/13 | 70326DC | 7M081 | (Light out) | Replaced HPS Fixture | High Pressure Sodium | 38.90343492000 | -76.94328092000
| 1117215 | 635 | 20TH ST | NE | 8/30/13 | 70021 | 7A022 | (Light out) | William Day at 8/30/2013 10:24:06 AM: installed (1) 250 watt power door; replace 250 watt bulb; twist lock photocell 100% 8377. 08/28/2013. 08:50pm. Needs 250 watt fixture. 13-00208704- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89707182000 | -76.97589261000
8/26/13 | 1117184 | 0 | 8TH ST | NW | 8/27/13 | 14213 | 1U035 | (Light out) | LL-8/26/13-11:10PM-REPLACED LAMP COMPLETE | High Pressure Sodium | 38.91834316000 | -77.02301191000
8/26/13 | 1117177 | 0 | 8TH ST | NW | 8/27/13 | 14213 | 1U035 | (Light out) | LL-8/26/13-11:10PM-REPLACED LAMP COMPLETE | High Pressure Sodium | 38.91834316000 | -77.02301191000
8/23/13 | 1117109 | 0000 | OVERLOOK AVE | SW | 8/23/13 | 81834 | 88095 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.83393831000 | -77.01328820000
8/23/13 | 1117098 | 1423 | SHIPPEN LN | SE | 8/23/13 | 81759 | 88036 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.84947902000 | -76.98358734000
| 1117084 | 3649 | BANGOR ST | SE | 8/29/13 | 74811DC | 7A091DC | (Light out) | LL-8/29/2013-2:55 AM -REPLACED 150 WATT HPS LAMP. 100% COMPLETE. Alley 13-00206052-DC NO. 74811DC...ONE WAY INTO ALLEY HAVE TO COME TO BANGOR.....VERY DARK WITHOUT LIGHT...LIGHT COMES ON IN THE EVENING BUT GOES OUT AROUND 10:00 PM cwDesc: ALLEYLIGHT | High Pressure Sodium | 38.86030744000 | -76.95386367000
| 1117052 | 1420 | 9TH ST | NW | 8/26/13 | 25470 | 6U457 | (Light out) | Jose Aguilar at 8/26/2013 3:58:32 PM:INSTALLED FIXTURES AND GLOBE 100% LL-8/22/2013-11:05PM. NEED 2 400 W KITS AND ONE GLOBE. 13-00205465-The globe fell off pole cwDesc: STREETLIGHT R | High Pressure Sodium | 38.90930620000 | -77.02386532000
8/22/13 | 1117039 | 3718 | 4TH ST | SE | 8/22/13 | 85727 | 8A144 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.83851611000 | -77.00004783000
8/22/13 | 1117010 | 0 | BANGOR ST | SE | 8/23/13 | 74833DC | 7A096DC | (Light out) | MJ-8/22/2013-9:27 PM –REPLACED 250 WATT POWER DOOR. 100 % COMPLETE | High Pressure Sodium | 38.86055117000 | -76.96088105000
8/22/13 | 1116979 | 3204 | 15TH PL | SE | 8/22/13 | 81716 | 87993 | (Light out) | Replaced photocell. operational upon departure | High Pressure Sodium | 38.84976378000 | -76.98203464000
8/21/13 | 1116956 | 1021 | 17TH ST | NE | 10/22/13 | 59346 | 59346 | (Light out) | BCM 8-28-13 11:30AM - POLE IS MISSING 13-00203912-streetlight pole was removed when Washington Gas or PEPCO was working on a construction job and never put the pole back. Some one was rob last night. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90312888000 | -76.97890387000
8/19/13 | 1116880 | 0000 | FRANKLIN ST | NE | 8/23/13 | 50066 | 5A057 | (Light out) | MJ-8/20/2013-8:30PM. NEED NEW LED FIXTURE. alley 13-00202213- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.92553854000 | -77.00229041000
8/13/13 | 1116674 | 1443 | LAWRENCE ST | NE | 8/13/13 | 52488DC | 5A159DC | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.93180662000 | -76.98505493000
8/8/13 | 1116426 | 5127 | H ST | SE | 8/9/13 | 75492 | 75492DC | (Light out) | MJ-8/8/2013-12:50PM REPLACED ONE 150 WATT HPS LAMP Alley 13-00192403-ALLEYLIGHTS NEEDS TO BE REPAIRED cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.87810752000 | -76.92948653000
8/8/13 | 1116425 | 5127 | H ST | SE | 8/9/13 | 75492 | 75492DC | (Light out) | MJ-8/8/2013-12:50PM REPLACED ONE 150 WATT HPS LAMP Alley 13-00192400-the alley between 819 and 823 51st street SE alleylights needs to be repaired, 853 between 5024 H street alleylights needs to be repaired also they are located in SE as well. cwDesc: A | High Pressure Sodium | 38.87810752000 | -76.92948653000
8/7/13 | 1116400 | 815 | V ST | NW | 8/7/13 | 14236 | 1U040 | (Light out) | WD 8-7-13 - MADE SPLICE IN MH. 100%. 8-7-13. No current at fixture. Manhole is located 4ft in front of Pole in question. | Incandescent | 38.91816509000 | -77.02346836000
8/6/13 | 1116372 | 226 | RHODE ISLAND AVE | NW | 8/8/13 | 59994 | 5A186 | (Light out) | LL-8/7/2013-8:58PM. REPLACED 2 300 W LAMP. LIGHT IS ON FOR POLES 59994 AND 59995 13-00190866-TWO ARE OUT IN THIS AREA, 1311 AND 1339 KEARNY ST PLEASE REPLACE LIGHT BULBS cwDesc: STREETLIGHT REPAIR | Incandescent | 38.91452540000 | -77.01525438000
8/6/13 | 1116348 | 4202 | 13TH ST | NW | 8/6/13 | 4K433 | 4U149 | (Light out) | replaced HPS Lamp and photocell | High Pressure Sodium | 38.94238501000 | -77.02962392000
8/5/13 | 1116310 | 1307 | NEW HAMPSHIRE AVE | NW | 8/8/13 | 24476 | 2G769 | (Light out) | LL-8/8/2013-3:09AM. REPLACED T-BASE DOOR AND CLEAN TRASH OUT. LIGHT IS ON 100%. 13-00189972-street light pole is missing panel on the t-base and it is full of trash. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90805639000 | -77.04505512000
8/2/13 | 1116230 | 3222 | 14TH ST | NE | 8/6/13 | 51220DC | 5A114DC | (Light out) | MJ-8/5/2013-8:55PM. REPLACED 300 W INCANDESCENT LAMP. | High Pressure Sodium | 38.93068379000 | -76.98625793000
7/31/13 | 1116092 | 1400 | SHIPPEN LN | SE | 8/6/13 | 81760 | 88037 | (Light out) | 08-06-2013 02:13 f.t 8-6-13 replaced photocell night watchman job is complete Alley 13-00185805- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.84942195000 | -76.98333819000
7/31/13 | 1116035 | 0000 | FRANKLIN ST | NE |  | 50066 | 5A057 | (Light out) | RW-7/31/2013-10:20 pm-replaced 400 watt hps lamp. Pole #50066. 100% Complete. | High Pressure Sodium | 38.92553854000 | -77.00229041000
7/31/13 | 1116034 | 0000 | FRANKLIN ST | NE | 8/8/13 | 50063 | 5A054 | (Light out) | 8-08-2013 12:07 f.t 8-8-13 there was a broken feed and neutral rewired the manhole light is working 100% completeRW-7/31/2013-10:45 pm-n/c underground white taped pole. NEUTRAL TO GROUND HAS 65VOLTS. BAD NEUTRAL UNDERGROUND. REPLACE NEUTRAL FROM T-BASE | High Pressure Sodium | 38.92567388000 | -77.00321706000
7/26/13 | 1115907 | 0 | 13TH ST | NW | 7/29/13 | 4K428 | 4U142 | (Light out) | LL-7/27/13-5:31AM-REPLACED LAMP AND PHOTOCELL | High Pressure Sodium | 38.94404010000 | -77.02978696000
7/26/13 | 1115906 | 0 | 13TH ST | NW | 7/29/13 | 4K426 | 4U140 | (Light out) | LL-7/27/13-2:24AM-REPLACED LAMP AND PHOTOCELL. NO CURRENT FROM MANHOLE | High Pressure Sodium | 38.94449236000 | -77.02978547000
7/24/13 | 1115757 | 4500 | EAST CAPITOL ST | SE | 8/12/13 | 70052 | 7A035 | (Light out) | 08-12-2013 11:36 Repaired a open neutral. FT LL-7/26/13-8:43PM-REPLACED LAMP AND PHOTOCELL NO CURRENT FROM MANHOLE | High Pressure Sodium | 38.88960932000 | -76.93729068000
7/24/13 | 1115720 | 715 | H ST | NW | 7/24/13 | 22567 | 2M435 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.89973194000 | -77.02259727000
7/24/13 | 1115699 | 650 | MASSACHUSETTS AVE | NW | 7/24/13 | 22465 | 6A979 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.90204075000 | -77.02130668000
7/24/13 | 1115687 | 1530 | 11TH ST | NW | 7/24/13 | 25286 | 2U045 | (Light out) | Replaced HPS Fixture | High Pressure Sodium | 38.91105847000 | -77.02715860000
7/24/13 | 1115673 | 700 | H ST | NW | 7/24/13 | 22425 | 6M656 | (Light out) | Replaced HPS Fixture | High Pressure Sodium | 38.89969708000 | -77.02201582000
7/24/13 | 1115647 | 1129 | 21ST ST | NW | 7/24/13 | 29732 | 2G716 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.90476149000 | -77.04814723000
7/23/13 | 1115468 | 919 | T ST | NW | 7/23/13 | 13451 | 1L370 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.91563328000 | -77.02474424000
7/18/13 | 1115165 | 0 | EAST CAPITOL ST | SE | 7/18/13 | 73588 | 73588DC | (Light out) | replaced HPS Lamp and photocell | High Pressure Sodium | 38.88965078000 | -76.92405517000
7/18/13 | 1115153 | 4887 | NANNIE HELEN BURROUGHS AVE | NE | 7/18/13 | 72344DC | 7A219 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.89854411000 | -76.93181305000
7/18/13 | 1115146 | 3000 | PENNSYLVANIA AVE | SE | 7/18/13 | 78561DC | 7E093DC | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.87074474000 | -76.96412983000
7/18/13 | 1115143 | 3100 | PENNSYLVANIA AVE | SE | 7/18/13 | 78560DC | 7E094DC | (Light out) | replaced HPS Lamp and photocell | High Pressure Sodium | 38.87059877000 | -76.96377234000
7/18/13 | 1115105 | 5037 | DRAKE PL | NE | 7/18/13 | 70045 | 7A028 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.88271180000 | -76.92957704000
7/17/13 | 1115091 | 2430 | 32ND ST | SE | 7/17/13 | 74752DC | 7A066DC | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.85947936000 | -76.96116565000
7/17/13 | 1115071 | 1534 | TANNER ST | SE | 7/17/13 | 81768 | 88045 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.84738657000 | -76.98124742000
7/17/13 | 1115005 | 1419 | ROBINSON ST | SE | 7/17/13 | 81737 | 88014 | (Light out) | Replaced HPS lamp. Operational upon departure | High Pressure Sodium | 38.84932042000 | -76.98393968000
7/16/13 | 1114917 | 1826 | 18TH ST | NW | 7/16/13 | 26780 | 2M106 | (Light out) | replaced HPS Lamp and photocell | High Pressure Sodium | 38.91492300000 | -77.04174945000
7/16/13 | 1114906 | 1605 | CORCORAN ST | NW | 7/16/13 | 26872 | 2M142 | (Light out) | replaced HPS Lamp and photocell | High Pressure Sodium | 38.91178157000 | -77.04159147000
7/16/13 | 1114859 | 0 | 8TH ST | NW | 7/16/13 | 25502 | 2M195 | (Light out) | replaced HPS Lamp and photocell | High Pressure Sodium | 38.91238326000 | -77.02288195000
7/16/13 | 1114835 | 1035 | CONNECTICUT AVE | NW | 7/16/13 | 27215 | 2G834 | (Light out) |  | High Pressure Sodium | 38.90340940000 | -77.03964906000
7/16/13 | 1114809 | 1218 | CONNECTICUT AVE | NW | 7/24/13 | 24532 | 2U519 | (Light out) | 07-23-2013 03:21 Tony A ..,,07/23/13 upon arrival I checked base for voltage .. there was no current then I traced wires to the first MH and everything was ok in this MH wires were running through this MH and they had no power. I traced wires to the foll | High Pressure Sodium | 38.90651643000 | -77.04185036000
7/15/13 | 1114729 | 3226 | 15TH PL | SE | 7/18/13 | 81778 | 88055 | (Light out) | LL-7/18/2013-6:30AM. REPLACED 250 W CONVERSION KIT, 300 W LAMP AND NIGHT WATCHMAN. 13-00168962-bulb burnt out. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84869559000 | -76.98249181000
7/15/13 | 1114713 | 919 | T ST | NW | 7/15/13 | 13451 | 1L370 | (Light out) |  | High Pressure Sodium | 38.91563328000 | -77.02474424000
7/12/13 | 1114562 | 500 | INDIANA AVE | NW | 7/12/13 | 60168 | 68366 | (Light out) |  | High Pressure Sodium | 38.89438381000 | -77.01972768000
7/12/13 | 1114559 | 80 | 1ST ST | SE | 7/12/13 | 67445 | 6A015 | (Light out) |  | High Pressure Sodium | 38.87689360000 | -77.00599612000
7/12/13 | 1114533 | 0 | H ST | NE | 7/12/13 | 62354 | 6S136 | (Light out) |  | High Pressure Sodium | 38.90011064000 | -76.98535317000
7/12/13 | 1114526 | 801 | D ST | NW | 7/12/13 | 60176 | 2M330 | (Light out) |  | High Pressure Sodium | 38.89474698000 | -77.02312090000
7/12/13 | 1114499 | 1509 | SOUTH CAPITOL ST | SE | 7/12/13 | 67017 | 68555 | (Light out) |  | High Pressure Sodium | 38.87101062000 | -77.00912305000
7/12/13 | 1114494 | 600 | 5TH ST | NW | 7/12/13 | 60083 | 6S528 | (Light out) |  | High Pressure Sodium | 38.89745914000 | -77.01883966000
7/12/13 | 1114467 | 309 | H ST | NE | 7/12/13 | 61520 | 6S048 | (Light out) |  | High Pressure Sodium | 38.90012250000 | -77.00160714000
7/10/13 | 1114214 | 0 | 17TH ST | NE | 7/10/13 | 59370 | 5M005 | (Light out) |  | High Pressure Sodium | 38.90153422000 | -76.97890987000
7/10/13 | 1114212 | 0 | MARYLAND AVE | NE | 7/10/13 | 59542 | 5M248 | (Light out) |  | High Pressure Sodium | 38.90066776000 | -76.98240388000
7/10/13 | 1114185 | 501 | NEW YORK AVE | NE | 7/10/13 | 56842 | 5A430 | (Light out) |  | High Pressure Sodium | 38.91132939000 | -76.99721837000
7/9/13 | 1114156 | 2714 | SOUTH DAKOTA AVE | NE | 7/9/13 | 58382 | 5M085 | (Light out) |  | High Pressure Sodium | 38.92691968000 | -76.96718869000
7/9/13 | 1114124 | 0 | NEW YORK AVE | NE | 7/9/13 | 50008 | 5A042 | (Light out) |  | High Pressure Sodium | 38.91724347000 | -76.96648514000
7/9/13 | 1114044 | 2010 | 48TH ST | NW | 7/9/13 | 35370DC | 3E030 | (Light out) |  | Incandescent | 38.91704622000 | -77.09453331000
7/9/13 | 1114019 | 0 | CANAL RD | NW | 7/9/13 | 35453 | 29784 | (Light out) |  | High Pressure Sodium | 38.90597248000 | -77.07886209000
| 1113849 | 0 | MASSACHUSETTS AVE | NW | 7/30/13 | 25964 | 2G953 | (Light out) | 7/3/13 - MJ REPAIRED light 13-00158526-light is on eastbound side slightly east of 9th st cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90320032000 | -77.02510725000
7/2/13 | 1113811 | 0 | NEW YORK AVE | NE | 7/4/13 | 50002 | 5A036 | (Light out) | MJ-7/3/13-8:10PM-REPLACED LAMP. 100% COMPLETE 13-00157777-The pole is located across from the Day's Inn cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91735721000 | -76.97069936000
7/2/13 | 1113769 | 0 | NEW YORK AVE | NE | 7/2/13 | 58770 | 5A047 | (Light out) |  | High Pressure Sodium | 38.91700054000 | -76.96267103000
7/2/13 | 1113746 | 0 | 9TH ST | NE | 7/2/13 | 52560 | 5M022 | (Light out) |  | High Pressure Sodium | 38.91125364000 | -76.99254153000
7/2/13 | 1113722 | 0 | SOUTH DAKOTA AVE | NE | 7/2/13 | 57799DC | 5M192DC | (Light out) |  | High Pressure Sodium | 38.92024462000 | -76.95803306000
7/2/13 | 1113660 | 0 | 14TH ST | NW | 7/2/13 | 12073 | 1G564 | (Light out) |  | High Pressure Sodium | 38.92089953000 | -77.03174747000
7/2/13 | 1113636 | 1300 | PARK RD | NW | 7/2/13 | 12954 | 1G060 | (Light out) |  | High Pressure Sodium | 38.93042789000 | -77.03244578000
7/2/13 | 1113630 | 0 | IRVING ST | NW | 7/2/13 | 12743 | 1G024 | (Light out) |  | High Pressure Sodium | 38.92879140000 | -77.03335110000
6/28/13 | 1113411 | 1400 | SHIPPEN LN | SE | 7/3/13 | 81733 | 88010 | (Light out) | TA 7/3/13 - INSTALLED 120' LF OF TRIPLEX TO POLE 81730 - PEPCO INSTALLED NEW POLES IN THIS AREA. 6592-06/29/13-4:15AM-NO CURRENT FROM OVERHEAD POLES 733DC,81731DC AND 81732DC 13-00154219-streetlights are out on this block cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84898543000 | -76.98275634000
| 1113401 | 907 | T ST | NW | 7/2/13 | 13453 | 1L372 | (Light out) | 11063-7/1/13-10:55PM-REPLACED LAMP. 100% COMPLETE 13-00153963- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91563204000 | -77.02439690000
6/28/13 | 1113348 | 0 | WISCONSIN AVE | NW | 7/9/13 | 30178 | 3G016 | (Light out) | 11063-7/9/13-2:00AM-POLE DOESNT EXIST IN THE AREA LL - REPALCED LAMP AND PHOTOCELL. 100% | High Pressure Sodium | 38.92652860000 | -77.07306865000
6/28/13 | 1113347 | 2844 | WISCONSIN AVE | NW | 7/9/13 | 30179 | 3G010 | (Light out) | 11063-7/9/13-2:00AM-POLE DOESNT EXIST IN THE AREA LL - REPLACED LAMP AND PHOTOCELL. 100% | High Pressure Sodium | 38.92718446000 | -77.07306789000
6/28/13 | 1113345 | 134 | L ST | NW | 7/9/13 | 61099 | 6S251 | (Light out) | 11063-7/9/13-11:30PM-THIS POLE DOESNT EXIST AROUND THIS ADDRESS LL - REPLACED LAMP AND PHOTOCELL. 100% | High Pressure Sodium | 38.90367396000 | -77.01345330000
6/28/13 | 1113344 | 0 | L ST | NW | 7/9/13 | 61098 | 6S254 | (Light out) | 11063-7/9/13-11:30PM-THIS POLE DOESNT EXIST AROUND THIS ADDRESS. LL - REPLACED LAMP AND PHOTOCELL. 100% | High Pressure Sodium | 38.90367060000 | -77.01389371000
6/28/13 | 1113343 | 127 | PIERCE ST | NW | 7/4/13 | 61097 | 6S262 | (Light out) | LL - REPLACED LAMP AND PHOTOCELL. 100% | High Pressure Sodium | 38.90464361000 | -77.01368699000
6/28/13 | 1113342 | 127 | PIERCE ST | NW | 7/2/13 | 61097 | 6S262 | (Light out) | surveyed entire block around 127 Pierce street, NW could not find any lights out or pole #61097 | High Pressure Sodium | 38.90464361000 | -77.01368699000
6/25/13 | 1113223 | 1418 | BRUCE PL | SE | 6/29/13 | 81788 | 88065 | (Light out) | 6592-06/29/13-4:25AM- REPLACED LAMP AND PHOTOCELL | High Pressure Sodium | 38.85054078000 | -76.98359853000
| 1113221 | 1748 | EAST CAPITOL ST | NE | 7/4/13 | 63712 | 6A501 | (Light out) | TA -7/3/13 MADE SPLICE IN MANHOLE - 100% 6592-6/26/2013-2:50AM. REPLACED 400 W LAMP AND PHOTOCELL. LIGHT OFF, NO CURRENT FROM MANHOLE. 6 LIGHTS OUT. 13-00150770- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88973040000 | -76.97991030000
| 1113191 | 1403 | KEARNEY ST | NW | 6/26/13 | 59990 | 5A182 | (Light out) | 6592-6/26/2013-4:45AM. REPLACED 250 W LAMP. LIGHT ON. UNABLE RO LOCATED POLE 66627. 13-00150404-light pole number 66627 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91424947000 | -77.01606264000
6/24/13 | 1113115 | 200 | W ST | NW | 6/25/13 | 13760 | 1U188 | (Light out) | MJ-6/25/2013-1:55AM. REPLACED 400 W HPS LAMP. | High Pressure Sodium | 38.91949574000 | -77.01713787000
6/24/13 | 1113114 | 200 | W ST | NW | 6/25/13 | 13760 | 1U188 | (Light out) | REFER TO WORK ORDER 1113115 | High Pressure Sodium | 38.91949574000 | -77.01713787000
6/24/13 | 1113070 | 200 | W ST | NW |  | 13760 | 1U188 | (Light out) | REFER TO WORK ORDER 1113115. 1909-6-24-2013-1:15 AM. SECURED GLOBE ON POLE NUMBER 13760. ONE LU 400 WATT HG LAMP IS NEEDED. | High Pressure Sodium | 38.91949574000 | -77.01713787000
| 1113045 | 0 | U ST | NW | 7/3/13 | 11722 | 1G527 | (Light out) | KB 7/3/13 - THE AREA IS UNDER CONSTRUCTION, CHECKED ALL LIGHTS AND ARE WORKING 100%. THERE IS AN OLD LIGHT AT THE LOCATION AND NEEDS TO BE REMOVED - GC IS REMOVING THE POLE. 11063-6/26/2013-9:30PM. N/C UNDERGROUND. 13-00148690- cwDesc: STREETLIGHT | High Pressure Sodium | 38.91709757000 | -77.02977696000
6/21/13 | 1112950 | 0 | 13TH ST | NW | 6/26/13 | 4K427 | 4U141 | (Light out) | MJ-06/26/13-5:10AM-REPLACED LAMP. 100% COMPLETE | High Pressure Sodium | 38.94426693000 | -77.02962255000
6/21/13 | 1112945 | 5928 | GEORGIA AVE | NW |  | 4E220 | 4A828 | (Light out) | 7/3/13 - AT THE WALMART CONSTRUCTION SITE THE CONTRACTOR DUG UP THE CONDUIT- THERE IS A BREAKDOWN IN THE CONDUIT. NOW LIGHT IS LOCATED BEHIND FENCED IN AREA LA 6/25/13 10:30 PM - NO CURRENT. | High Pressure Sodium | 38.96245901000 | -77.02779791000
6/19/13 | 1112806 | 0 | WISCONSIN AVE | NW | 7/8/13 | 38770 | 3U406 | (Light out) | MJ-6/21/2013-4:05AM. N/C UNDERGROUND. 13-00145094-Light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93584295000 | -77.07318687000
6/18/13 | 1112696 | 2400 | 14TH ST | NW | 6/18/13 | 12048 | 1A046 | (Light out) |  | High Pressure Sodium | 38.92087041000 | -77.03196022000
6/18/13 | 1112674 | 3200 | KENYON PL | NW | 6/18/13 | 14683 | 1G052 | (Light out) |  | High Pressure Sodium | 38.93003166000 | -77.03236323000
6/18/13 | 1112617 | 1933 | 18TH ST | NW | 6/18/13 | 26784 | 21410 | (Light out) |  | High Pressure Sodium | 38.91663347000 | -77.04174081000
6/18/13 | 1112612 | 0 | SOUTH CAPITOL ST | SW | 6/18/13 | 21726 | 68654 | (Light out) |  | High Pressure Sodium | 38.88398813000 | -77.00914717000
6/18/13 | 1112603 | 1133 | 21ST ST | NW | 6/18/13 | 29685 | 2G786 | (Light out) |  | Mercury Vapor | 38.90394416000 | -77.04671946000
6/18/13 | 1112581 | 0 | 23RD ST | NW | 6/18/13 | 28321 | 2M269 | (Light out) |  | High Pressure Sodium | 38.89287719000 | -77.05003596000
6/18/13 | 1112574 | 2133 | P ST | NW | 6/18/13 | 24412 | 2G644 | (Light out) |  | High Pressure Sodium | 38.90970976000 | -77.04838690000
6/18/13 | 1112566 | 1400 | CHURCH ST | NW | 6/18/13 | 26313 | 29795 | (Light out) |  | High Pressure Sodium | 38.91043747000 | -77.03229408000
6/18/13 | 1112562 | 0 | 9TH ST | NW | 6/18/13 | 22988 | 2G982 | (Light out) |  | High Pressure Sodium | 38.90042206000 | -77.02407679000
6/18/13 | 1112559 | 1724 | 17TH ST | NW | 6/18/13 | 26740 | 2M054 | (Light off/on) |  | High Pressure Sodium | 38.91352294000 | -77.03857053000
6/18/13 | 1112546 | 1100 | CONNECTICUT AVE | NW | 6/18/13 | 24537 | 2U557 | (Light out) |  | High Pressure Sodium | 38.90429111000 | -77.04049306000
6/17/13 | 1112416 | 2224 | 18TH ST | NW | 6/17/13 | 11536 | 1G500 | (Light out) |  | High Pressure Sodium | 38.91934203000 | -77.04175301000
| 1112414 | 0 | KENILWORTH AVE | SE | 6/21/13 | 79495 | 7A148 | (Light out) | MJ-6/21/2013-5:10AM. REPLACED 70 W LAMP AND NIGHT WATCHMAN. Alley 13-00142123- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.88589091000 | -76.96283495000
6/17/13 | 1112406 | 0 | H ST | NE | 6/17/13 | 68257DC | 68257 | (Light out) |  | High Pressure Sodium | 38.90032958000 | -77.00695053000
6/17/13 | 1112399 | 1500 | SOUTH CAPITOL ST | SE | 6/17/13 | 67034 | 68534 | (Light out) |  | High Pressure Sodium | 38.87322455000 | -77.00888362000
6/17/13 | 1112382 | 900 | I ST | SE | 6/17/13 | 67461 | 6A033 | (Light out) |  | High Pressure Sodium | 38.87920360000 | -77.00688084000
6/17/13 | 1112353 | 444 | 7TH ST | NW | 6/17/13 | 60649 | 6M624 | (Light out) |  | High Pressure Sodium | 38.89571105000 | -77.02201326000
6/17/13 | 1112343 | 210 | I ST | NE | 6/17/13 | 61389 | 6S323 | (Light out) |  | High Pressure Sodium | 38.90127504000 | -77.00312711000
6/17/13 | 1112336 | 0 | H ST | NE | 6/17/13 | 68249DC | 68249 | (Light out) |  | High Pressure Sodium | 38.90004036000 | -77.00401332000
6/17/13 | 1112334 | 840 | E ST | NW | 6/17/13 | 60180 | 2M349 | (Light out) |  | High Pressure Sodium | 38.89605627000 | -77.02249512000
6/17/13 | 1112324 | 3023 | 14TH ST | NW | 6/17/13 | 14688 | 1G005 | (Light out) |  | High Pressure Sodium | 38.92812470000 | -77.03247317000
6/17/13 | 1112321 | 3532 | GEORGIA AVE | NW | 6/17/13 | 12969 | 1G210 | (Light out) |  | High Pressure Sodium | 38.93411676000 | -77.02407525000
6/17/13 | 1112314 | 0 | MT PLEASANT ST | NW | 6/17/13 | 10180 | 1G395 | (Light out) |  | High Pressure Sodium | 38.93248624000 | -77.03896686000
6/17/13 | 1112308 | 0 | MT PLEASANT ST | NW | 6/17/13 | 10109 | 1G337 | (Light out) |  | High Pressure Sodium | 38.93242898000 | -77.03870517000
6/17/13 | 1112303 | 0 | COLLEGE ST | NW | 6/17/13 | 13997 | 1U197 | (Light out) |  | High Pressure Sodium | 38.92133591000 | -77.01793225000
6/14/13 | 1112261 | 0 | 7TH ST | NW | 6/29/13 | 22430 | 2A186 | (Light out) | TA - 6-28-13 SURVEYED ENTIRE BLOCK COULD NOT LOCATE EXPOSED WIRES CHECK ALL STREETLIGHTS ON THIS BLOCK ALL 100% OPERATIONAL This needs the day crew to survey this pole 13-00140419-Wiring is exposed on street pole; SW corner of 7th and F St cwDesc: ST | High Pressure Sodium | 38.89710115000 | -77.02201609000
6/13/13 | 1112206 | 0000 | OVERLOOK AVE | SE | 6/18/13 | 81807 | 85794 | (Light out) | MJ-6/18/2013-12:55AM. REPLACED 250 W HPS LAMP. | High Pressure Sodium | 38.82876179000 | -77.01739325000
6/13/13 | 1112205 | 0000 | OVERLOOK AVE | SW | 6/18/13 | 81836 | 88097 | (Light out) | MJ-6/18/2013-1:55AM. REPLACED 250 W LAMP. | High Pressure Sodium | 38.83334467000 | -77.01372200000
6/13/13 | 1112203 | 0000 | OVERLOOK AVE | SW | 6/18/13 | 81833 | 88094 | (Light out) | MJ-6/18/2013-2:00. REPLACED 250 W HPS LAMP. | High Pressure Sodium | 38.83423707000 | -77.01306892000
6/13/13 | 1112119 | 3100 | SHERMAN AVE | NW | 6/13/13 | 12820 | 1L255 | (Light out) |  | High Pressure Sodium | 38.92892725000 | -77.02615558000
| 1112116 | 0 | WISCONSIN AVE | NW | 6/17/13 | 38770 | 3U406 | (Light out) | TA 6-17-13 10AM found false connection in the mh.. material used ... 1- # 10 butt splice LA-06/14/13-1:30AM- NO CURRENT 13-00138962-Light is out in front of Burka's cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93584295000 | -77.07318687000
6/13/13 | 1112096 | 2224 | 18TH ST | NW | 6/13/13 | 11536 | 1G500 | (Light out) |  | High Pressure Sodium | 38.91934203000 | -77.04175301000
6/13/13 | 1112085 | 0 | 14TH ST | NW | 6/13/13 | 12074 | 1G562 | (Light out) |  | High Pressure Sodium | 38.92050364000 | -77.03173722000
6/13/13 | 1112069 | 0 | W ST | NW | 6/13/13 | 11808 | 1G576 | (Light out) |  | High Pressure Sodium | 38.91938866000 | -77.03020579000
6/12/13 | 1112027 | 2425 | 14TH ST | NW | 6/12/13 | 12046 | 1A049 | (Light off/on) |  | High Pressure Sodium | 38.92156215000 | -77.03202917000
6/12/13 | 1112012 | 0 | IRVING ST | NW | 6/12/13 | 12738 | 1G044 | (Light out) |  | High Pressure Sodium | 38.92871205000 | -77.03568647000
6/12/13 | 1111953 | 1428 | TOBIAS DR | SE | 6/12/13 | 81783 | 88060 | (Light out) |  | High Pressure Sodium | 38.85014068000 | -76.98274637000
6/12/13 | 1111947 | 0000 | OVERLOOK AVE | SW | 6/12/13 | 81835 | 88096 | (Light out) |  | High Pressure Sodium | 38.83364467000 | -77.01350898000
6/12/13 | 1111937 | 2500 | SHERIDAN RD | SE | 6/12/13 | 81361DC | 88103 | (Light out) |  | High Pressure Sodium | 38.85871022000 | -76.99326612000
6/12/13 | 1111936 | 0 | STANTON RD | SE | 6/12/13 | 81360DC | 88104 | (Light out) |  | High Pressure Sodium | 38.85852446000 | -76.99323709000
6/11/13 | 1111855 | 401 | 51ST ST | SE | 6/11/13 | 70046 | 7A029 | (Light out) |  | High Pressure Sodium | 38.88264938000 | -76.92923070000
6/11/13 | 1111847 | 0 | ANACOSTIA FWY | SE | 6/11/13 | 79482 | 7A151 | (Light out) |  | High Pressure Sodium | 38.88927741000 | -76.95876088000
6/11/13 | 1111834 | 0 | KENILWORTH AVE | NE | 6/11/13 | 70306 | 7M058 | (Light out) |  | High Pressure Sodium | 38.90838237000 | -76.93790987000
6/11/13 | 1111822 | 4202 | BENNING RD | NE | 6/11/13 | 73867DC | 73867 | (Light out) |  | High Pressure Sodium | 38.89298310000 | -76.94251439000
6/11/13 | 1111806 | 643 | BARNES ST | NE | 6/14/13 | 72469 | 7U750 | (Light off/on) | 6592-6/13/2013-8:50pm Replaced lamp 100% complete | High Pressure Sodium | 38.90075954000 | -76.95122635000
6/11/13 | 1111782 | 1333 | NEW HAMPSHIRE AVE | NW | 6/11/13 | 24473 | 2G775 | (Light out) |  | High Pressure Sodium | 38.90894364000 | -77.04422669000
6/10/13 | 1111772 | 0 | R ST | NW | 6/12/13 | 25645 | 6A831 | (Light out) | MD-06/11/13-10:10PM- REPLACED LAMP. 100% COMPLETE 13-00136050-Light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91269915000 | -77.02207113000
6/10/13 | 1111736 | 0 | 7TH ST | NW | 6/10/13 | 22433 | 6M631 | (Light out) |  | High Pressure Sodium | 38.89625834000 | -77.02182627000
6/10/13 | 1111732 | 811 | 7TH ST | NW | 6/10/13 | 22421 | 6M664 | (Light out) |  | High Pressure Sodium | 38.90029959000 | -77.02201191000
6/10/13 | 1111731 | 0 | M ST | NW | 6/10/13 | 23730 | 2U534 | (Light out) |  | High Pressure Sodium | 38.90557436000 | -77.04154706000
6/10/13 | 1111717 | 1404 | 11TH ST | NW | 6/10/13 | 25256 | 2M243 | (Light out) |  | High Pressure Sodium | 38.90869361000 | -77.02692105000
6/10/13 | 1111692 | 1301 | 20TH ST | NW | 6/10/13 | 24830 | 2A017 | (Light out) |  | High Pressure Sodium | 38.90756285000 | -77.04480461000
6/10/13 | 1111690 | 3338 | P ST | NW | 6/10/13 | 21010 | 2G137 | (Light out) |  | High Pressure Sodium | 38.90871624000 | -77.06742500000
6/10/13 | 1111686 | 737 | 7TH ST | NW | 6/10/13 | 22450 | 6M647 | (Light out) |  | High Pressure Sodium | 38.89929255000 | -77.02181765000
6/10/13 | 1111685 | 1428 | 35TH ST | NW | 6/10/13 | 20900 | 2G198 | (Light out) |  | High Pressure Sodium | 38.90862777000 | -77.06914877000
6/10/13 | 1111678 | 1011 | CONNECTICUT AVE | NW | 6/10/13 | 27213 | 2G833 | (Light out) |  | High Pressure Sodium | 38.90292468000 | -77.03936525000
6/7/13 | 1111540 | 0 | 7TH ST | NW | 6/7/13 | 25703 | 6A818 | (Light out) |  | High Pressure Sodium | 38.91121698000 | -77.02181678000
6/7/13 | 1111536 | 610 | H ST | NW | 6/7/13 | 22559 | 6M700 | (Light out) |  | High Pressure Sodium | 38.89973402000 | -77.02073448000
6/7/13 | 1111511 | 616 | E ST | NW | 6/7/13 | 23329 | 2M344 | (Light out) |  | High Pressure Sodium | 38.89622042000 | -77.02109786000
6/7/13 | 1111503 | 0 | 7TH ST | NW | 6/7/13 | 22411 | 6M684 | (Light out) |  | High Pressure Sodium | 38.90163849000 | -77.02201799000
6/7/13 | 1111501 | 0 | 22ND ST | NW | 6/7/13 | 24268 | 2A055 | (Light out) |  | High Pressure Sodium | 38.91118772000 | -77.04866913000
6/7/13 | 1111475 | 300 | D ST | SW | 6/7/13 | 21632 | 6L647 | (Light out) |  | High Pressure Sodium | 38.88513746000 | -77.01599912000
6/7/13 | 1111453 | 1332 | 35TH ST | NW | 6/7/13 | 20903 | 2G192 | (Light out) |  | High Pressure Sodium | 38.90762144000 | -77.06910533000
6/6/13 | 1111344 | 2400 | 14TH ST | NW | 6/6/13 | 12048 | 1A046 | (Light out) |  | High Pressure Sodium | 38.92087041000 | -77.03196022000
6/6/13 | 1111325 | 3200 | KENYON PL | NW | 6/6/13 | 14683 | 1G052 | (Light out) |  | High Pressure Sodium | 38.93003166000 | -77.03236323000
6/5/13 | 1111249 | 2721 | PENNSYLVANIA AVE | SE | 7/31/13 | 78571DC | 7E082 | (Light out) | BCM 7-31-13 - This is an old pole number that is not in use anymore due to SL Project upgrading to Teardrop fixtures. Which the new pole numbers are not yet entered into iSlims. KB-6/10/2013-1:05PM. THE ARM AND LIGHT FIXTURE ARE MISSING. NEED TO INSTALL | High Pressure Sodium | 38.87220266000 | -76.96783710000
| 1111228 | 3616 | BANGOR ST | SE | 6/8/13 | 74817DC | 7A085DC | (Light out) | 6592-6/7/2013-10:45PM. REPLACED 250 W HPS AND PHOTOCELL. 13-00131510-Light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86054136000 | -76.95538027000
5/30/13 | 1110852 | 1350 | CONNECTICUT AVE | NW | 6/18/13 | 24527 | 2U491 | (Light out) | 397, 9250. 06/04/2013. Both the lamp and photo cell are intact. However, there is a short causing the light to be inoperable. 13-00125779-Light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90838138000 | -77.04291014000
| 1110764 | 800 | 12TH ST | NE | 6/13/13 | 62461 | 6S167 | (Light out) | MD-06/04/13-12:20AM-REPAIRED LIGHT 13-00124591-Light out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90029932000 | -76.99009243000
5/29/13 | 1110748 | 1517 | TUBMAN RD | SE | 5/29/13 | 81801 | 88078 | (Light out) |  | High Pressure Sodium | 38.84828043000 | -76.98176787000
5/29/13 | 1110715 | 0 | EAST CAPITOL ST | NE | 5/29/13 | 73560 | 73560DC | (Light out) |  | High Pressure Sodium | 38.88963991000 | -76.91490257000
5/29/13 | 1110699 | 0 | EAST CAPITOL ST | NE | 5/29/13 | 73561 | 73561DC | (Light out) |  | High Pressure Sodium | 38.88964269000 | -76.91530308000
| 1110646 | 2201 | L ST | NW | 6/4/13 | 24592 | 2G710 | (Light out) | TA. 06/03/2013. replaced photocell. Operational upon departure. 13-00123467-Light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90381203000 | -77.04905931000
5/24/13 | 1110545 | 0 | O ST | NW | 5/29/13 | 25844 | 6U450 | (Light out) | MD-5-29-2013-4:50AM. LOCATED IN CONSTRUCTION AREA. 13-00121611-Light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90864165000 | -77.02306302000
5/24/13 | 1110479 | 5127 | H ST | SE | 5/24/13 | 75492 | 75492DC | (Light out) |  | High Pressure Sodium | 38.87810752000 | -76.92948653000
5/24/13 | 1110474 | 4930 | NANNIE HELEN BURROUGHS AVE | NE | 5/24/13 | 71279DC | 7A213 | (Light out) |  | High Pressure Sodium | 38.89845445000 | -76.92986688000
5/24/13 | 1110443 | 0 | KENILWORTH AVE | NE | 5/24/13 | 70311 | 7M067 | (Light out) |  | High Pressure Sodium | 38.90629475000 | -76.93975849000
5/24/13 | 1110428 | 5334 | NANNIE HELEN BURROUGHS AVE | NE | 5/24/13 | 72643DC | 7A197 | (Light out) |  | High Pressure Sodium | 38.89845128000 | -76.92456414000
| 1110404 | 1400 | L ST | NW | 6/8/13 | 27352 | 2M417 | (Light out) | CH-6/8/2013-4:35AM. AT THIS LOCATION NO POLE TAG#27352. THE ONE NOT WORKIG AT THIS LOCATION IS POLE 2M399 COMBO POLE. REPLACED 250 W HPS LAMP. 100% COMPLETE. 06/5/2012 TN: this is 1400 block of L Street. pole tag # 27352. REFER TO DDOT - TRAFFIC C | High Pressure Sodium | 38.90364351000 | -77.03208379000
5/23/13 | 1110328 | 0 | O ST | NE | 5/23/13 | 62314 | 5M113 | (Light out) |  | High Pressure Sodium | 38.90852329000 | -77.00447657000
5/23/13 | 1110325 | 122 | C ST | NW | 5/23/13 | 60960 | 68292 | (Light out) |  | High Pressure Sodium | 38.89365430000 | -77.01227034000
5/23/13 | 1110317 | 600 | 5TH ST | NW | 5/23/13 | 60550 | 68367 | (Light out) |  | High Pressure Sodium | 38.89749142000 | -77.01979745000
5/23/13 | 1110314 | 933 | K ST | SE | 5/23/13 | 67656 | 6B428 | (Light out) |  | High Pressure Sodium | 38.87847018000 | -76.99984439000
5/23/13 | 1110308 | 476 | K ST | NW | 5/23/13 | 60469 | 6A108 | (Light out) |  | High Pressure Sodium | 38.90245377000 | -77.01877131000
5/23/13 | 1110307 | 476 | K ST | NW | 5/29/13 | 60469 | 6A108 | (Light out) | 6592-30482-5-28-2013-1:05am. NEED 2 mh 175/U/MED LAMP. | High Pressure Sodium | 38.90245377000 | -77.01877131000
5/23/13 | 1110300 | 900 | 3RD ST | SE | 5/23/13 | 67530 | 6A454 | (Light out) |  | High Pressure Sodium | 38.87919095000 | -77.00197695000
5/23/13 | 1110293 | 33 | PATTERSON ST | NE | 5/23/13 | 61267 | 6U241 | (Light out) |  | High Pressure Sodium | 38.90640945000 | -77.00861364000
5/23/13 | 1110273 | 3402 | 15TH ST | NE | 5/23/13 | 51213DC | 5A102DC | (Light out) |  | High Pressure Sodium | 38.93214204000 | -76.98444256000
5/23/13 | 1110256 | 2902 | BLADENSBURG RD | NE | 5/23/13 | 51236DC | 5A132DC | (Light out) |  | High Pressure Sodium | 38.92743073000 | -76.96259421000
5/22/13 | 1110039 | 5326 | CONNECTICUT AVE | NW | 5/22/13 | 30542 | 3E017 | (Light out) |  | High Pressure Sodium | 38.96076273000 | -77.07303810000
5/22/13 | 1110037 | 3213 | M ST | NW | 5/22/13 | 33001 | 2A104 | (Light out) |  | Mercury Vapor | 38.90558059000 | -77.06488983000
5/21/13 | 1109971 | 3600 | O ST | NW | 5/21/13 | 21093 | 2G154 | (Light out) |  | High Pressure Sodium | 38.90765947000 | -77.07043171000
5/21/13 | 1109954 | 1435 | NEWTON ST | NW | 5/21/13 | 13913 | 1G072 | (Light out) |  | High Pressure Sodium | 38.93143118000 | -77.03279918000
5/21/13 | 1109953 | 600 | S ST | NW | 5/21/13 | 14382 | 1G601 | (Light out) |  | High Pressure Sodium | 38.91444559000 | -77.02127006000
5/21/13 | 1109933 | 2400 | SHERMAN AVE | NW | 5/21/13 | 12585 | 1G465 | (Light out) |  | High Pressure Sodium | 38.92169397000 | -77.02539372000
5/21/13 | 1109899 | 750 | I ST | NW | 5/21/13 | 22481 | 2M183 | (Light out) |  | High Pressure Sodium | 38.90094560000 | -77.02237583000
5/16/13 | 1109728 | 18 | 3RD ST | SE | 5/18/13 | 6A003 | 6A003 | (Light out) | 6592,30482-5-18-2013-1:35AM. REPLACED 300 WATT INCANDESCENT LAMP. 13-00114487-light out cwDesc: STREETLIGHT REPAIR | Incandescent | 38.87723028000 | -77.00452085000
| 1109729 | 100 | 3RD ST | SE | 5/21/13 | 6A002 | 6A002 | (Light out) | 6592,30842-5-18-2013-1:25AM. REPLACED 300 WATT INCANDESCENT LAMP. 13-00114491-light out cwDesc: STREETLIGHT REPAIR | Incandescent | 38.87703665000 | -77.00445216000
5/16/13 | 1109667 | 0 | KENILWORTH AVE | SE |  | 79497 | 7A150 | (No current) | REFER TO DDOT - NEED ASSISTANCE TO REMOVE JERSEY WAY TO ALLOW OUR BUCKET TRUCK INSIDE AREA | High Pressure Sodium | 38.88456308000 | -76.96344581000
| 1109657 | 1748 | EAST CAPITOL ST | NE |  | 63712 | 6A501 | (Light out) | BCM - 5-20-13 - REFER TO DDOT IN CONSTRUCTION SITE- NO ACCESS MD-05/17/13- 12:55AM- NO CURRENT 13-00113648-All the streetlighs on the South Side of E. Cap by 17th St are out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88973040000 | -76.97991030000
5/9/13 | 1109327 | 100 | STODDERT PL | SE | 5/9/13 | 70028 | 74231 | (Light out) | MD-05/08/13-11:00PM-REPLACED LAMP AND PHOTOCELL. 100% COMPLETE | High Pressure Sodium | 38.88967004000 | -76.94839956000
5/6/13 | 1108879 | 1748 | EAST CAPITOL ST | NE |  | 63712 | 6A501 | (Light out) | REFER TO DDOT - SL POLE IS IN CONSTRUCTION AREA os 5/9/13 9:30 pm - NO CURRENT FOUND. 13-00104452-light out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88973040000 | -76.97991030000
5/2/13 | 1108666 | 100 | STODDERT PL | SE | 5/9/13 | 70028 | 74231 | (Light out) | MD-05/08/13-11:00PM- REPLACED LAMP AND PHOTOCELL. 100% COMPLETE | High Pressure Sodium | 38.88967004000 | -76.94839956000
4/29/13 | 1108520 | 5928 | GEORGIA AVE | NW | 12/17/14 | 4E220 | 4A828 | (Light out) | TA 5-4-13 10:50A - NO ACCESS TO MH. HAVE NO ACCESS TO T-BASE DUE TO CONSTRUCTION SITE. MD-04/30/13-12:05AM- NO CURRENT | High Pressure Sodium | 38.96245901000 | -77.02779791000
4/25/13 | 1108371 | 4469 | WISCONSIN AVE | NW | 4/26/13 | 30131 | 3L465 | (Light out) | 6592, MELVIN P-4/26/2013-3:50AM. REPALCED PHOTOCELL. LIGHTS ARE ON. | High Pressure Sodium | 38.94724720000 | -77.06516811000
4/23/13 | 1108208 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79467 | 7A131 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88310417000 | -76.96392124000
4/23/13 | 1108207 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79466 | 7A130 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88384591000 | -76.96362320000
4/23/13 | 1108206 | 0 | KENILWORTH AVE | SE | 4/23/13 | 79495 | 7A148 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88589091000 | -76.96283495000
4/23/13 | 1108205 | 0 | KENILWORTH AVE | SE | 4/23/13 | 79496 | 7A149 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88522570000 | -76.96311007000
4/23/13 | 1108204 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79494 | 7A147 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88656390000 | -76.96255943000
4/23/13 | 1108203 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79493 | 7A146 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88732787000 | -76.96219078000
4/23/13 | 1108194 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79491 | 7A160 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88928656000 | -76.95990942000
4/23/13 | 1108193 | 0 | KENILWORTH AVE | NE | 4/23/13 | 79463 | 7A127 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88994563000 | -76.95813630000
4/23/13 | 1108192 | 0 | KENILWORTH AVE | NE | 4/23/13 | 79462 | 7A126 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.89001850000 | -76.95803705000
4/23/13 | 1108191 | 0 | KENILWORTH AVE | NE | 4/23/13 | 79461 | 7A125 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.89037514000 | -76.95748332000
4/23/13 | 1108188 | 908 | EASTERN AVE | NE | 4/23/13 | 79483 | 7A152 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88978699000 | -76.95795735000
4/23/13 | 1108187 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79482 | 7A151 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88927741000 | -76.95876088000
4/23/13 | 1108186 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79481 | 7A145 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88647157000 | -76.96221690000
4/23/13 | 1108185 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79480 | 7A144 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88580800000 | -76.96248765000
4/23/13 | 1108184 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79479 | 7A143 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88513632000 | -76.96276237000
4/23/13 | 1108183 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79478 | 7A142 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88446501000 | -76.96303530000
4/23/13 | 1108182 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79477 | 7A141 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88375073000 | -76.96332098000
4/23/13 | 1108181 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79476 | 7A140 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88303360000 | -76.96361101000
4/23/13 | 1108180 | 809 | EASTERN AVE | NE | 4/23/13 | 79475 | 7A139 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88244563000 | -76.96384495000
4/23/13 | 1108179 | 809 | INTERSTATE 295 | NE | 4/23/13 | 79474 | 7A138 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88176234000 | -76.96414383000
4/23/13 | 1108178 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79473 | 7A137 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88109425000 | -76.96448919000
4/23/13 | 1108177 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79472 | 7A136 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88045569000 | -76.96488247000
4/23/13 | 1108176 | 803 | EASTERN AVE | NE | 4/23/13 | 79471 | 7A135 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88055222000 | -76.96517808000
4/23/13 | 1108175 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79470 | 7A134 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88120301000 | -76.96478109000
4/23/13 | 1108174 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79469 | 7A133 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL - REFER TO WO#1108173 FOR MATERIALS USED. | High Pressure Sodium | 38.88182711000 | -76.96446211000
4/23/13 | 1108173 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79468 | 7A132 | (Light out) | TA 4-23-13 9:30AM - MADE SPLICE IN MH. REPLACE PHOTOCELL | High Pressure Sodium | 38.88252291000 | -76.96415772000
4/23/13 | 1108172 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79467 | 7A131 | (Light out) |  | High Pressure Sodium | 38.88310417000 | -76.96392124000
4/23/13 | 1108171 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79466 | 7A130 | (Light out) |  | High Pressure Sodium | 38.88384591000 | -76.96362320000
4/23/13 | 1108170 | 0 | KENILWORTH AVE | SE | 4/23/13 | 79496 | 7A149 | (Light out) |  | High Pressure Sodium | 38.88522570000 | -76.96311007000
4/23/13 | 1108169 | 0 | KENILWORTH AVE | SE | 4/23/13 | 79495 | 7A148 | (Light out) |  | High Pressure Sodium | 38.88589091000 | -76.96283495000
4/23/13 | 1108168 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79494 | 7A147 | (Light out) |  | High Pressure Sodium | 38.88656390000 | -76.96255943000
4/23/13 | 1108167 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79493 | 7A146 | (Light out) |  | High Pressure Sodium | 38.88732787000 | -76.96219078000
4/23/13 | 1108158 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79482 | 7A151 | (Light out) |  | High Pressure Sodium | 38.88927741000 | -76.95876088000
4/23/13 | 1108157 | 908 | EASTERN AVE | NE | 4/23/13 | 79483 | 7A152 | (Light out) |  | High Pressure Sodium | 38.88978699000 | -76.95795735000
4/23/13 | 1108155 | 0 | ANACOSTIA FWY | SE | 4/23/13 | 79491 | 7A160 | (Light out) |  | High Pressure Sodium | 38.88928656000 | -76.95990942000
4/23/13 | 1108154 | 0 | ANACOSTIA FWY | NE | 4/23/13 | 79490 | 7A159 | (Light out) |  | High Pressure Sodium | 38.88986353000 | -76.95869496000
4/23/13 | 1108153 | 0 | KENILWORTH AVE | NE | 4/23/13 | 79461 | 7A125 | (Light out) |  | High Pressure Sodium | 38.89037514000 | -76.95748332000
4/23/13 | 1108152 | 0 | KENILWORTH AVE | NE | 4/23/13 | 79463 | 7A127 | (Light out) |  | High Pressure Sodium | 38.88994563000 | -76.95813630000
4/23/13 | 1108151 | 0 | KENILWORTH AVE | NE | 4/23/13 | 79462 | 7A126 | (Light out) |  | High Pressure Sodium | 38.89001850000 | -76.95803705000
| 1107945 | 1500 | KEARNEY ST | NE | 4/17/13 | 59986 | 5A177 | (Light out) | 6592-4-16-2013-8:45PM. REPLACED 300 WATT LAMP. 13-00084785- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91401980000 | -77.01759054000
3/21/13 | 1107287 | 2826 | BLADENSBURG RD | NE | 4/5/13 | 51239DC | 5A135DC | (Light out) | 5503/9070 - 4-4-13 12:50 AM REPLACED PHOTOCELL AND LAMP. 13-00063216- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92654970000 | -76.96367069000
3/21/13 | 1107277 | 3230 | PENNSYLVANIA AVE | SE | 4/2/13 | 78549DC | 7E106 | (Light out) |  | High Pressure Sodium | 38.86896025000 | -76.95979555000
3/21/13 | 1107276 | 3144 | PENNSYLVANIA AVE | SE | 4/11/13 | 78554DC | 7E101DC | (Light out) | 78554DC - NO CURRENT | High Pressure Sodium | 38.86981292000 | -76.96183892000
3/21/13 | 1107274 | 0 | SHERIDAN RD | SE | 4/6/13 | 81365DC | 8M049 | (Light out) |  | High Pressure Sodium | 38.85966279000 | -76.99341499000
3/21/13 | 1107273 | 0 | SHERIDAN RD | SE | 4/6/13 | 81364DC | 8M048 | (Light out) | TA went to this pole and light was found to be working. however, light on pole 8M048 was found defective and he replaced the 250W HPS and it corrected the problem. Light working upon depatrure. | High Pressure Sodium | 38.85942886000 | -76.99337741000
3/21/13 | 1107255 | 4000 | SOUTHERN AVE | SE | 4/11/13 | 78576 | 78576DC | (Light out) | WD 4-11-13 12:30PM - pULLED NEW CONDUCTOR WIRE AND TERMINATED SPLICES IN MH TA found no current at this pole. A910PM and C 910PM. | High Pressure Sodium | 38.86379385000 | -76.94657249000
3/21/13 | 1107254 | 3945 | PENNSYLVANIA AVE | SE | 4/6/13 | 78518DC | 7E149DC | (Light out) | TA replaced a 400W HPS lamp. Problem resolved and light was working upon departure. | High Pressure Sodium | 38.86392263000 | -76.94743025000
3/20/13 | 1107195 | 1475 | BRUCE PL | SE | 3/21/13 | 81731 | 88008 | (Light out) | DA 3/20/13 Rickard repaired pole 81731 | High Pressure Sodium | 38.85043302000 | -76.98303184000
3/20/13 | 1107193 | 1524 | TANNER CT | SE | 3/21/13 | 81771 | 88048 | (Light out) | DA 3/20/13 Rickard repaired pole 81771 | High Pressure Sodium | 38.84771521000 | -76.98170485000
3/20/13 | 1107181 | 521 | G ST | NW | 3/20/13 | 60667 | 60081 | (Light out) | DA 3/20/13 Favors repaired pole 60667 | Incandescent | 38.89840382000 | -77.01908312000
3/19/13 | 1107095 | 0 | L ST | NW | 12/22/13 | 24637 | 2G783 | (Light out) | DA 3/18/13 Favors/Buigre pole 24637 Temp pole NC Underground low voltage 27 volts - NO CURRENT PENDING | High Pressure Sodium | 38.90367717000 | -77.04866329000
3/18/13 | 1107077 | 4300 | GEORGIA AVE | NW | 3/19/13 | 4K516 | 4G310 | (Light out) | DA 3/19/13 Hill/Gary repaired pole 4k516 | High Pressure Sodium | 38.94386006000 | -77.02614886000
| 1107034 | 1133 | CONNECTICUT AVE | NW | 3/19/13 | 27219 | 2U550 | (Light out) | DA 3/18/13 Favors/Buige repaired pole 27219 13-00059867-Light is out behind 1215 CT AVE NW cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90491369000 | -77.04052615000
3/18/13 | 1107031 | 2606 | BOWEN RD | SE | 3/20/13 | 81380DC | 8M044 | (Light out) | DA 3/19/13 Richard/Hutchins pole 81380dc | High Pressure Sodium | 38.85914186000 | -76.99291332000
3/18/13 | 1107030 | 2606 | BOWEN RD | SE | 3/20/13 | 81379DC | 8M042 | (Light out) | DA 3/20/13 Rickard/hutchins pole 81379dc on and working refer to 1106444 | High Pressure Sodium | 38.85930440000 | -76.99289157000
3/18/13 | 1107029 | 0 | SAYLES PL | SE | 3/20/13 | 81374DC | 88115 | (Light out) | DA 3/19/13 Richard/Hutchins pole 81374dc | High Pressure Sodium | 38.86067966000 | -76.99269860000
3/18/13 | 1107023 | 0 | SHERIDAN RD | SE | 3/19/13 | 81364DC | 8M048 | (Light out) | DA 3/18/13 Rickard/Hutchins repaired pole 81364dc | High Pressure Sodium | 38.85942886000 | -76.99337741000
3/14/13 | 1106852 | 1700 | RHODE ISLAND AVE | NW | 3/14/13 | 26383 | 2U538 | (Light out) | DA 3/14/13 Favors/Buige repaired pole 26383 | High Pressure Sodium | 38.90590732000 | -77.04061898000
3/13/13 | 1106794 | 5928 | GEORGIA AVE | NW | 12/22/13 | 4E220 | 4A828 | (Light out) | DA 3/17/13 Hill/ Gary pole 4E220 NC @ Base NO CURRENT PENDING | High Pressure Sodium | 38.96245901000 | -77.02779791000
3/12/13 | 1106748 | 44 | H ST | NW | 3/14/13 | 60389 | 6A223 | (Light out) | DA 3/14/13 Favors/Buige repaired pole 60389 | High Pressure Sodium | 38.90031219000 | -77.01173524000
3/12/13 | 1106706 | 600 | 5TH ST | NW | 3/25/13 | 60083 | 6S528 | (Light out) | DA 3/14/13 Favors/Buige pole 60708 or 6S528 NCU NO CURRENT PENDING Duplicate WO#1107167 - 600 5th Street NW - 3/20/2013 | High Pressure Sodium | 38.89745914000 | -77.01883966000
3/12/13 | 1106704 | 3220 | CONNECTICUT AVE | NW | 3/13/13 | 30082 | 3M128 | (Light off/on) | DA 3/12/13 Arrington repaired pole 30082 | High Pressure Sodium | 38.93343112000 | -77.05739079000
3/11/13 | 1106554 | 58 | 58TH ST | SE | 5/16/13 | 73650DC | 7A062DC | (Light out) | DA 3/14/13 Favors/Buige pole 73650dc this light is behind a fenced area that is locked and is not accessable | Incandescent | 38.88902649000 | -76.91686911000
3/11/13 | 1106544 | 4651 | BENNING RD | SE | 3/14/13 | 75822 | 75822DC | (Light out) | DA 3/14/13 Rickard/Hutchins repaired pole 75822 repaired wire in powerdoor | High Pressure Sodium | 38.87611644000 | -76.93130301000
3/11/13 | 1106519 | 0 | NEW YORK AVE | NW | 3/12/13 | 22913 | 2L062 | (Light out) | DA 3/12/13 FAvors/Buige repaired pole 22913 | High Pressure Sodium | 38.90113457000 | -77.02657407000
3/10/13 | 1106497 | 3440 | WISCONSIN AVE | NW | 3/12/13 | 38771 | 3U404 | (Light out) | 13-00053631-Streetlight Repair 3401-3499 Idaho Avenue Northwest, Washington, DC 20016, USA Street light always on cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93547449000 | -77.07299335000
3/8/13 | 1106444 | 2606 | BOWEN RD | SE | 3/12/13 | 81379DC | 8M042 | (Light out) | DA 3/11/13 Rickard/Hutchins repaired pole 81379dc | High Pressure Sodium | 38.85930440000 | -76.99289157000
3/8/13 | 1106443 | 0 | SAYLES PL | SE | 3/12/13 | 81374DC | 88115 | (Light out) | DA 3/12/13 Rickard/Hutchins repaired pole 81374dc | High Pressure Sodium | 38.86067966000 | -76.99269860000
3/8/13 | 1106442 | 0 | SHERIDAN RD | SE | 3/12/13 | 81364DC | 8M048 | (Light out) | DA 3/11/13 Rickard/Hutchins repaired pole 81364dc secured starter | High Pressure Sodium | 38.85942886000 | -76.99337741000
3/8/13 | 1106421 | 0 | 4TH ST | SW | 3/13/13 | 21594 | 6A379 | (Light out) | WBlack-will schedule for next MOT route DA 3/10/13 Favors pole 21594 request for map | High Pressure Sodium | 38.88674391000 | -77.01372694000
3/8/13 | 1106401 | 2319 | PENNSYLVANIA AVE | NW | 3/8/13 | 24653 | 2G667 | (Light out) | DA 3/8/13 Favors/Buige repaire pole 24653 | High Pressure Sodium | 38.90301348000 | -77.05112594000
3/7/13 | 1106349 | 0 | FIRTH STERLING AVE | SE | 3/8/13 | 81557DC | 8M085 | (Light out) | DA 3/7/13 Rickard/Hutchins repaired pole 81557dc | High Pressure Sodium | 38.86188851000 | -76.99918765000
3/7/13 | 1106344 | 3214 | 15TH PL | SE | 3/8/13 | 81717 | 87994 | (Light out) | DA 3/7/13 Rickard/Hutchins repaired pole 81717 secured photocell | High Pressure Sodium | 38.84944405000 | -76.98207051000
3/7/13 | 1106343 | 3136 | 15TH PL | SE | 3/11/13 | 81712 | 87989 | (Light out) | 3-7-13 Hutchins/Rickard--n/c underground NO CURRENT PENDING 3-11-2013 Al Young--install 150hps lamp, tlpc | High Pressure Sodium | 38.85063867000 | -76.98193762000
3/6/13 | 1106272 | 0 | 23RD ST | NW | 3/8/13 | 24656 | 2G673 | (Light out) | DA 3/8/13 Favors/Buige repaired pole 24656 Alley 13-00050783-2 lights are out in the alley south of Q Street NW between 15th & 16th street NW. 26456 is just east of 16th street. 26453 is midway through the alley and is covered with ivy. Also, 26456 i | High Pressure Sodium | 38.90314639000 | -77.05003724000
3/6/13 | 1106202 | 775 | H ST | NE | 3/7/13 | 61991 | 6S197 | (Light out) | DA 3/7/13 Rickard/Hutchins pole 61991 light is on and working | High Pressure Sodium | 38.90030060000 | -76.99586046000
| 1106186 | 2311 | 33RD ST | SE | 3/7/13 | 74837DC | 7A101DC | (Light out) | DA 3/7/13 Rickard/Hutchins repaired pole 74837dc secured photocell 13-00050544-3 doors down from this address cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86135172000 | -76.96056260000
3/5/13 | 1106129 | 5928 | GEORGIA AVE | NW | 3/6/13 | 4E220 | 4A828 | (Light out) | DA 3/5/13 Hill/Thompson repaired pole 4e220 | High Pressure Sodium | 38.96245901000 | -77.02779791000
3/4/13 | 1106040 | 3220 | CONNECTICUT AVE | NW | 3/5/13 | 30082 | 3M128 | (Light off/on) | DA 3/5/13 Arrington repaired pole 30082 | High Pressure Sodium | 38.93343112000 | -77.05739079000
3/4/13 | 1105992 | 0 | NEW HAMPSHIRE AVE | NW | 3/4/13 | 23850 | 2G760 | (Light out) | DA 3/4/13 FAvors/Buige repaired pole 23850 | High Pressure Sodium | 38.90716866000 | -77.04587425000
3/1/13 | 1105916 | 0 | C ST | SW | 3/4/13 | 21786 | 6A357 | (Light out) | DA 3/3/13 Favors/Buige new construction transferred pole id tag to new poles | High Pressure Sodium | 38.88598785000 | -77.01417875000
3/1/13 | 1105915 | 0 | C ST | SW | 3/4/13 | 21787 | 6A355 | (Light out) | DA 3/3/13 Favors/Buige new construction transferred pole id tag to new poles | High Pressure Sodium | 38.88598751000 | -77.01461550000
3/1/13 | 1105818 | 0 | NEW HAMPSHIRE AVE | NW | 3/5/13 | 24483 | 2G776 | (Light out) | DA 3/5/13 Favors/Buige repaired pole 24483 | High Pressure Sodium | 38.90893171000 | -77.04399572000
3/1/13 | 1105814 | 0 | 13TH ST | NW | 3/11/13 | 22828 | 27285 | (Light dim) | DA 3/5/13 Favors/Buige pole 22828 NCU NO CURRENT UNDERGROUND 3-11-2013 AL Young--BAD ADDRESS | High Pressure Sodium | 38.90239968000 | -77.02978601000
3/1/13 | 1105785 | 4625 | 13TH ST | NW | 3/5/13 | 4K417 | 4U123 | (Light out) | DA 3/5/13 Hill/Thompson repaired pole 4K417 | High Pressure Sodium | 38.94669824000 | -77.02961658000
2/28/13 | 1105733 | 4700 | NORTH CAPITOL ST | NE | 3/1/13 | 4R754 | 4A795 | (Light out) | DA 2/28/13 Hill/Thompson repaired pole 4r754 | High Pressure Sodium | 38.94814388000 | -77.00879153000
2/28/13 | 1105705 | 0 | NEW HAMPSHIRE AVE | NW | 3/12/13 | 24483 | 2G776 | (Light out) | DA 3/1/13 Favors/Buige pole 24483 needs 400 fixture 3-12-2013 AL Young--FOUND OK | High Pressure Sodium | 38.90893171000 | -77.04399572000
2/28/13 | 1105704 | 1270 | NEW HAMPSHIRE AVE | NW | 3/7/13 | 23873 | 2G758 | (Light out) | Same as W.O. 1103965 (No current) 23873 DA 2/11/13 Favors/Buige pole 23873 NC Underground - NO CURRENT PENDING 2-15-2013 J.Lancaster--Joy construction on site removing pole and foundation | High Pressure Sodium | 38.90672638000 | -77.04606427000
| 1105691 | 3223 | SHERMAN AVE | NW | 3/5/13 | 12872 | 1L273 | (Light out) | 3/5/13 TN: this is the new construction. the contractor just had PEPCO energize the streetlight poles. DA 3/1/13 new pole consturction 13-00045755-This light is on for two weeks, never get off cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93042323000 | -77.02636750000
2/26/13 | 1105636 | 0000 | NANNIE HELEN BURROUGHS AVE | NE | 3/1/13 | 70029 | 7A059 | (Light off/on) | DA 2/28/13 Rickard/Hutchins repaired pole 70029 | High Pressure Sodium | 38.89830988000 | -76.91657202000
2/25/13 | 1105555 | 0000 | INTERSTATE 395 | SW | 2/27/13 | 395-005S-4 | 395S237 | (Navigation light out) | K. Greenfield on 2/26/12. Installed two 67w inc lamps. On navigation light is a no-current. 2-27-2013 K.Greenfield--Install four 67w inc. lamps | High Pressure Sodium | 38.87715942000 | -77.04101811000
2/25/13 | 1105554 | 0000 | INTERSTATE 395 | SW | 12/22/13 | 395-005S-4 | 395S237 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.87715942000 | -77.04101811000
2/25/13 | 1105553 | 0 | INTERSTATE 395 | NW | 12/22/13 | 395-005N-4 | 395N234 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.87624339000 | -77.04138535000
2/25/13 | 1105552 | 0000 | INTERSTATE 395 | SW | 12/22/13 | 395-003S-4 | 395S235 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.87847753000 | -77.03939283000
2/25/13 | 1105551 | 0000 | INTERSTATE 395 | SW | 12/22/13 | 395-003N-4 | 395N230 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.87838840000 | -77.03926247000
2/25/13 | 1105550 | 0000 | INTERSTATE 395 | SW | 12/22/13 | 395-003N-2 | 395N222 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.87943190000 | -77.03237272000
2/25/13 | 1105515 | 2430 | 32ND ST | SE | 2/26/13 | 74753DC | 7A067DC | (Light off/on) | DA 2/25/13 Hall/Thompson repaired pole 74753dc | High Pressure Sodium | 38.85947899000 | -76.96089343000
2/25/13 | 1105415 | 0000 | INTERSTATE 395 | SW | 3/11/13 | 395-055N-4 | 395N608 | (Overhead guide sign light out) | R. Arrington completed on 3/8/13. Installed two 150w hps lamp. | High Pressure Sodium | 38.88226944000 | -77.01480955000
2/25/13 | 1105409 | 0 | INTERSTATE 395 | SW | 12/22/13 | 395-022N-9 | 395N612 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88233608000 | -77.01846985000
2/25/13 | 1105406 | 0000 | INTERSTATE 395 | SW | 12/22/13 | 395-015N-5 | 395N220 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88059592000 | -77.03064406000
2/25/13 | 1105400 | 0000 | INTERSTATE 395 | SW | 12/22/13 | 395-011N-3 | 395N224 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.87906148000 | -77.03367357000
2/19/13 | 1104785 | 0 | 4TH ST | SW | 2/21/13 | 21594 | 6A379 | (Light off/on) | waiting MOT schedule | High Pressure Sodium | 38.88674391000 | -77.01372694000
2/19/13 | 1104766 | 0 | MAPLE ST | NW | 2/20/13 | 4H592DC | 4L608 | (Light off/on) | DA 2/19/13 Hill/Thompson repaired pole 4H592dc | High Pressure Sodium | 38.97445255000 | -77.01510221000
2/19/13 | 1104765 | 0 | MAPLE ST | NW | 2/20/13 | 4H589DC | 4L603 | (Light off/on) | DA 2/19/13 Hill/Thompson repaired pole 4H589dc | High Pressure Sodium | 38.97428343000 | -77.01522309000
2/19/13 | 1104759 | 0000 | PENNSYLVANIA AVE | SE | 2/20/13 | 68309 | 65357 | (Light out) | DA 2/19/13 Rickard/Hutchins repaired pole 68309 light found on and working | High Pressure Sodium | 38.88034949000 | -76.98507594000
2/19/13 | 1104749 | 0 | 3RD ST | NE | 2/20/13 | 4P470DC | 4U156 | (Light off/on) | DA 2/19/13 Hall/Thompson repaired pole 4P470dc | High Pressure Sodium | 38.95890737000 | -77.00284046000
2/15/13 | 1104627 | 3170 | BLADENSBURG RD | NE | 2/20/13 | 51230DC | 5A126DC | (Light off/on) | DA 2/20/13 Rickard/Hutchins repaired pole 51230dc | High Pressure Sodium | 38.92882531000 | -76.96080667000
2/13/13 | 1104565 | 819 | 6TH ST | NW | 2/15/13 | 60541 | 6M706 | (Light off/on) | DA 2/15/13 Rickard/Hutchins repaired poles 60541 | High Pressure Sodium | 38.90043550000 | -77.01979597000
2/13/13 | 1104563 | 1133 | CONNECTICUT AVE | NW | 2/25/13 | 27219 | 2U550 | (Light off/on) | DA 2/18/13 Favors/Buige pole 27219 Temp pole NC Underground - NO CURRENT PENDING 2-25-2013 AL Young--found ok | High Pressure Sodium | 38.90491369000 | -77.04052615000
2/12/13 | 1104451 | 0 | WASHINGTON AVE | SW | 2/15/13 | 21662 | 6A381 | (Light out) | DA 2/15/13 Favors/Buige repaired pole 21662 right side twin light | High Pressure Sodium | 38.88686324000 | -77.01343008000
2/12/13 | 1104446 | 0 | 4TH ST | SW | 2/19/13 | 21594 | 6A379 | (Light out) | DA 1/18/13 could not locate | High Pressure Sodium | 38.88674391000 | -77.01372694000
2/12/13 | 1104404 | 0 | BROAD BRANCH TER | NW | 2/15/13 | 34711DC | 34730DC | (Light out) | DA 2/14/13 Arrington repaired pole 34711dc | High Pressure Sodium | 38.95576043000 | -77.06567453000
2/12/13 | 1104380 | 3217 | CONNECTICUT AVE | NW | 2/14/13 | 30100 | 30427 | (Light out) | DA 2/13/13 Arrington repaired pole 30100 | High Pressure Sodium | 38.93294186000 | -77.05685295000
2/12/13 | 1104374 | 1318 | 45TH PL | SE | 2/15/13 | 75843 | 75843DC | (Light off/on) | DA 2/15/13 Rickard/Hutchins repaired pole 75843 | High Pressure Sodium | 38.87412284000 | -76.93443579000
2/11/13 | 1104258 | 5928 | GEORGIA AVE | NW | 2/14/13 | 4E220 | 4A828 | (Light out) | DA 2/14/13 Hill/Thompson repaired pole 4E220 | High Pressure Sodium | 38.96245901000 | -77.02779791000
2/7/13 | 1104058 | 0 | 7TH ST | NW | 2/15/13 | 22455 | 6M667 | (Light out) | DA 2/10/13 Favors/Buige pole 22455 NC Underground - NO CURRENT PENDING 2-15-2013 J.Lancaster--install 90ft #10 wire, 4 hot links | High Pressure Sodium | 38.90101301000 | -77.02181903000
2/7/13 | 1104041 | 0 | M ST | NW | 2/13/13 | 23728 | 2U535 | (Light out) | DA 2/13/13 FAvors/Buige repaired pole 23728 | High Pressure Sodium | 38.90574873000 | -77.04183268000
2/7/13 | 1103991 | 0 | ANACOSTIA FWY | SE | 2/12/13 | 79473 | 7A137 | (Light out) | DA 2/12/13 Rickard/Hutchins no access to rear of this location DA 2/7/13 Hill/Thompson no access to alley - alley was blocked off | High Pressure Sodium | 38.88109425000 | -76.96448919000
2/7/13 | 1103965 | 1270 | NEW HAMPSHIRE AVE | NW | 12/20/13 | 23873 | 2G758 | (Light out) | DA 2/11/13 Favors/Buige pole 23873 NC Underground - NO CURRENT PENDING 2-15-2013 J.Lancaster--Joy construction on site removing pole and foundation 2-25-2013 AL Young--refer to construction | High Pressure Sodium | 38.90672638000 | -77.04606427000
2/7/13 | 1103963 | 0000 | NANNIE HELEN BURROUGHS AVE | NE | 2/13/13 | 70029 | 7A059 | (Light out) | DA 2/12/13 Rickard/Hutchins 70029 light is on and working | High Pressure Sodium | 38.89830988000 | -76.91657202000
| 1103914 | 1035 | CONNECTICUT AVE | NW | 5/22/13 | 27215 | 2G834 | (Light out) | 5/22/13 TN: IPMA project. waiting for PEPCO connect power. DA 2/12/13 Arrington pole 27215 NC Underground NO CURRENT PENDING -Temp pole 13-00029153-The street light is not working (lighting up). cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90340940000 | -77.03964906000
2/6/13 | 1103837 | 200 | I ST | SE | 2/12/13 | 67650 | 6A426 | (Light out) | DA 2/12/13 Black bad address | High Pressure Sodium | 38.87923749000 | -77.00159557000
2/6/13 | 1103805 | 100 | 3RD ST | SE | 2/12/13 | 6A002 | 6A002 | (Light out) | DA 2/12/13 Favors/Buige repaired pole 6A002 | Incandescent | 38.87703665000 | -77.00445216000
2/5/13 | 1103636 | 600 | 1ST ST | NE | 2/8/13 | 60927 | 6U601 | (Light out) | DA 2/7/13 Favors/Buige repaired pole 60927 repaired loose connection hot to TLP | High Pressure Sodium | 38.89824861000 | -77.00746947000
2/5/13 | 1103633 | 1100 | 1ST ST | NE | 2/6/13 | 61235 | 6S233 | (Light out) | DA 2/6/13 Favors/ Buige repaired pole 61235 | High Pressure Sodium | 38.90411117000 | -77.00597136000
2/1/13 | 1103387 | 5220 | WISCONSIN AVE | NW | 2/6/13 | 3A084DC | 3A084 | (Light off/on) | DA 1/5/13 Arrington pole 3A084DC light is on and working | High Pressure Sodium | 38.95810245000 | -77.08423960000
| 1103268 | 0 | 1ST ST | NE | 2/14/13 | 61239 | 6A264 | (Light out) | 2-14-2013 G.Edwards--install base door 13-00022922-Streetlight Repair 1112-1198 First Street Northeast, Washington, DC 20002, USA This issue has an image. You can view it here http://seeclickfix.com/issues/378786 . Electrical shock hazard from ope | High Pressure Sodium | 38.90515476000 | -77.00581203000
1/30/13 | 1103244 | 3536 | MINNESOTA AVE | SE | 2/4/13 | 76384DC | 7S263 | (Light off/on) | DA 2/4/13 Rickard/Hutchins could not locate pole 76384dc need better info | High Pressure Sodium | 38.88718063000 | -76.95487395000
1/29/13 | 1103137 | 714 | 21ST ST | NW | 1/31/13 | 28278 | 2L389 | (Light off/on) | DA 1/31/11 Favors/Buige repaired pole 28278 | High Pressure Sodium | 38.89893750000 | -77.04659509000
1/29/13 | 1103110 | 2914 | SHERMAN AVE | NW | 1/30/13 | 12529 | 12534 | (Light out) | DA 1/29/13 Hill/Thompson repaired pole 12529 spliced t base | High Pressure Sodium | 38.92730578000 | -77.02611400000
1/29/13 | 1103084 | 3400 | 14TH ST | NE | 1/30/13 | 51209DC | 5A098DC | (Light out) | DA 1/29/13 Hill/Thompson repaired pole 51209dc | High Pressure Sodium | 38.93218051000 | -76.98638139000
1/28/13 | 1103018 | 901 | HALF ST | SE | 1/30/13 | 67433 | 6U342 | (Light out) | DA 1/30/13 Rickard/Hutchins repaired pole 67433 | High Pressure Sodium | 38.87894793000 | -77.00752512000
1/27/13 | 1102962 | 7051 | SPRING PL | NW | 2/1/13 | 4H523DC | 4H523 | (Light out) | DA 1/31/13 Hill/Thompson repaired pole 4h523dc 13-00019847-This is the streetlight in the Spring Place Alley located directly behind The Gables apartments cwDesc: STREETLIGHT REPAIR | Incandescent | 38.97594098000 | -77.01865986000
1/27/13 | 1102961 | 7051 | SPRING PL | NW | 2/1/13 | 4H522DC | 4H522 | (Light out) | DA 1/31/13Hill/Thompson repaired pole 4H522dc Alley 13-00019846-This is the streetlight on the corner near the auto garage. cwDesc: ALLEYLIGHT REPAIR | Incandescent | 38.97614004000 | -77.01896257000
1/27/13 | 1102960 | 2327 | 33RD ST | SE | 1/28/13 | 74831DC | 79438DC | (Light out) | DA 1/28/13 Rickard/Hutchins repaired pole #74831dc 13-00019826- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86054471000 | -76.95992861000
1/25/13 | 1102944 | 1011 | NORTH CAPITOL ST | NW | 1/29/13 | 60044 | 6A234 | (Light out) | DA 1/29/13 Favors/Buige two poles at this location out temp pole has no Current at fixture, removed ballist kit for repairs from second pole 13-00019146- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90382567000 | -77.00893584000
1/25/13 | 1102911 | 2318 | 32ND ST | SE | 1/28/13 | 74839DC | 7A103DC | (Light off/on) | DA 1/28/13 Rickard/Hutchins repaired pole #74839dc | High Pressure Sodium | 38.86076984000 | -76.96087210000
1/25/13 | 1102909 | 2327 | 33RD ST | SE | 1/28/13 | 74831DC | 79438DC | (Light off/on) | DA 1/28/13 Rickard/Hutchins repaired pole #74831dc refer to 1102960 | High Pressure Sodium | 38.86054471000 | -76.95992861000
1/22/13 | 1102673 | 5139 | HANNA PL | SE | 1/28/13 | 75460 | 75460DC | (Light off/on) | DA 1/28/13 Rickard/Hutchins repaired pole #75460 | High Pressure Sodium | 38.87932889000 | -76.92844534000
1/22/13 | 1102610 | 0000 | NAYLOR RD | SE | 1/23/13 | 81707 | 82851 | (Light out) | DA 1/23/13 Rickard/Hutchins repaired pole 81707 | High Pressure Sodium | 38.85869909000 | -76.96824421000
1/22/13 | 1102589 | 0 | D ST | SW | 1/24/13 | 21554 | 6A359 | (Light out) | DA 1/23/13 Favors/Buige repaired pole 61554 | High Pressure Sodium | 38.88513671000 | -77.01505083000
1/21/13 | 1102504 | 900 | VIRGINIA AVE | SE | 1/22/13 | 67623 | 6L983 | (Light out) | DA 1/22/13 Rickard/Hutchins repaired pole #67623 | High Pressure Sodium | 38.87841973000 | -76.99513021000
1/21/13 | 1102493 | 1016 | 22ND ST | NW | 1/23/13 | 23901 | 2G782 | (Light out) | DA 1/22/13 Favors/Buige pole #23901 temp pole needs to be leveled 13-00015618-Streetlight Repair 1014 22nd Street Northwest, Washington, DC 20037, USA Street light knocked sideways by city workers and might fall down unless repaired cwDesc: STREETL | High Pressure Sodium | 38.90364037000 | -77.04888304000
1/19/13 | 1102482 | 1936 | EAST CAPITOL ST | NE | 1/28/13 | 63721 | 6M804 | (Light out) | DA 1/21/13 Rickard/Hutchins pole 63721 NC Underground | High Pressure Sodium | 38.88960987000 | -76.97672435000
1/16/13 | 1102216 | 625 | BURNS ST | SE | 1/18/13 | 76071 | 76071DC | (Light off/on) | DA 1/18/13 @ 120am Rickard/Hutchins repaired pole #76071 | High Pressure Sodium | 38.88020983000 | -76.94386284000
1/15/13 | 1102180 | 3209 | ALABAMA AVE | SE | 1/16/13 | 74836DC | 7A100DC | (Light out) | DA 1/15/13 @ 330am Rickard/Hutchins repaired pole #74836dc Alley 13-00011327-Light burnt out. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.86132638000 | -76.96088830000
1/15/13 | 1102137 | 1335 | 11TH ST | NW | 1/16/13 | 25282 | 2M248 | (Light off/on) | DA 1/16/13 @ 1043pm Favors/Buige repaired pole #25282 | High Pressure Sodium | 38.90790310000 | -77.02715169000
1/15/13 | 1102134 | 1420 | 9TH ST | NW | 1/21/13 | 25470 | 6U457 | (Light off/on) | aunguration traffic could not access will repair tomorrow | High Pressure Sodium | 38.90930620000 | -77.02386532000
1/15/13 | 1102133 | 0 | 7TH ST | NW | 1/21/13 | 25659 | 6A800 | (Light off/on) | aunguration traffic could not access will repair tomorrow | High Pressure Sodium | 38.90822210000 | -77.02201697000
1/14/13 | 1102022 | 809 | INTERSTATE 295 | NE | 2/13/13 | 79474 | 7A138 | (Light out) | DA 2/13/12 Black pole 79474 completed | High Pressure Sodium | 38.88176234000 | -76.96414383000
1/14/13 | 1102013 | 3400 | 14TH ST | NE | 1/15/13 | 51208DC | 5A097DC | (Light out) | DA 1/14/13 @ 1140pm Rickard/Hutchins repaired pole #51208dc secured photocell | High Pressure Sodium | 38.93195155000 | -76.98636408000
1/11/13 | 1101952 | 0 | L ST | NW | 1/16/13 | 24637 | 2G783 | (Light out) | DA 1/16/13 @ 142am Favors/Buige repaired pole #24637 | High Pressure Sodium | 38.90367717000 | -77.04866329000
1/11/13 | 1101939 | 0 | BARNEY CIR | SE | 1/15/13 | 65365 | 6U669 | (Light out) | DA 1/15/13 @ 120am Favors/Buige repaired pole #65365 | High Pressure Sodium | 38.87902463000 | -76.98181649000
1/11/13 | 1101853 | 740 | 6TH ST | NW | 1/14/13 | 22514 | 6S426 | (Light out) | DA 1/13/13 @ 909pm Favors/Buige repaired pole #22514 now tagged as 6S429 | High Pressure Sodium | 38.89941296000 | -77.02001456000
1/10/13 | 1101725 | 0 | 7TH ST | NW | 1/11/13 | 22452 | 6M651 | (Light out) | DA 1/11/13 @ 218am Favors/Buige repaired pole #22452 | High Pressure Sodium | 38.89955549000 | -77.02182020000
1/10/13 | 1101724 | 825 | 7TH ST | NW | 1/11/13 | 22420 | 6M666 | (Light out) | DA 1/11/13 @ 213am Favors/Buige repaired pole #22420 | High Pressure Sodium | 38.90039135000 | -77.02201360000
1/10/13 | 1101723 | 0 | 7TH ST | NW | 1/11/13 | 22412 | 6M682 | (Light out) | DA 1/11/13 @ 201am Favors/Buige repaired pole marked 6M688 | High Pressure Sodium | 38.90153465000 | -77.02201827000
1/10/13 | 1101722 | 0 | 7TH ST | NW | 1/11/13 | 22415 | 6M676 | (Light out) | DA 1/11/13 @ 209am Favors/Buige repaired pole #22415 | High Pressure Sodium | 38.90118128000 | -77.02201316000
| 1101533 | 4431 | F ST | SE | 1/10/13 | 75746 | 75746DC | (Light out) | DA 1/1/13 @ 120am Rickard/Hutchins repaired pole #75746 13-00006069- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88172196000 | -76.93845241000
1/8/13 | 1101423 | 1222 | 1ST ST | NE | 1/9/13 | 61244 | 6A275 | (Light out) | DA 1/8/13 @ 928pm Favors/Buige repaired pole #61244 | High Pressure Sodium | 38.90676525000 | -77.00596728000
1/7/13 | 1101302 | 0 | NEW YORK AVE | NW | 1/9/13 | 22913 | 2L062 | (Light out) | DA 1/9/13 @ 405am Favors/Buige repaired pole #22913 | High Pressure Sodium | 38.90113457000 | -77.02657407000
1/4/13 | 1101085 | 900 | VIRGINIA AVE | SE | 1/4/13 | 67623 | 6L983 | (Light out) |  | High Pressure Sodium | 38.87841973000 | -76.99513021000
| 1101024 | 0 | BROAD BRANCH TER | NW | 1/4/13 | 34711DC | 34730DC | (Light out) | DA 1/4/13 @ 245am Arrington repaired pole #34711dc Rear 13-00002053- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.95576043000 | -77.06567453000
1/3/13 | 1100969 | 1200 | CONNECTICUT AVE | NW | 1/7/13 | 27221 | 2U530 | (Light out) | DA 1/6/13 @ 1118pm Favors/Buige repaired pole #27221 | High Pressure Sodium | 38.90584530000 | -77.04105305000
12/28/12 | 1100700 | 1765 | NEW YORK AVE | NE | 12/31/12 | 50059 | 5A050 | (Light out) | DA 12/30/12 @ 825pm Hill/Thompson repaired pole #50059 | High Pressure Sodium | 38.91711725000 | -76.97869992000
12/26/12 | 1100521 | 206 | D ST | SE | 1/7/13 | 65644 | 65618 | (Light out) | 1-5-2013 I.Paraway---found ok | High Pressure Sodium | 38.88502510000 | -77.00336540000
12/26/12 | 1100444 | 1015 | KENILWORTH AVE | NE | 1/1/13 | 71172DC | 7M119 | (Light out) | DA 1/01/13 @ 900pm Rickard/Hutchins repaired pole #71172dc DA 12/27/12 @ 930pm Rickard/Hutchins pole #71172dc needs MOT heavy traffic | High Pressure Sodium | 38.90271798000 | -76.94306831000
12/26/12 | 1100437 | 4611 | NANNIE HELEN BURROUGHS AVE | NE | 12/27/12 | 71562DC | 7A233 | (Light out) | DA 12/27/12 @ 157am Rickard/Hutchins pole #71562dc light found on and working | High Pressure Sodium | 38.89924568000 | -76.93571393000
12/26/12 | 1100431 | 2201 | 22ND ST | NW | 12/27/12 | 24723 | 2G689 | (Light out) | DA 12/27/12 @ 332am Favors/Buige repaired pole #24723 | High Pressure Sodium | 38.90269343000 | -77.04895947000
12/26/12 | 1100420 | 703 | 49TH ST | NE | 12/28/12 | 71285DC | 7A218 | (Light out) | DA 12/28/12 W Black light is no longer at this address | High Pressure Sodium | 38.89869349000 | -76.93152778000
12/26/12 | 1100321 | 0 | WISCONSIN AVE | NW | 12/27/12 | 3A061DC | 3A061 | (Light out) | DA 12/27/12 @ 240am Arrington repaired pole #3A061dc | High Pressure Sodium | 38.94998940000 | -77.08058258000
12/26/12 | 1100282 | 1936 | EAST CAPITOL ST | NE | 12/20/13 | 63721 | 6M804 | (Light out) | J. Lancaster completed on 3/21/13. Installed 3FT of 2inch conduit, 220FT of #10 cable and made splices inside manhole. DA 12/28/12 @ 355am Hill/Thompson pole #63721 NC @ Base 1-4-2013 M.Scanland---refer to construction pipe broken | High Pressure Sodium | 38.88960987000 | -76.97672435000
12/21/12 | 1100201 | 3172 | BLADENSBURG RD | NE | 12/27/12 | 51229DC | 5A125DC | (Light out) | DA 12/27/12 @ 805pm Hill/Thompson pole #51229dc teardrop fixture found ok | High Pressure Sodium | 38.92909257000 | -76.96040483000
12/21/12 | 1100189 | 408 | RHODE ISLAND AVE | NW | 12/24/12 | 59989 | 5A181 | (Light out) | DA 12/24/12 @ 110am Rickard/Hutchins repaired pole #59989 | High Pressure Sodium | 38.91392931000 | -77.01700898000
12/21/12 | 1100183 | 0 | 22ND ST | NW | 12/27/12 | 28304 | 2M295 | (Light out) | DA 12/27/12 @ 102am Favors/Buige repaired pole #28304 | High Pressure Sodium | 38.90133435000 | -77.04875951000
12/21/12 | 1100166 | 200 | W ST | NW | 12/23/12 | 13760 | 1U188 | (Light out) | DA 12/23/12 @ 1020pm R Arrington pole #13760 light found on and in working condition | High Pressure Sodium | 38.91949574000 | -77.01713787000
12/21/12 | 1100148 | 2838 | BLADENSBURG RD | NE | 12/27/12 | 50096 | 5A082 | (Light out) | DA 12/27/12 @ 730pm Hill/Thompson repaired pole #50096 12-00349576-Streetlight Repair 2600-2606 Bladensburg Road Northeast, Washington, DC 20018, USA DDOT removed a damaged fixture but did not replace it. Please reinstall fixture - the area is dark c | High Pressure Sodium | 38.92653880000 | -76.96331853000
12/20/12 | 1100079 | 901 | HALF ST | SE | 12/21/12 | 67433 | 6U342 | (Light out) | DA 12/21/12 @ 116am Rickard/Hutchins pole #67433 light is on and working new lamp | High Pressure Sodium | 38.87894793000 | -77.00752512000
12/20/12 | 1100044 | 1218 | CONNECTICUT AVE | NW | 1/2/13 | 24532 | 2U519 | (Light out) | Same as W.O. 1082845 Refer to DDOT traffic combo pole. Streetlight and traffic light share the same duct. DA 12/24/12 @ 330am Favors/Buige pole #24532 NC Underground | High Pressure Sodium | 38.90651643000 | -77.04185036000
12/19/12 | 1099940 | 737 | 7TH ST | NW | 12/24/12 | 22449 | 6M645 | (Light out) | DA 12/23/12 Favors/Buige request for map could not locate | High Pressure Sodium | 38.89917822000 | -77.02181820000
12/19/12 | 1099932 | 1900 | 37TH ST | NW | 12/21/12 | 36891 | 30482 | (Light out) | DA 12/21/12 @ 1255am R Arrington pole #36891 light found on and working | High Pressure Sodium | 38.91672906000 | -77.07292654000
12/19/12 | 1099922 | 1218 | CONNECTICUT AVE | NW | 1/2/13 | 24532 | 2U519 | (Light out) | Same as W.O. 1082845 Refer to DDOT traffic combo pole. Streetlight and traffic light share the same duct. DA 12/21/12 @ 309am Favors/Buige pole #24532 NC Underground | High Pressure Sodium | 38.90651643000 | -77.04185036000
12/19/12 | 1099920 | 1133 | CONNECTICUT AVE | NW | 12/21/12 | 27219 | 2U550 | (Light out) | DA 12/21/12 @ 255am Favors/Buige repaired pole #27219 | High Pressure Sodium | 38.90491369000 | -77.04052615000
12/19/12 | 1099915 | 1270 | NEW HAMPSHIRE AVE | NW | 2/14/13 | 23873 | 2G758 | (Light out) | DA 12/21/12 @ 315am Favors/Buige lights are out due to construction | High Pressure Sodium | 38.90672638000 | -77.04606427000
12/19/12 | 1099907 | 4801 | MASSACHUSETTS AVE | NW | 12/20/12 | 38256 | 30468 | (Light out) | DA 12/20/12 @ 345am R Arrington repaired pole #38256 12-00347292-Streetlight Repair 4820 43rd Street Northwest, Washington, DC 20016, USA Light has been out for several weeks. Located at the ally on 43rd st NW across from 4817 and in front of 4820 cw | High Pressure Sodium | 38.94464587000 | -77.09547742000
12/14/12 | 1099722 | 0 | NEW HAMPSHIRE AVE | NW | 12/18/12 | 23870 | 2G728 | (Light out) | DA 12/18/12 @ 1230am Favors/Buige pole #23870 light previously repaired on and working | High Pressure Sodium | 38.90595274000 | -77.04670836000
12/14/12 | 1099673 | 0 | 4TH ST | SW | 12/19/12 | 21594 | 6A379 | (Light out) | DA 12/19/12 @ 220am Favor/Buige repaired pole #21594 | High Pressure Sodium | 38.88674391000 | -77.01372694000
| 1099659 | 0 | 4TH ST | SW | 12/19/12 | 21594 | 6A379 | (Light out) | DA 12/19/12 Duplicate tickit to wo #1099673 12-00343402- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88674391000 | -77.01372694000
| 1099626 | 408 | RHODE ISLAND AVE | NW | 12/19/12 | 59989 | 5A181 | (Light out) | DA 12/19/12 @ 1250am Hill/ THompson repaired pole #59989 12-00343260-two lights out together cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91392931000 | -77.01700898000
12/13/12 | 1099594 | 800 | 4TH ST | NW | 12/19/12 | 60448 | 6S459 | (Light out) | DA 12/18/12 @ 1125pm Rickards/Hutchins pole #60448 new pole and lamp on and in working conditions | High Pressure Sodium | 38.90032749000 | -77.01608012000
| 1099559 | 1005 | 1ST ST | NE | 12/18/12 | 61231 | 6S439 | (Light out) | 12-17-2012 W.HUTCHINS---duplicate wo# 1099554 12-00342703- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90311217000 | -77.00596908000
| 1099554 | 1005 | 1ST ST | NE | 12/19/12 | 61231 | 6S439 | (Light out) | DA 12/19/12 B Black defective teardrop fixture/ witing on materials DA 12/18/12 @ 135am Rickard/hutchins pole #61231 defective teardrop fixture 12-00342686- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90311217000 | -77.00596908000
12/13/12 | 1099515 | 0000 | FRANKLIN ST | NE |  | 50063 | 5A054 | (Light out) | DA 12/17/12 @ 1250am Hill Thompsom pole #50063 NC underground | High Pressure Sodium | 38.92567388000 | -77.00321706000
12/13/12 | 1099514 | 408 | RHODE ISLAND AVE | NW | 12/17/12 | 59989 | 5A181 | (Light out) | DA 12/17/12 @ 1230am Hill/Thompson repaired pole #59989 | High Pressure Sodium | 38.91392931000 | -77.01700898000
12/12/12 | 1099396 | 3209 | ALABAMA AVE | SE | 12/12/12 | 74836DC | 7A100DC | (Light out) |  | High Pressure Sodium | 38.86132638000 | -76.96088830000
12/12/12 | 1099364 | 860 | E ST | NW | 12/28/12 | 60177 | 29709 | (Light out) | DA 12-13/12 @ 12am C Hill/ F Thompson reattached globe taped so light would not shine on watchman, globe needs to be shaded 12-28-2012 I.Paraway---bad address | High Pressure Sodium | 38.89605599000 | -77.02382578000
12/12/12 | 1099363 | 775 | H ST | NE | 12/13/12 | 61991 | 6S197 | (Light out) | DA C Hill/ F Thompson repaired pole #65197 | High Pressure Sodium | 38.90030060000 | -76.99586046000
12/11/12 | 1099242 | 1437 | MONROE ST | NE | 12/11/12 | 51219DC | 5A109DC | (Light out) | 1437 Monroe St. NE Ward-5 | High Pressure Sodium | 38.93282306000 | -76.98452829000
12/11/12 | 1099183 | 418 | NEW YORK AVE | NW | 12/17/12 | 60064 | 6A170 | (Light out) | DA 12/16/12 @ 1105pm Rickard/hutchins pole #60064 light found on and in working condition 418 NEW YORK ( AVE ) NW | High Pressure Sodium | 38.90422287000 | -77.01773238000
12/11/12 | 1099181 | 418 | NEW YORK AVE | NW | 12/13/12 | 60063 | 6A172 | (Light out) | DA 12/13/12 @ 1145pm C Hill/ F Thompson pole #60065, 25925, 25924, 6m765, 6m764 and 29738 checked all lights found on and in working condition | High Pressure Sodium | 38.90441345000 | -77.01718759000
12/11/12 | 1099178 | 3553 | GEORGIA AVE | NW | 12/11/12 | 19992 | 1G211 | (Light out) |  | High Pressure Sodium | 38.93426687000 | -77.02389331000
| 1099145 | 1133 | CONNECTICUT AVE | NW | 12/12/12 | 27219 | 2U550 | (Light out) | DA 12/11/12 @ 1118pm Waymond Favors/ Tony Buige pole #27219 light is on and in working condition previously repaired 12-00339947-Street light appears to be burned out. Has not come on at all. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90491369000 | -77.04052615000
12/7/12 | 1098987 | 901 | HALF ST | SE | 12/7/12 | 67433 | 6U342 | (Light out) |  | High Pressure Sodium | 38.87894793000 | -77.00752512000
12/6/12 | 1098898 | 504 | K ST | NW | 12/11/12 | 60461 | 6A101 | (No current) | A. Jackson completed on 12/11/12. Made splices inside manhole. 500 K St. NW (front) | High Pressure Sodium | 38.90260703000 | -77.01950617000
12/6/12 | 1098799 | 711 | ANACOSTIA AVE | NE | 12/6/12 | 72358DC | 7A481 | (Light out) |  | High Pressure Sodium | 38.90197539000 | -76.95056600000
12/5/12 | 1098673 | 0 | 13TH ST | NW | 12/5/12 | 4K431 | 4U145 | (Light out) |  | High Pressure Sodium | 38.94333464000 | -77.02962264000
12/5/12 | 1098650 | 1400 | S ST | NW | 12/5/12 | 26184 | 2A080 | (Light out) |  | High Pressure Sodium | 38.91415171000 | -77.03212341000
11/24/12 | 1098188 | 0000 | NAYLOR RD | SE | 11/29/12 | 81707 | 82851 | (Light out) | 11-29-2012 W.Hutchins---found ok | High Pressure Sodium | 38.85869909000 | -76.96824421000
11/23/12 | 1098132 | 1401 | LAWRENCE ST | NE | 11/24/12 | 52485DC | 5A156DC | (Light out) | Robert Arrington completed on 11/24/12. Installed 150w lamp. | High Pressure Sodium | 38.93175822000 | -76.98604463000
11/23/12 | 1098080 | 1300 | BRYANT ST | NE | 11/25/12 | 51336DC | 5A254 | (Light out) | I. Paraway on 11/25/12 Found OK | High Pressure Sodium | 38.92097735000 | -76.98895164000
11/23/12 | 1098055 | 1534 | TANNER ST | SE | 11/24/12 | 81768 | 88045 | (Light out) | A. Young completed on 11/24/12. Installed 250w lamp. | High Pressure Sodium | 38.84738657000 | -76.98124742000
| 1097092 | 0 | 22ND ST | NW | 12/7/12 | 28304 | 2M295 | (Light out) | 12-00310552-next to meter # 20220909 cwDesc: STREETLIGHT REPAIR 11-11-2012 J.Whalen/C.Gallagher---needs new ballast..pole is loose 11-17-12 J.Lancaster---pole is loose need to be fixed opp/ of loading dock in the 900blk of 22nd st. n.w. | High Pressure Sodium | 38.90133435000 | -77.04875951000
10/31/12 | 1096710 | 0 | MASSACHUSETTS AVE | NW | 1/9/13 | 25939 | 2L551 | (Light out) | 12-00306112-Base cover has come lose cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90325148000 | -77.02477750000
10/31/12 | 1096568 | 1243 | 16TH ST | NE | 12/13/12 | 53402 | 5A167 | (Light out) | R. Fike on 11-2-12 Aley pole is leaning. 12-00305069-caller report the alleylight is leaning cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.90650125000 | -76.97986786000
| 1096158 | 0 | RHODE ISLAND AVE | NW | 11/3/12 | 59997 | 5A189 | (Light out) | G. Edwards completed on 11-2-12. All lights are working properly. 12-00293099-Caller is reporting one street light out and is requesting to have the light repaired and it has been out for two days. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91491231000 | -77.01415169000
9/24/12 | 1095615 | 717 | BARNES ST | NE | 9/25/12 | 72462DC | 7A473 | (Light out) | DA 9-25-12 @ 1240am B Brown repaire pole #72462dc trimmed tree | High Pressure Sodium | 38.90163933000 | -76.95010523000
9/24/12 | 1095592 | 0 | 22ND ST | NW | 9/24/12 | 28303 | 2M294 | (Light out) | DA 9-24-12 @ 320am C Ashton repaired pole #28303 | High Pressure Sodium | 38.90108157000 | -77.04875963000
9/24/12 | 1095572 | 1112 | Q ST | NW | 9/24/12 | 29306DC | 2U047DC | (Light out) | DA 9-24-12 @ 120am K Dunton repaired pole #29306dc | Incandescent | 38.91083084000 | -77.02756095000
9/24/12 | 1095541 | 36 | PORTER PL | NE | 9/25/12 | 56992 | 5M146 | (Light out) | DA 9-25-12 @ 305am K Simmons repaired pole #56992 (short cap) 12-00269535-Streetlight directly behind our house - in the alley - went out Thursday. It's still out today (Sunday). cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91041299000 | -77.00788639000
9/23/12 | 1095519 | 1826 | 18TH ST | NW | 11/17/12 | 26780 | 2M106 | (Light out) | J. Lancaster completed on 11-17-12. Found OK. | High Pressure Sodium | 38.91492300000 | -77.04174945000
9/21/12 | 1095473 | 600 | 1ST ST | NE | 9/21/12 | 60930 | 6U604 | (Light out) | DA 9-21-12 @ 218am B Brown repaired pole #60930 | High Pressure Sodium | 38.89760383000 | -77.00770399000
9/20/12 | 1095402 | 0 | 9TH ST | NW | 9/25/12 | 25438 | 2L557 | (Light out) | 9-21-12 AL Young completed - bad address (vw) | High Pressure Sodium | 38.90343694000 | -77.02408444000
9/20/12 | 1095369 | 1129 | NEW HAMPSHIRE AVE | NW | 9/24/12 | 23866 | 2G715 | (Light out) | 9-24-12 Hudson/Tom - completed - tried to route - duct is broken in street - Metro Payving is placing new poles, duct and mh's - pole #23866 will be repaced with twin-20 pole (vw) DA 9-20-12 C Ashton pole #23866 NC Underground | High Pressure Sodium | 38.90463214000 | -77.04803157000
9/19/12 | 1095312 | 1129 | NEW HAMPSHIRE AVE | NW | 11/24/12 | 23866 | 2G715 | (Light out) | J. Lancaster completed on 11/24/12. Insatlled 20Feet of conduit, 130Feet of No10 cable and 7 bags of concrete. | High Pressure Sodium | 38.90463214000 | -77.04803157000
9/19/12 | 1095308 | 5900 | EAST CAPITOL ST | NE | 9/20/12 | 73559 | 73559DC | (Light out) | DA 9-19-12 B Brown repaired pole #73559 | High Pressure Sodium | 38.88964122000 | -76.91459774000
9/19/12 | 1095256 | 0 | 13TH ST | NW | 9/19/12 | 4K426 | 4U140 | (Light out) | DA 9-19-12 @ 1247am J Brown repaired pole #4k426 cleaned lens | High Pressure Sodium | 38.94449236000 | -77.02978547000
9/18/12 | 1095230 | 1530 | TANNER CT | SE | 9/19/12 | 81770 | 88047 | (Light out) | DA 9-19-12 @ 335an K Simmons repaired pole #81770 12-00263961-Caller reporting streetlight out on metal pole. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84763364000 | -76.98153866000
9/18/12 | 1095189 | 1209 | U ST | NW | 9/18/12 | 13284 | 1G534 | (Light out) | DA 9-8-12 @ 234am CAshton repaired pole #13284 | High Pressure Sodium | 38.91691923000 | -77.02846873000
9/17/12 | 1095170 | 4801 | NORTH CAPITOL ST | NW | 9/17/12 | 4R752 | 4A793 | (Light out) | mistake refer to wo 1095152 | High Pressure Sodium | 38.94885643000 | -77.00884149000
9/17/12 | 1095152 | 4801 | NORTH CAPITOL ST | NW | 9/18/12 | 4R752 | 4A793 | (Light dim) | DA 9-17-12 @ 928pm J Brown repaired pole #4R752 | High Pressure Sodium | 38.94885643000 | -77.00884149000
9/12/12 | 1094880 | 0 | 18TH ST | NW | 9/12/12 | 24534 | 2U529 | (Light out) | DA 9-12-12 @ 958pm C Ashton adjusted tlpc pole #24534 | High Pressure Sodium | 38.90591907000 | -77.04143681000
9/12/12 | 1094837 | 921 | 4TH ST | NE |  | 61438 | 6A299 | (Light out) | 9-17-12 Darryl Dixon - open refer to DDOT duct and wires are dug up in construction area - took pics the contact is outside unlimited Danny (443) 375-0692 pole is located behind construction fence (vw) DA 9-13-12 @ 242am B Brown pole #61438 NC under | High Pressure Sodium | 38.90192178000 | -77.00064462000
9/12/12 | 1094802 | 2430 | 32ND ST | SE | 9/12/12 | 74751DC | 7A065DC | (Light out) | DA 9-12-12 @ 152am K Simmons repaired pole #74751dc | High Pressure Sodium | 38.85950408000 | -76.96143389000
9/11/12 | 1094785 | 0 | NEW YORK AVE | NW | 9/12/12 | 22913 | 2L062 | (Light out) | DA 9-11-12 @ 951pm C Ashton epaired pole #22913 reattached globe | High Pressure Sodium | 38.90113457000 | -77.02657407000
9/11/12 | 1094698 | 1350 | CONNECTICUT AVE | NW | 9/11/12 | 24527 | 2U491 | (Light out) | DA 9-11-12 @ 1255am C Ashton reapired pole #24527 | High Pressure Sodium | 38.90838138000 | -77.04291014000
9/10/12 | 1094588 | 0 | 24TH ST | NW | 9/10/12 | 24804 | 2G664 | (Light out) | DA 9-10-12 @ 205am C Ashton repaired pole #24804 | High Pressure Sodium | 38.90272824000 | -77.05133683000
9/10/12 | 1094584 | 0 | INTERSTATE 295 | SE | 9/10/12 | 68050 | 6L972 | (Light out) | DA 9-10-12 @ 155am K Simmons repaired pole #68050 | High Pressure Sodium | 38.87795866000 | -76.99246087000
9/10/12 | 1094583 | 0 | VIRGINIA AVE | SE | 9/10/12 | 68047 | 6L987 | (Light out) | DA 9-10-12 @ 145am K Simmons repaired pole #68047 | High Pressure Sodium | 38.87807147000 | -76.99363313000
8/31/12 | 1094006 | 1614 | 7TH ST | NW | 8/31/12 | 25704 | 6A822 | (Light out) | DA 8-31-12 @ 336am C Ashton repaired pole #25704 | High Pressure Sodium | 38.91165663000 | -77.02182317000
8/31/12 | 1094005 | 600 | 1ST ST | NE | 8/31/12 | 60927 | 6U601 | (Light out) | DA 8-31-12 B Brown repaired pole #60927 | High Pressure Sodium | 38.89824861000 | -77.00746947000
8/30/12 | 1093930 | 515 | NEW YORK AVE | NE | 8/31/12 | 56841 | 5A428 | (Light out) | DA 8-31-12 K Simmons repaired pole #56841 | High Pressure Sodium | 38.91151960000 | -76.99667276000
8/29/12 | 1093831 | 815 | V ST | NW | 9/4/12 | 14236 | 1U040 | (Light out) | DA 9-4-12 C Ashton repaired light is on and working DA 8-29-12 @ 945pm C Ashton repaired pole #14236 | Incandescent | 38.91816509000 | -77.02346836000
8/28/12 | 1093759 | 3408 | SHERMAN AVE | NW | 8/28/12 | 13073 | 1L294 | (Light out) | DA 8-28-12 @ 936pm C Ashton repaired pole #13073 | High Pressure Sodium | 38.93221585000 | -77.02683398000
8/28/12 | 1093724 | 0 | MONROE ST | NE | 8/29/12 | 56154DC | 5U722 | (Light out) | DA 8-28-12 1140pm K Simmons repaired pole #56154dc | High Pressure Sodium | 38.93231182000 | -76.99759860000
8/27/12 | 1093609 | 600 | 1ST ST | NE | 8/29/12 | 60930 | 6U604 | (Light out) | DA 5-29-12 2 321am B Brown pole #60930 light is on and working DA 8-28-12 @ 150am K Dunton repaired pole #60930 | High Pressure Sodium | 38.89760383000 | -77.00770399000
8/26/12 | 1093525 | 5600 | 2ND ST | NE | 2/26/13 | 4P472DC | 4U160 | (Light out) | 9-17-12 Damien Smith - open - pepco installing new secondary (vw) 8-27-12 DArryl Dixon - open - pepco installing new secondary (vw) DA 8-26-12 @ 945pm J Brown pole #4P472DC NC to Overhead 12-00240019-multiple lights are out on this block in | High Pressure Sodium | 38.95826310000 | -77.00300671000
8/24/12 | 1093504 | 5600 | 3RD ST | NE | 2/26/13 | 4P471DC | 4U158 | (Light out) | 9-17-12 Damien Smith - open - pepco installing new secondary (vw) 8-27-12 DArryl Dixon - open - pepco installing new secondary (vw) 08-24-12 Damien No current to overhead line (WP)DA 8-24-12 @ 410am J Brown pole #4p471DC NC to Overhead | High Pressure Sodium | 38.95858464000 | -77.00292664000
8/24/12 | 1093503 | 5600 | 2ND ST | NE | 2/26/13 | 4P472DC | 4U160 | (Light out) | 9-17-12 Damien Smith - open - pepco installing new secondary (vw) 8-27-12 DArryl Dixon - open - pepco installing new secondary (vw) 08-24-12 Damien No current to overhead line (WP)DA 8-24-12 @ 405am J Brown pole #4p472DC NC to Overhead | High Pressure Sodium | 38.95826310000 | -77.00300671000
8/23/12 | 1093449 | 1231 | U ST | NW | 8/23/12 | 12573 | 1G531 | (Light out) | DA 8-23-12 @ 944pm C Ashton repaired pole #12573 | High Pressure Sodium | 38.91709688000 | -77.02906097000
| 1093276 | 815 | 6TH ST | NW | 8/23/12 | 60542 | 6M707 | (Light out) | DA 8-23-12 @ 231am CAshton secured t base door pole #60542 12-00235985-Cover on street pole is missing; exposed wires cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90031850000 | -77.01979505000
| 1093273 | 815 | 6TH ST | NW | 8/23/12 | 60542 | 6M707 | (Light out) | DA 8-23-12 C AShton secured t base door 12-00235994-Cover on street pole is missing; exposed wires cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90031850000 | -77.01979505000
8/21/12 | 1093187 | 1100 | 11TH ST | SE | 8/22/12 | 67614 | 6L993 | (Light out) | DA 8-21-12 @ 1050pm B Brown repaired pole #67614 | High Pressure Sodium | 38.87689854000 | -76.99165831000
8/21/12 | 1093142 | 0 | CONNECTICUT AVE | NW | 8/21/12 | 38584 | 3E026 | (Light out) | DA 8-20-12 @ 1030pm K Dunton repaired pole #38584 | High Pressure Sodium | 38.94397582000 | -77.06352631000
8/20/12 | 1093118 | 3408 | SHERMAN AVE | NW | 8/24/12 | 13073 | 1L294 | (Light out) | J. Lancaster completed on 8-23-12. Installed 350 FT of No#10 cable and made splices inside manhole. DA 8-21-12 @ 255am K dunton pole #13073 NC Underground 0 volts | High Pressure Sodium | 38.93221585000 | -77.02683398000
8/19/12 | 1093034 | 418 | NEW YORK AVE | NW | 8/27/12 | 60064 | 6A170 | (Light out) | DA 8-26-12 K Dunton light is on and working 8-20-12 Hudson/Tom - poles are being replaced by new twin 20 poles other contractor (vw) DA 8-20-12 @ 155am B Brown pole #60064 NC Underground | High Pressure Sodium | 38.90422287000 | -77.01773238000
8/15/12 | 1092791 | 611 | K ST | NW | 8/16/12 | 22404 | 6A973 | (Light out) | DA 8-16-12 @ 316am B Brown repaired pole #22404 12-00229222- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90245457000 | -77.02040204000
8/15/12 | 1092756 | 1225 | 18TH ST | NW | 8/15/12 | 26764 | 2U516 | (Light out) | DA 8-15-12 @ 245am C Ashton repaired pole #26764 and leveled fixture | High Pressure Sodium | 38.90679324000 | -77.04161488000
8/14/12 | 1092666 | 3310 | F ST | SE | 8/23/12 | 76596 | 76596DC | (Light off/on) | DA 8-23-12 B Brown light is on and working DA 8-14-12 B Brown repaired pole #76596dc | High Pressure Sodium | 38.88221029000 | -76.95914329000
8/13/12 | 1092603 | 0329 | RHODE ISLAND AVE | NE | 8/14/12 | 50083 | 5A064 | (Light out) | DA 8-14-12 K Simmons repaired pole #50083 and trimmed tree | High Pressure Sodium | 38.91949870000 | -77.00096444000
8/12/12 | 1092513 | 0 | C ST | SW | 8/13/12 | 21785 | 6A373 | (Light out) | DA 8-13-12 @ 125am Cashton repaired pole #21785 (#10 splice) | High Pressure Sodium | 38.88597703000 | -77.01373350000
8/9/12 | 1092413 | 1207 | 7TH ST | NW | 8/10/12 | 25696 | 6A793 | (Light out) | DA 8-9-12 @ 1005pm C Ashton repaired pole #25696 | High Pressure Sodium | 38.90732750000 | -77.02182134000
8/9/12 | 1092411 | 0 | 7TH ST | NW | 8/10/12 | 14394 | 1M003 | (Light out) | DA 8-9-12 @ 936pm C Ashton repaired pole #14394 | High Pressure Sodium | 38.91567433000 | -77.02182460000
| 1092403 | 0 | I ST | NW | 8/15/12 | 22496 | 6S558 | (Light out) | 8-15-12 N Woodland - no problem found (vw) DA 8-9-12 @ 1052pm C Ashton pole #22496 needs base cover light found okay 12-00223145-Base cover missing. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90081044000 | -77.02175292000
| 1092280 | 1000 | NEW YORK AVE | NW | 8/9/12 | 22948 | 2L032 | (Light out) | DA 8-9-12 @ 137am C Ashton # 1093656 12-00221825-Street pole located on island in front of Againn is missing base cover cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90132896000 | -77.02684244000
8/7/12 | 1092125 | 0 | U ST | NW | 8/7/12 | 13283 | 1G528 | (Light out) | DA 8-7-12 @ 356am C Ashton repaired pole #13283 | High Pressure Sodium | 38.91691876000 | -77.02945599000
8/1/12 | 1091753 | 1423 | 36TH ST | NW | 8/9/12 | 21000 | 2G201 | (Light out) | 8/9/2012 Al Young and Vernon Ham Found OK (WP)DA 8-9-12 C Ashton light found on and working8-8-12 Hudson/Tom - completed - this road is colsed no access (vw) DA 8-6-12 @ 225am C Ashton pole #21000 NC Underground no feed | High Pressure Sodium | 38.90835025000 | -77.07043482000
7/31/12 | 1091591 | 815 | V ST | NW | 7/31/12 | 14236 | 1U040 | (Light out) | DA 7-31-12 @ 315am C AShton repaired pole #14236 | Incandescent | 38.91816509000 | -77.02346836000
7/30/12 | 1091508 | 1765 | NEW YORK AVE | NE | 8/3/12 | 50061 | 5A052 | (Light out) | 8-3-12 B Woodland - completed - installed 1 ee (vw) DA 7-30-12 @ 1030pm J brown repaired pole #50061 missing 1 elephant ear | High Pressure Sodium | 38.91710088000 | -76.97956686000
7/30/12 | 1091502 | 0 | 8TH ST | NE | 7/31/12 | 56194DC | 56194 | (Light out) | DA 7-31-12 @ 310am J Brown repaired pole #56194dc | High Pressure Sodium | 38.93214286000 | -76.99503981000
7/30/12 | 1091479 | 0 | ANACOSTIA FWY | SE | 7/30/12 | 79478 | 7A142 | (Light out) | DA 7-30-12 K Simmons repaired pole #79478 | High Pressure Sodium | 38.88446501000 | -76.96303530000
7/30/12 | 1091478 | 0 | ANACOSTIA FWY | SE | 7/30/12 | 79477 | 7A141 | (Light out) | DA 7-30-12 K Simmons repaired pole #79477 | High Pressure Sodium | 38.88375073000 | -76.96332098000
7/30/12 | 1091460 | 0 | OVERLOOK AVE | SE | 7/30/12 | 81816 | 88089 | (Light out) | DA 7-30-12 K Simmons repaired pole #81816 | High Pressure Sodium | 38.83181785000 | -77.01472372000
7/29/12 | 1091378 | 0 | EAST CAPITOL ST | NE | 7/29/12 | 74205DC | 7A063DC | (Light out) | DA 7-29-12 @ 921pm B Brown pole #74205dc already referred to Ddot wo 1082854 | High Pressure Sodium | 38.89216210000 | -76.94254713000
7/29/12 | 1091377 | 0 | EAST CAPITOL ST | NE | 7/30/12 | 73561 | 73561DC | (Light out) | DA 7-30-12 B Brown repaired pole #73561 | High Pressure Sodium | 38.88964269000 | -76.91530308000
7/29/12 | 1091369 | 22 | RANDLE CIR | SE | 7/31/12 | 77503DC | 7S054 | (Light out) | DA 7-31-12 @ 231am B Brown could not fimd pole #77503dc at this location but all lights were on and working | High Pressure Sodium | 38.87771015000 | -76.96092291000
7/25/12 | 1091167 | 0 | CHILLUM PL | NE | 7/26/12 | 4P513DC | 4U169 | (Light out) | DA 7-26-12 @ 405am J BRown repaired pole #4p513dc | High Pressure Sodium | 38.95927698000 | -77.00253696000
7/24/12 | 1091087 | 2826 | BLADENSBURG RD | NE | 7/24/12 | 51240DC | 5A136DC | (Light out) | DA 7-24-12 @ 955pm K Simmons repaired pole #51240dc adjusted photocell | High Pressure Sodium | 38.92627322000 | -76.96401150000
7/24/12 | 1091081 | 2820 | BLADENSBURG RD | NE | 7/26/12 | 50094 | 5A080 | (Light out) | WBlack-7-26-12-MWilcots QC'd light is on DA 7-24-12 @ 1005pm K Simmons repaired pole #50094 trimmed tree | High Pressure Sodium | 38.92604672000 | -76.96392000000
7/23/12 | 1090948 | 3267 | P ST | NW | 8/2/12 | 21017 | 2G142 | (Light out) | 8-2-12 Darcmpleted - poles being installed by other contractors (MC Dean) (vw) DA 7-25-12 @ 300am C Ashton no pole id tag NC Underground trimmed tree 12-00203315-sTREET LIGHT IS IN FRONT OF WINDOW OF CITIZEN HOME cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90886358000 | -77.06536598000
7/23/12 | 1090833 | 504 | K ST | NW | 7/24/12 | 60461 | 6A101 | (Light out) | DA 7-24-12 @ 1040pm R WAlton repaired pole #60461 | High Pressure Sodium | 38.90260703000 | -77.01950617000
7/22/12 | 1090673 | 2121 | WISCONSIN AVE | NW | 7/27/12 | 30158 | 3G102 | (Light out) | DA 7-27-12 @ 330am K Dunton repaired pole #30158 | High Pressure Sodium | 38.91818441000 | -77.06963611000
7/22/12 | 1090670 | 1900 | 37TH ST | NW | 7/26/12 | 36891 | 30482 | (Light out) | DA 7-26-12 @ 320am K Dunton repaired pole #36891 | High Pressure Sodium | 38.91672906000 | -77.07292654000
7/19/12 | 1090480 | 1300 | BRENTWOOD RD | NE | 8/15/12 | 51354 | 5A258 | (Light out) | DA 8-15-12 @ 255am K simmons pole #51354 light is on an working 7-25-12 Al Young - completed - checked pole found 124volts at base installed pole tag (vw) DA 7-20-12 @ 225am B Brown pole #51354 NC UNderground installed id tag | High Pressure Sodium | 38.92186515000 | -76.98853396000
7/19/12 | 1090469 | 0 | IDAHO AVE | NW | 7/19/12 | 38890DC | 3U412 | (Light out) | DA 7-19-12 @ 1220am K Dunton closed open lens pole #38890dc trimmed tree | High Pressure Sodium | 38.93479211000 | -77.07412054000
| 1090440 | 1633 | FORT DUPONT ST | SE | 7/24/12 | 78170DC | 7A341DC | (Light out) | 7-23-12 Damien smith - completed - installed 150' #6 triplex cable made 1 taps and 4 splices (vw) DA 7-23-12 @ 130am R Walton pole #78170dc NC to overhead rear alley 12-00198302-since the violent wind storm alley lights have been out cwDesc: ALLE | High Pressure Sodium | 38.86620718000 | -76.94625361000
7/17/12 | 1090373 | 3307 | O ST | NW | 7/22/12 | 21105 | 2G169 | (Light out) | DA 7-22-12 @ 945pm J Brown repaired pole #21105 12-00197442-Streetlight Repair 3307 O St NW, Washington, DC 20007, USA This issue has an image. You can view it here http://seeclickfix.com/issues/207661 . Someone has painted the inside of the cover | High Pressure Sodium | 38.90785307000 | -77.06621385000
7/17/12 | 1090274 | 1517 | TUBMAN RD | SE | 7/18/12 | 81801 | 88078 | (Light out) | DA 7-18-12 @ 325am B Brown repaired pole #81801 refer to wo #1090279 12-00196316- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84828043000 | -76.98176787000
7/16/12 | 1090176 | 1262 | NEW HAMPSHIRE AVE | NW | 7/18/12 | 23852 | 2G757 | (Light out) | DA 7-18-12 @ 200am C Ashton secured t base door pole #23852 12-00195248-Base plate is off; wires exposed. Possible hazard. Plate is on sidewalk. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90669938000 | -77.04633627000
7/15/12 | 1090008 | 0 | U ST | NW | 7/27/12 | 11722 | 1G527 | (Light out) | DA 7-26-12 @ 1025pm C Ashton adjusted photocell pole #11722 DA 7-16-12 @ 210am K dunton repaired pole #11722 | High Pressure Sodium | 38.91709757000 | -77.02977696000
7/15/12 | 1089997 | 2119 | H ST | NW | 7/16/12 | 27992 | 2A182 | (Light out) | DA 7-16-12 @ 329am C Ashton repaired pole #27992 | High Pressure Sodium | 38.89963409000 | -77.04759972000
7/15/12 | 1089996 | 2200 | H ST | NW | 7/16/12 | 27997 | 2A216 | (Light out) | DA 7-16-12 @ 351am C Ashton repaired pole # 27997 | High Pressure Sodium | 38.89963632000 | -77.04973980000
| 1089954 | 3700 | MILITARY RD | NW | 7/26/12 | 32716DC | 3E023 | (Light out) | WBlack-7-26-12-CFreeburger QC'd light is on 7-17-12 Darryl dixon - completed - span was down - installed 100' #6 triplex cable 2 #2 copper split bolts & tape (vw) DA 7-15-12 @ 1100pm K Dunton pole #32716dc NC to overhead Alley 12-00193140-IN ALLEY | High Pressure Sodium | 38.96062593000 | -77.07197706000
7/12/12 | 1089903 | 3043 | BLADENSBURG RD | NE | 7/17/12 | 51245DC | 5A141DC | (Light out) | DA 7-17-12 @ 1235am J Brown repaired pole #51245dc Alley 12-00192159-Light is out in alley, on pole, across from tennis court cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.93032628000 | -76.95815755000
7/12/12 | 1089898 | 0000 | FRANKLIN ST | NE | 7/18/12 | 50063 | 5A054 | (Light out) | DA 7-17-12 @ 1155pm B Browwn repaired pole #5063 | High Pressure Sodium | 38.92567388000 | -77.00321706000
7/12/12 | 1089897 | 0000 | FRANKLIN ST | NE | 7/18/12 | 50064 | 5A055 | (Light out) | DA 7-17-12 @ 1130pm B Brown repaired pole #50064 | High Pressure Sodium | 38.92554079000 | -77.00303515000
7/12/12 | 1089896 | 2800 | LINCOLN RD | NE | 7/18/12 | 50065 | 5A056 | (Light out) | DA 7-17-12 @ 1135pm B Brown repaired pole #50065 | High Pressure Sodium | 38.92549974000 | -77.00275988000
7/12/12 | 1089895 | 2800 | LINCOLN RD | NE |  | 50065 | 5A056 | (Light out) |  | High Pressure Sodium | 38.92549974000 | -77.00275988000
7/12/12 | 1089894 | 2521 | SHERIDAN RD | SE | 7/13/12 | 81368DC | 8M054 | (Light out) | DA 7-13-12 B Brown repaired pole 381368dc refer to wo #1089879 | High Pressure Sodium | 38.86044914000 | -76.99354009000
7/12/12 | 1089881 | 2521 | SHERIDAN RD | SE | 7/13/12 | 81368DC | 8M054 | (Light out) | DA 7-13-12 B Brown repaired pole 381368dc refer to wo #1089879 | High Pressure Sodium | 38.86044914000 | -76.99354009000
7/12/12 | 1089879 | 2521 | SHERIDAN RD | SE | 7/13/12 | 81368DC | 8M054 | (Light out) | DA 7-13-12 @ 305am B Brown repaired pole #81368dc | High Pressure Sodium | 38.86044914000 | -76.99354009000
7/12/12 | 1089866 | 1633 | FORT DUPONT ST | SE | 7/26/12 | 78170DC | 7A341DC | (No Current to Over Head) | WBlack-7-26-12-MWilcots QC'd light is on 7-23-12 Damien smith - completed - installed 150' #6 triplex cable made 1 taps and 4 splices (vw) | High Pressure Sodium | 38.86620718000 | -76.94625361000
7/12/12 | 1089818 | 2820 | BLADENSBURG RD | NE | 7/18/12 | 50094 | 5A080 | (Light out) | DA 7-17-12 @ 920pm B Brown installed teardrop fixture pole #50094 DA 7-17-12 @ 345am J Brown removed old broken fixture needs teardrop fixture DA 7-13-12 @ 405am J Brown pole #50094 needs teardrop fixture | High Pressure Sodium | 38.92604672000 | -76.96392000000
7/12/12 | 1089785 | 3700 | MILITARY RD | NW | 7/26/12 | 32716DC | 3E023 | (Light out) | WBlack-7-26-12-CFreeburger QC'd light is on 7-17-12 Darryl dixon - completed - span was down - installed 100' #6 triplex cable 2 #2 copper split bolts & tape (vw) DA 7-12-12 @ 325am K Dunton pole #32716dc NC to Overhead | High Pressure Sodium | 38.96062593000 | -77.07197706000
7/8/12 | 1089391 | 705 | ANACOSTIA AVE | NE | 7/10/12 | 72357DC | 7A480 | (Light out) | DA 7-9-12 @ 1006pm A Smith/ tony repaired pole #72357dc | High Pressure Sodium | 38.90177755000 | -76.95081946000
7/5/12 | 1089246 | 3513 | O ST | NW | 7/10/12 | 21096 | 2G159 | (Light out) | DA 7-9-12 @ 1047pm C Ashton old pole waiting for removal new pole already installed | High Pressure Sodium | 38.90777166000 | -77.06970579000
7/5/12 | 1089245 | 3525 | O ST | NW | 7/10/12 | 21095 | 2G156 | (Light out) | DA 7-9-12 @ 1044pm C Ashton old pole waiting for removal new pole already installed | High Pressure Sodium | 38.90766972000 | -77.07002828000
7/5/12 | 1089231 | 1270 | NEW HAMPSHIRE AVE | NW | 7/9/12 | 23873 | 2G758 | (Light out) | DA 7-9-12 @ 1259am C Ashton repaired pole #23873 and trimmed tree | High Pressure Sodium | 38.90672638000 | -77.04606427000
7/2/12 | 1088957 | 0 | CHILLUM PL | NE | 7/11/12 | 4P513DC | 4U169 | (Light out) | BCM - 7-3-2012 TREE TRIMMING NEEDED BEFORE REPAIRS CAN BE MADE TO LIGHT | High Pressure Sodium | 38.95927698000 | -77.00253696000
6/29/12 | 1088793 | 900 | 3RD ST | SE | 7/3/12 | 67529 | 6A457 | (Light out) | 07-03-12 Al Young 124v in base and in fixture (WP). DA 7-1-12 @ 1000pm B Brown repaired pole #67529 request for underground wire bare neturial | High Pressure Sodium | 38.87896332000 | -77.00211088000
6/29/12 | 1088774 | 4202 | 13TH ST | NW | 7/3/12 | 4K434 | 4U150 | (Light out) | DA 7-3-12 WM light found okay BCM - 7-2-2012 - S. Manning repaired pole. | High Pressure Sodium | 38.94219793000 | -77.02978242000
6/28/12 | 1088652 | 5656 | 3RD ST | NE | 6/29/12 | 4P473DC | 4U162 | (Light out) | 06-29-12 Hudson and Tom 1- TL PC 400W HPS bulb (WP). | High Pressure Sodium | 38.95791886000 | -77.00307597000
6/28/12 | 1088638 | 0 | KENNEDY ST | NW | 7/2/12 | 4M070 | 4M070DC | (Light out) | BCM- 7-2-2012 - I. Paraway repaired Light. | High Pressure Sodium | 38.95645469000 | -77.02220865000
6/28/12 | 1088637 | 0 | 8TH ST | NW | 7/2/12 | 4M075 | 4M075DC | (Light out) | BCM- 7-2-2012 - I. Paraway repaired Light. | High Pressure Sodium | 38.95640844000 | -77.02396296000
6/28/12 | 1088636 | 0 | 8TH ST | NW | 6/28/12 | 4M075 | 4M075DC | (Light out) |  | High Pressure Sodium | 38.95640844000 | -77.02396296000
6/27/12 | 1088392 | 0000 | SUITLAND PKY | SE | 6/28/12 | 83281 | 82381 | (No current) | BCM - 6-27-12 I. Paraway repaired by resplicing Wire in Pole# 82392 | High Pressure Sodium | 38.86351812000 | -77.00055997000
6/25/12 | 1088282 | 1423 | 35TH ST | NW | 9/7/12 | 20901 | 2G196 | (Light out) | 4-17-12 Hudson/Tom - open - these are old poles that will be removed (VW) DA 4-17-12 @ 240am C .aShton pole #20901 NC Underground - no feed DA 6-28-12 @ 1006pm C Ashton pole #20901 NC Underground no feed wire | High Pressure Sodium | 38.90838737000 | -77.06913765000
6/25/12 | 1088252 | 300 | 34TH PL | NE | 6/28/12 | 74813DC | 7A088DC | (Light out) | BCM - 6-28-12 - S. Manning repaired Light | High Pressure Sodium | 38.85998206000 | -76.95477112000
6/25/12 | 1088189 | 1001 | NEW HAMPSHIRE AVE | NW | 6/27/12 | 23862 | 2G674 | (Light out) | DA 6-27-12 @ 110am C AShton repaired pole #23862 twin light and trimmed tree | High Pressure Sodium | 38.90308383000 | -77.04974132000
6/25/12 | 1088130 | 0 | OVERLOOK AVE | SE | 6/25/12 | 81816 | 88089 | (Light out) | DA 6-25-12 @ 300am B Brown repaired pole #81816 | High Pressure Sodium | 38.83181785000 | -77.01472372000
6/21/12 | 1087942 | 300 | D ST | SW | 6/21/12 | 21632 | 6L647 | (Light out) | DA 6-21-12 @ 1025pm C Ashton repaired pole #21632 | High Pressure Sodium | 38.88513746000 | -77.01599912000
6/21/12 | 1087941 | 300 | C ST | SW | 6/21/12 | 21791 | 6L634 | (Light out) | DA 6-21-12 @ 1015pm C Ashton repaired pole #21791 | High Pressure Sodium | 38.88598796000 | -77.01678754000
6/21/12 | 1087933 | 1000 | H ST | NW | 7/18/12 | 22618 | 2G962 | (Light out) | 7-16-12 Hudson/tom - open - light is in construction area (vw) BCM - 7-10-12 - I. Paraway No Current - DA 6-26-12 @ 215am C Ashton pole #22618 not accessable construction are - City Central, Clark construction | High Pressure Sodium | 38.89990719000 | -77.02660550000
6/21/12 | 1087932 | 0 | H ST | NW | 7/11/12 | 22620 | 2G966 | (Light out) | DA 6-26-12 @ 215am C Ashton pole #22620 not accessable construction are - City Central, Clark construction | High Pressure Sodium | 38.89996191000 | -77.02590015000
6/21/12 | 1087931 | 0 | H ST | NW | 7/11/12 | 22622 | 2G972 | (Light out) | DA 6-26-12 @ 215am C Ashton pole #22622 not accessable construction are - City Central, Clark construction | High Pressure Sodium | 38.89990526000 | -77.02482158000
6/21/12 | 1087930 | 1000 | NEW YORK AVE | NW | 7/11/12 | 22912 | 2L064 | (Light out) | DA 6-26-12 @ 1115pm C Ashton pole #22912 not accessable construction are - City Central, Clark construction | High Pressure Sodium | 38.90130097000 | -77.02614564000
6/21/12 | 1087929 | 0 | 11TH ST | NW | 7/11/12 | 23377 | 2L023 | (Light out) | BCM - I. Paraway repaired pole. 2 CRACKED GLOBES DA 6-26-12 @ 215am C Ashton pole #23377 not accessable construction are - City Central, Clark construction | High Pressure Sodium | 38.90046875000 | -77.02690544000
6/21/12 | 1087928 | 800 | 11TH ST | NW | 7/11/12 | 23378 | 2L020 | (Light out) | DA 6-26-12 @ 215am C Ashton pole #23378 not accessable construction are - City Central, Clark construction | High Pressure Sodium | 38.90015315000 | -77.02690628000
6/20/12 | 1087851 | 3300 | SHERMAN AVE | NW | 6/21/12 | 12898 | 1L288 | (Light out) | DA 6-21-12 @ 325am K dunton repaired pole #12898 | High Pressure Sodium | 38.93167505000 | -77.02676573000
6/20/12 | 1087850 | 3408 | SHERMAN AVE | NW | 8/29/12 | 13073 | 1L294 | (Light out) | 06-21-12 Hudson and Tom Refer to DDOT. new foundation and light wires were not incorporated in duct (WP).DA 6-21-12 @ 315am K dunton pole #13073 NC underground 0 volts | High Pressure Sodium | 38.93221585000 | -77.02683398000
6/19/12 | 1087812 | 1301 | U ST | NW | 6/20/12 | 11721 | 1G521 | (Light out) | DA 6-20-12 @ 220am CAShton pole #11721all t base doors are secured in this area 12-00164592-Streetlight Repair 1301 U St NW, Washington, DC 20009, USA This issue has an image. You can view it here http://seeclickfix.com/issues/197125 . Plate is | High Pressure Sodium | 38.91709342000 | -77.03069626000
6/19/12 | 1087733 | 2124 | I ST | NW | 6/19/12 | 28107 | 2A184 | (Light out) | DA 6-19-12 @ 140am T Richards repaired pole #28107 | High Pressure Sodium | 38.90064216000 | -77.04764401000
6/18/12 | 1087698 | 3213 | M ST | NW | 6/19/12 | 33000 | 2A105 | (Light out) | DA 6-19-12 @ 235am C Ashton pole #33000 needs 175 lens refer to wo #1087651 unknown 12-00163447-alley light is down please repair cwDesc: ALLEYLIGHT REPAIR | Mercury Vapor | 38.90555735000 | -77.06458373000
6/18/12 | 1087697 | 0 | K ST | NW | 6/19/12 | 22403 | 6A076 | (Light out) | DA 6-19-12 @ 1200am C AShton repaired pole #22403 | High Pressure Sodium | 38.90260529000 | -77.02008282000
6/18/12 | 1087651 | 3213 | M ST | NW | 6/22/12 | 33000 | 2A105 | (Light out) | K. Greenfield completed on 6-21-12 Installed 3FT arm, 70hps fixture DA 6-19-12 @ 235am C Ashton pole #33000 needs 175mv lens poe is only accessable by ladder 12-00163177-POLE WAS HIT BY A TRUCK....LIVE WIRES FROM POLE cwDesc: STREETLIGHT REPAIR | Mercury Vapor | 38.90555735000 | -77.06458373000
6/18/12 | 1087632 | 1426 | ROBINSON ST | SE | 6/18/12 | 81726 | 88003 | (Light out) | DA 6-17-12 @ 1055pm B Brown repaired pole #81726 | High Pressure Sodium | 38.84958811000 | -76.98335695000
6/17/12 | 1087608 | 0 | NEW YORK AVE | NE | 6/18/12 | 58770 | 5A047 | (Light out) | DA 6-18-12 @ 1210am T Richards repaired pole #58770 | High Pressure Sodium | 38.91700054000 | -76.96267103000
6/17/12 | 1087606 | 1301 | U ST | NW | 6/19/12 | 11721 | 1G521 | (Light out) | DA 6-9-12 @ 140am C Ashton pole #11721 fixture is secured 12-00162446-Streetlight Repair 1301 U St NW, Washington, DC 20009, USA This issue has an image. You can view it here http://seeclickfix.com/issues/196244 . Plate is ajar. Used as stash sto | High Pressure Sodium | 38.91709342000 | -77.03069626000
6/14/12 | 1087524 | 1418 | SHIPPEN LN | SE | 6/19/12 | 81758 | 88035 | (Light out) | DA 6-19-12 @ 110am B Brown repaired pole #81758 12-00160423-The street light is located in front of 1416 and 1418 Shippen Ln SE. Thank you so much!! cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84969312000 | -76.98374846000
6/14/12 | 1087503 | 2316 | 18TH ST | NW | 6/19/12 | 11534 | 1G495 | (Light out) | DA 6-19-12 @ 1245am C ashton repaired pole #11534 | High Pressure Sodium | 38.92021109000 | -77.04195657000
6/13/12 | 1087383 | 1332 | 35TH ST | NW | 6/20/12 | 20903 | 2G192 | (Light out) | 06-20-12 Al Young pulled in30' #10 cable 15' per le. Spliced MH and in base of pole. 4#8 splices (WP). DA 6-15-12 @ 255am C AShton pole #20903 NC Underground | High Pressure Sodium | 38.90762144000 | -77.06910533000
6/13/12 | 1087371 | 0 | 18TH ST | NW | 6/15/12 | 24750 | 2U536 | (Light out) | DA 6-15-12 @ 1205am CAshton repaired pole #24750 | High Pressure Sodium | 38.90553328000 | -77.04178130000
6/13/12 | 1087334 | 0 | I ST | SE | 7/6/12 | 67647 | 6A423 | (No current) | 07-06-12 Hudson and Tom Area under construction(WP). | High Pressure Sodium | 38.87920166000 | -77.00270681000
6/12/12 | 1087308 | 0 | NEW YORK AVE | NE | 6/12/12 | 58770 | 5A047 | (Light out) | WBlack-MOT sceduled for the 16th | High Pressure Sodium | 38.91700054000 | -76.96267103000
6/12/12 | 1087238 | 418 | NEW YORK AVE | NW | 7/3/12 | 60064 | 6A170 | (Light out) | Work Completed 07-02-12 Jeremiah Lancaster and Crew. New pole next to old pole (WP). 06-15-12 Darrell Dixon and Damien Smith Breakdown. Unable to rod. Refer to construction. New light have been installed at this location. Appears the old lights are coming | High Pressure Sodium | 38.90422287000 | -77.01773238000
6/12/12 | 1087227 | 0 | U ST | NW | 6/14/12 | 11722 | 1G527 | (Light out) | DA 6-14-12 @ 115am C Ashton repaired pole #11722 | High Pressure Sodium | 38.91709757000 | -77.02977696000
6/12/12 | 1087224 | 1713 | 7TH ST | NW | 6/13/12 | 25650 | 6A833 | (Light out) | DA 6-12-12 @ 930pm C Ashton repaired pole #25650 | High Pressure Sodium | 38.91300300000 | -77.02201369000
6/12/12 | 1087214 | 5400 | 54TH ST | SE | 6/18/12 | 75634 | 75634DC | (Light out) | DA 6-17-12 @ 950pm B Brown repaired pole #75634 | High Pressure Sodium | 38.88271266000 | -76.92421599000
6/12/12 | 1087210 | 815 | V ST | NW | 6/13/12 | 14236 | 1U040 | (Light out) | DA 6-13-12 @ 940pm C Ashton repaired pole #14236 | Incandescent | 38.91816509000 | -77.02346836000
6/12/12 | 1087179 | 900 | 3RD ST | SE | 6/13/12 | 67529 | 6A457 | (Light out) | DA 6-13-12 @ 240am K dunton repaired pole #37529 | High Pressure Sodium | 38.87896332000 | -77.00211088000
6/12/12 | 1087154 | 1400 | SHIPPEN LN | SE | 6/12/12 | 81734 | 88011 | (Light out) | DA 6-11-12 @ 1005pm B Brown repaired pole #81734 | High Pressure Sodium | 38.84897224000 | -76.98310254000
6/12/12 | 1087149 | 1475 | BRUCE PL | SE | 6/12/12 | 81731 | 88008 | (Light out) | DA 6-11-12 @ 1105pm B Brown repaired pole #81731 | High Pressure Sodium | 38.85043302000 | -76.98303184000
6/11/12 | 1087109 | 4918 | 49TH PL | NE | 6/27/12 | 71283DC | 7A215 | (Light out) | BCM - 6-26-2012 LIGHT ON D. WEBB.DA 6-14-12 @ 110am T Richards repired pole #71283dc reinserted loose starter | High Pressure Sodium | 38.89857711000 | -76.93088757000
6/10/12 | 1086946 | 3600 | O ST | NW | 6/14/12 | 21091 | 2G152 | (Light out) | 06-11-12 Hudson and Tom Pole removed by MC Dean (WP). DA 6-0-12 @ 1155pm CAshton pole #21091 NC Underground no feed | High Pressure Sodium | 38.90765383000 | -77.07088676000
6/10/12 | 1086945 | 3623 | O ST | NW | 6/12/12 | 21090 | 2G153 | (Light out) | 06-11-12 Hudson and Tom Pole removed by MC Dean (WP).DA 6-11-12 @ 1200am C Ashton pole #21090 NC Underground | High Pressure Sodium | 38.90774375000 | -77.07124202000
6/4/12 | 1086532 | 4918 | 49TH PL | NE | 6/8/12 | 71283DC | 7A215 | (Light out) | DA 6-7-12 @ 1145pm T Richards pole #71283dc light is on and working DA 6-7-12 @ 235am T Richards repaired pole #71283dc reinstalled loose starter | High Pressure Sodium | 38.89857711000 | -76.93088757000
6/4/12 | 1086492 | 929 | MONROE ST | NE | 6/4/12 | 56163 | 56163DC | (Light out) | DA 6-4-12 @ 355am B Brown repaired pole #56163 instaled dc on pole tag | High Pressure Sodium | 38.93252669000 | -76.99290402000
5/31/12 | 1086327 | 0 | 23RD ST | NW | 6/1/12 | 28306 | 2L462 | (Light out) | DA 6-1-12 @ 140am CAshton repaired pole #28306 | High Pressure Sodium | 38.90131405000 | -77.05023193000
5/31/12 | 1086302 | 0 | NEW YORK AVE | NE | 6/5/12 | 58770 | 5A047 | (Light out) | WBlack-6-5-12-scheduled for next MOT visit DA 6-5-12 @ 355am B Brown pole #58770 needs big boom | High Pressure Sodium | 38.91700054000 | -76.96267103000
5/30/12 | 1086192 | 2001 | 38TH ST | SE | 6/5/12 | 74791DC | 7A080DC | (Light out) | DA 6-5-12 2 255am T Richards repaired pole #74791dc | High Pressure Sodium | 38.86491456000 | -76.95229527000
5/29/12 | 1086052 | 2715 | WISCONSIN AVE | NW | 6/4/12 | 30176 | 3G024 | (Light out) | DA 6-4-12 @ 315am K Dunton repaired pole #30176 | High Pressure Sodium | 38.92562288000 | -77.07307088000
5/29/12 | 1085998 | 0 | SHERIDAN RD | SE | 5/30/12 | 81353DC | 8U654 | (Light out) | DA 5-30-12 @ 320am B Brown repaired pole #81353dc | High Pressure Sodium | 38.85641207000 | -76.99331957000
5/29/12 | 1085951 | 1411 | 37TH ST | NW | 2/11/13 | 21142 | 2G206 | (Light out) | D.Dixon on 6-1-12. Refer to DDOT Unknown company are installing new streetlights next to exiting poles. DA 5-30-12 @ 1200am C Ashton pole #21142 NC Underground no feed - needs t base door | High Pressure Sodium | 38.90801099000 | -77.07168004000
5/29/12 | 1085950 | 3500 | P ST | NW | 5/30/12 | 21005 | 2G130 | (Light out) | New pole has been installed. DA 5-29-12 @ 1120pm C Ashton pole #21005 there is no pole - pole base intact | High Pressure Sodium | 38.90876207000 | -77.06960266000
5/29/12 | 1085949 | 1428 | 35TH ST | NW | 6/4/12 | 20900 | 2G198 | (Light out) | DA 6-3-12 pole #20900 light is on and working DA 5-29-12 @ 1115pm C AShton pole #20900 NC Underground - no feed D.Dixion 5/30/2012 2 #8 copper butt splice | High Pressure Sodium | 38.90862777000 | -77.06914877000
5/29/12 | 1085948 | 3424 | P ST | NW | 9/7/12 | 21006 | 2G131 | (Light out) | Wayne Richard on 6-18-12. Refer to DDOT) M.C. Dean is in the process of installing new streetlight pole and removing the old ones. DA 5-29-12 @ 1130pm C AShton pole #21006 NC Underground - no feed D.Dixion 5/30/2012 | High Pressure Sodium | 38.90869051000 | -77.06861216000
5/24/12 | 1085855 | 4202 | 13TH ST | NW | 5/25/12 | 4K434 | 4U150 | (Light out) | DA 5-24-12 @ 1130pm J Brown repaired pole #4k43 | High Pressure Sodium | 38.94219793000 | -77.02978242000
5/24/12 | 1085816 | 4832 | NANNIE HELEN BURROUGHS AVE | NE | 6/4/12 | 71293DC | 7A223DC | (Light out) | WBlack-CFreeburger-6-3-12-QC'd light is onDA 5-30-12 @ 125am T Richards repaired lose wire in powerdoor pole #71293dc | High Pressure Sodium | 38.89895905000 | -76.93289413000
5/23/12 | 1085769 | 3008 | SHERMAN AVE | NW | 5/25/12 | 12818 | 1G417 | (Light out) | DA 5-25-12 @ 1225am K Dunston repaired pole #12818 12-00137283-Light appeared to have been fixed on Monday after being reported, however light is out again. Resident thinks it might be a shortage cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92802282000 | -77.02621999000
5/21/12 | 1085635 | 0 | MONTANA AVE | NE | 5/23/12 | 59013 | 59013DC | (Light off/on) | DA 5-22-12 @ 1150pm B Brown pole #59013 light is on and working DA 5-22-12 @ 245am B Brown repaired pole #59013 | High Pressure Sodium | 38.91653600000 | -76.97768633000
5/17/12 | 1085257 | 1421 | 34TH ST | NW | 5/21/12 | 21073 | 2G189 | (Light out) | DA -- @ 100am C Ashton repaired pole #21073 installed globe and trimmed tree | High Pressure Sodium | 38.90848178000 | -77.06790108000
5/16/12 | 1085185 | 4918 | 49TH PL | NE | 5/21/12 | 71283DC | 7A215 | (Light out) | 05-21-12 Lancaster/Edwards Replaced TL Photo Cell (WP) | High Pressure Sodium | 38.89857711000 | -76.93088757000
5/16/12 | 1085153 | 0 | 7TH ST | NW | 5/17/12 | 25658 | 6U446 | (Light out) | DA 5-17-12 @ 300am C Ashtn repaired pole #25658 | High Pressure Sodium | 38.90864244000 | -77.02207884000
5/16/12 | 1085097 | 2720 | WISCONSIN AVE | NW | 5/16/12 | 30138 | 3G023 | (Light out) | DA 5-16-12 @ 115am K unton repaired pole #30138 and trimmed tree | High Pressure Sodium | 38.92584443000 | -77.07330461000
5/15/12 | 1085045 | 2206 | 18TH ST | NW | 5/23/12 | 11411 | 1G502 | (Light out) | DA 5-23-12 @ 130am C Ashton pole #11411 light is on and working 05-18 D.Dixon Neutral loose in T-Base - 1 #8 copper butt splice (WP)DA 5-16-12 @ 205am C Ashton pole #11411 after installing new fixture low voltage HN 0 volts, HG 121volts GN 121 Volts | High Pressure Sodium | 38.91905896000 | -77.04152631000
5/14/12 | 1084949 | 200 | RIGGS RD | NW | 5/30/12 | 4A002 | 4J683 | (Light out) | DA 5-29-12 @ 1143pm J Brown pole #4A002 light is on an working 5-24-12 A Young/R Fike - completed - had to blow out hole - installed 440 #10 wire 220' #8 bare copper 4 #8 butt splices and 2 #6 butt splices - made splices in base of pole grounded pole in | High Pressure Sodium | 38.93966490000 | -77.03282752000
5/14/12 | 1084933 | 3043 | BLADENSBURG RD | NE | 5/15/12 | 51245DC | 5A141DC | (Light out) | DA 5-14-12 @ 10455pm B Brown repaired pole #51245dc | High Pressure Sodium | 38.93032628000 | -76.95815755000
5/14/12 | 1084902 | 4700 | NORTH CAPITOL ST | NE | 6/4/12 | 4R754 | 4A795 | (Light out) | DA 5-14-12 @ 340am B Brown repaired no pole id tag | High Pressure Sodium | 38.94814388000 | -77.00879153000
5/11/12 | 1084683 | 0 | 18TH ST | NW | 5/11/12 | 24534 | 2U529 | (Light out) | DA 5-11-12 @ 250am C AShton repaired pole #24534dc | High Pressure Sodium | 38.90591907000 | -77.04143681000
5/10/12 | 1084596 | 5139 | HANNA PL | SE | 5/11/12 | 75459 | 75459DC | (Light out) | DA 5-10-12 @ 1135pm T Richards repaired pole #75459 and cleaned lens | High Pressure Sodium | 38.87962468000 | -76.92848157000
5/9/12 | 1084537 | 1200 | NEW HAMPSHIRE AVE | NW | 5/10/12 | 23855 | 2G724 | (Light out) | DA 5-9-12 @ 1140pm C Ashton repaired pole #23855 | High Pressure Sodium | 38.90575777000 | -77.04721112000
5/9/12 | 1084522 | 800 | 4TH ST | NW | 5/10/12 | 60448 | 6S459 | (Light out) | DA 5-10-12 @ 355pm pole #60448 no longer at this location was replaced with a new teardrop with pole #6S459 | High Pressure Sodium | 38.90032749000 | -77.01608012000
5/9/12 | 1084478 | 3222 | 14TH ST | NE | 5/10/12 | 51220DC | 5A114DC | (Light out) | DA 5-10-12 @ 1240am B Brown repaired pole #51220dc 12-00121252- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93068379000 | -76.98625793000
5/6/12 | 1084243 | 0329 | RHODE ISLAND AVE | NE | 5/7/12 | 50083 | 5A064 | (Light out) | DA 5-7-12 @ 330am B Brown repaired pole #50083 | High Pressure Sodium | 38.91949870000 | -77.00096444000
5/2/12 | 1084067 | 3231 | P ST | NW | 5/10/12 | 21021 | 2G146 | (Light out) | 5-8-12 Hudson/Tom - completed - this pole will be replaced by new poles and new duck - this is non-existing pole (vw) DA 5-8-12 @ 210am C AShton pole #21021 NC Underground | High Pressure Sodium | 38.90888764000 | -77.06433429000
5/2/12 | 1084054 | 1101 | NEW HAMPSHIRE AVE | NW | 5/8/12 | 23859 | 2G712 | (Light dim) | DA 5-8-12 @ 115am C Ashton pole #23859 light is on and working 122/122/0 DA 5-7-12 @ 150am C AShton repaired pole #23859 | High Pressure Sodium | 38.90420020000 | -77.04868539000
5/2/12 | 1084052 | 1101 | NEW HAMPSHIRE AVE | NW | 5/2/12 | 23859 | 2G712 | (Light out) |  | High Pressure Sodium | 38.90420020000 | -77.04868539000
5/1/12 | 1083980 | 422 | K ST | NW | 5/3/12 | 60465 | 6A123 | (Light out) | DA 5-2-12 @ 1150pm T Richards adjusted TLPC pole #60465 | High Pressure Sodium | 38.90260315000 | -77.01690044000
5/1/12 | 1083970 | 815 | 6TH ST | NW | 5/7/12 | 60542 | 6M707 | (Light out) | DA 5-7-12 @ 425am T Richards pole #60542 light is on and working DA 5-3-12 @ 1240am T Richards repaired pole no pole id tag next to pole #60542 | High Pressure Sodium | 38.90031850000 | -77.01979505000
5/1/12 | 1083969 | 1811 | WILTBERGER ST | NW | 2/14/13 | 29506 | 1M016 | (Light out) | 5-3-12 Darryl/Damien - completed - new DCSL mh's being installed by Ft. Myers Construction (VW) DA 5-3-12 @ 350am C Ashton pole #29506 NC Underground 0 volts | High Pressure Sodium | 38.91459765000 | -77.02092164000
5/1/12 | 1083968 | 1827 | WILTBERGER ST | NW | 2/14/13 | 29507 | 1M014 | (Light out) | 5-3-12 Darryl/Damien - completed - new DCSL mh's being installed by Ft. Myers Construction (VW) DA 5-3-12 @ 400am C Ashton pole #29507 NC Underground 0 volts | High Pressure Sodium | 38.91496601000 | -77.02091840000
5/1/12 | 1083960 | 926 | T ST | NW | 5/2/12 | 13450 | 1L367 | (Light out) | DA 5-2-12 @ 355am K Dunton repaired pole #13450 | High Pressure Sodium | 38.91552698000 | -77.02529625000
5/1/12 | 1083899 | 717 | BARNES ST | NE | 5/1/12 | 72462DC | 7A473 | (Light out) | DA 5-1-12 @ 349am T .Richards repaired pole #72462dc | High Pressure Sodium | 38.90163933000 | -76.95010523000
4/30/12 | 1083827 | 723 | BARNES ST | NE | 5/1/12 | 72463DC | 7A472 | (Light out) | DA 5-1-12 @ 342am T Richards repaired pole #71463dc installed bird flap | High Pressure Sodium | 38.90181026000 | -76.94988632000
4/30/12 | 1083802 | 1200 | ALLISON ST | NW | 5/2/12 | 4K102 | 4U137 | (Light out) | DA 5-2-12 @ 110am J Brown repaired pole #4K102 | High Pressure Sodium | 38.94501678000 | -77.02957418000
4/30/12 | 1083783 | 2313 | WISCONSIN AVE | NW | 5/2/12 | 30164 | 3G074 | (Light out) | DA 5-2-12 @ 300am K Dunton pole #30164 light is okay powerdoor okay 4-30-12 Hudson/Tom - open - unable to service due to construction area (VW) DA 4-30-12 @ 320am C Ashton installed 400hps lmap pole #30164 needs 400 powerdoor | High Pressure Sodium | 38.92075726000 | -77.07170014000
4/30/12 | 1083782 | 0 | WISCONSIN AVE | NW | 4/30/12 | 30134 | 3G003 | (Light out) | DA 4-30-12 @ 300am C Ashton repaired pole #30134 | High Pressure Sodium | 38.92806668000 | -77.07330376000
4/25/12 | 1083555 | 60 | M ST | SE | 4/26/12 | 67424 | 6L599 | (Light out) | DA 4-26-12 @ 315am T Richards repaired pole #67424 | High Pressure Sodium | 38.87659105000 | -77.00715580000
| 1083533 | 423 | NEW YORK AVE | NW | 2/21/13 | 25923 | 6M764 | (Light out) | 2/21/13 TN: there is no funding for pole painting at this time. it is on the list since we have funding for pole painting. DA 4-26-12 pole #25923 light is on needs painted 12-00106642-Streetlight Repair 906 O St NW, Washington, DC 20001, USA This | High Pressure Sodium | 38.90450411000 | -77.01761089000
4/24/12 | 1083436 | 1410 | 34TH ST | NW | 4/26/12 | 21074 | 2G187 | (Light out) | DA 4-26-12 @ 125am C Ashton repaired pole #21074 | High Pressure Sodium | 38.90809992000 | -77.06790137000
4/23/12 | 1083248 | 0000 | DAVENPORT ST | NW | 4/29/12 | 30009DC | 3A246DC | (Light out) | DA 4-29-12 @ 1115pm K Dunton repaired pole #30009dc DA 4-23-12 @ 1215am K Dunton pole #30009dc - needs 100 fixture waiting on materials | Mercury Vapor | 38.95206814000 | -77.08071551000
4/23/12 | 1083247 | 0 | SEDGWICK ST | NW | 4/29/12 | 30008DC | 3A368DC | (Light out) | DA 4-29-12 @ 1045pm K Dunton repaired pole #30008dc 4-25-12 M Craig/Bobby - completed - installed pole tag (VW) DA 4-23-12 @ 1200am K Dunton no pole tag - needs 100 fixture waiting on materials | Incandescent | 38.94040143000 | -77.09254074000
4/20/12 | 1083198 | 0 | H ST | NE | 4/20/12 | 68250DC | 68520 | (Light out) | DA 4-20-12 @ 150am T .Richards repaired pole #68250dc | High Pressure Sodium | 38.87458286000 | -77.00571187000
4/19/12 | 1083165 | 1625 | NEW YORK AVE | NE | 6/4/12 | 50062 | 5A053 | (Light out) | A. Johnson repaired leaning pole from Failed Q.C. 05-18 Al Johnson 28' pole and lighting equipment installed (WP) DeVon Smith - pole still standing 4-19-12 AL Johnson/V Ham - open - need foundation for a 15inch t-base. | High Pressure Sodium | 38.91708690000 | -76.98011488000
4/19/12 | 1083086 | 3945 | PENNSYLVANIA AVE | SE | 4/19/12 | 78518DC | 7E149DC | (Light out) | DA 4-18-12 @ 1140pm T> Richards repaired pole #78518dc | High Pressure Sodium | 38.86392263000 | -76.94743025000
4/19/12 | 1083085 | 4000 | SOUTHERN AVE | SE | 4/19/12 | 78576 | 78576DC | (Light out) | DA 4-18-12 @ 1050pm T .Richards repaired pole #78576 and installed pole id tag | High Pressure Sodium | 38.86379385000 | -76.94657249000
4/18/12 | 1083073 | 301 | 4TH ST | SW | 4/19/12 | 21580 | 6L636 | (Light out) | DA 4-18-12 @ 1100pm C. Ashton repaired pole #21580 | High Pressure Sodium | 38.88593815000 | -77.01743975000
4/18/12 | 1082989 | 0 | 3RD ST | NW | 4/19/12 | 59991 | 5A184 | (Light out) | DA 4-18-12 @ 1125pm B Brown repaired pole #59991 | High Pressure Sodium | 38.91407956000 | -77.01569433000
4/18/12 | 1082982 | 2403 | BENNING RD | NE | 4/19/12 | 59616DC | 5M310 | (Light out) | DA 4-18-12 @ 1040pm B Brown repaired pole #59616dc | High Pressure Sodium | 38.89825539000 | -76.97195297000
4/18/12 | 1082980 | 0 | 3RD ST | SW | 2/11/13 | 21552 | 6L629 | (Light out) | Grundley Construction with the approval of DDOT contact person is Pat (240) 285-4347 (VW) 3-5-12 AL Young complete - mh is being discontinued call Mike Fudrowski (240) 372-7135 or Pat (240) 285-4347 o(VW) | High Pressure Sodium | 38.88594959000 | -77.01531492000
4/18/12 | 1082972 | 0 | D ST | SW | 4/18/12 | 21625 | 6L714 | (Light out) | DA 4-18-12 @ 310am C Ashton repaired pole #21625 | High Pressure Sodium | 38.88478652000 | -77.01928219000
4/17/12 | 1082948 | 1112 | Q ST | NW | 4/17/12 | 29306DC | 2U047DC | (Light out) | DA 4-17-12 @ 1010pm C Ashton repaired pole #29306dc | Incandescent | 38.91083084000 | -77.02756095000
4/16/12 | 1082864 | 0 | KENILWORTH AVE | SE |  | 79497 | 7A150 | (Light out) | BCM - 5-8-2011 - NEED HELP TO MOVE JERSEY WALLS TO GET BOOM TRUCK IN ORDER TO PULL WIRE FROM HANDHOLD OF POLE. | High Pressure Sodium | 38.88456308000 | -76.96344581000
4/16/12 | 1082845 | 1218 | CONNECTICUT AVE | NW |  | 24532 | 2U519 | (No current) | Refer to DDOT traffic combo pole. Streetlight and traffic light share the same duct. | High Pressure Sodium | 38.90651643000 | -77.04185036000
4/15/12 | 1082791 | 1500 | 35TH ST | NW | 9/7/12 | 20899 | 2G132 | (Light out) | 4-17-12 Hudson/Tom - open - these are old poles that will be removed (VW) DA 4-17-12 @ 233am C .aShton pole #20599 NC Underground - no feed | High Pressure Sodium | 38.90878186000 | -77.06885614000
4/15/12 | 1082790 | 3424 | P ST | NW | 4/17/12 | 21006 | 2G131 | (Light out) | DA 4-17-12 @ 224am C. Ashton repired pole #21006 | High Pressure Sodium | 38.90869051000 | -77.06861216000
4/15/12 | 1082782 | 0000 | H ST | NE | 4/17/12 | 68260DC | 68260 | (Light out) | DA 4-17-12 @ 1010pm T. Richards repaired pole #68260dc DA 4-16-12 @ 1120pm T. Richards - needs big boom and MOT | High Pressure Sodium | 38.90032135000 | -77.00885912000
4/15/12 | 1082781 | 777 | NORTH CAPITOL ST | NE | 4/17/12 | 68241DC | 68241 | (Light out) | DA 4-17-12 @ 1040pm T Richards pole #68241dc light is on and working 4-17-12 Hudson/Tom - completed - replaced 25' #10 wire from pole base to mh - made terminations 1 #8 butt splice 1pink c-crimp dyd 1/0 (VW) DA 4-16-12 @ 1105pm T. Richards pole #682 | High Pressure Sodium | 38.90010486000 | -77.00885876000
4/15/12 | 1082780 | 0 | H ST | NE | 4/17/12 | 68250DC | 68520 | (Light out) | DA 4-17-12 @ 1025pm T. Richards repaired pole #68250dc DA 4-16-12 @ 1115pm T. Richards - needs big boom and MOT | High Pressure Sodium | 38.87458286000 | -77.00571187000
4/15/12 | 1082764 | 1810 | 14TH ST | NW | 4/19/12 | 26563 | 2A082 | (Light out) | DA 4-19-12 @ 110am CAshton pole #26563 light is on and working DA 4-17-12 @ 1020pm C Ashton repaired pole #26563 | High Pressure Sodium | 38.91448846000 | -77.03208389000
| 1082740 | 1423 | 35TH ST | NW | 1/29/13 | 20901 | 2G196 | (Light out) | 4-17-12 Hudson/Tom - open - these are old poles that will be removed (VW) DA 4-17-12 @ 240am C .aShton pole #20901 NC Underground - no feed 12-00096350-The light has been out for weeks cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90838737000 | -77.06913765000
4/11/12 | 1082582 | 2512 | SHERIDAN RD | SE | 4/11/12 | 81366DC | 8M051 | (Light out) | DA 4-11-12 @ 325am B. Brown repaired pole #81366dc adjusted photocell | High Pressure Sodium | 38.85995179000 | -76.99345916000
4/10/12 | 1082536 | 1500 | 35TH ST | NW | 4/11/12 | 20899 | 2G132 | (Light out) | DA 4-11-12 @ 1210am C.ashton repaired pole #20899 made splice @ T Base | High Pressure Sodium | 38.90878186000 | -77.06885614000
4/10/12 | 1082535 | 3400 | O ST | NW | 4/11/12 | 21100 | 2G166 | (Light out) | DA 4-11-12 @ 1225am C.ashton repaired pole #21100 made splice @ T Base | High Pressure Sodium | 38.90771415000 | -77.06801859000
4/10/12 | 1082525 | 777 | BARNES ST | NE | 4/12/12 | 72464DC | 7A470 | (Light off/on) | DA 4-12-12 T .Richards light is on and working DA 4-10-12 @ 1015pm T. Richards repaired pole #72464dc | High Pressure Sodium | 38.90215555000 | -76.94944817000
4/9/12 | 1082451 | 0 | NEW HAMPSHIRE AVE | NW | 4/10/12 | 23870 | 2G728 | (Light out) | DA 4-10-12 @ 1215am C. Ashton repaired pole #23870 | High Pressure Sodium | 38.90595274000 | -77.04670836000
4/9/12 | 1082445 | 3623 | O ST | NW | 4/10/12 | 21090 | 2G153 | (Light out) | DA 4-10-12@ 210am CaShton repaired pole #21090 | High Pressure Sodium | 38.90774375000 | -77.07124202000
4/9/12 | 1082444 | 1411 | 37TH ST | NW | 4/10/12 | 21142 | 2G206 | (Light out) | DA 4-10-12 @ 235am C .ashton repaired pole #21142 | High Pressure Sodium | 38.90801099000 | -77.07168004000
4/9/12 | 1082443 | 3624 | P ST | NW | 4/12/12 | 21001 | 2G124 | (Light out) | DA 4-12-12 C >ashton light found on and working 4-11-12 Hudson/Tom -completed - respliced hot and nuetral in pole base replaced 150w hps bulb 2 #8 butt splices (VW) | High Pressure Sodium | 38.90872996000 | -77.07099893000
4/9/12 | 1082442 | 1428 | 35TH ST | NW | 4/10/12 | 20900 | 2G198 | (Light out) | DA 4-10-12 @ 155am C. Ashton repaired pole #20900 | High Pressure Sodium | 38.90862777000 | -77.06914877000
4/8/12 | 1082359 | 1000 | 1ST ST | NW |  | 61105 | 6A232 | (Light out) | 4-11-12 Darryl/Damien - open - REFER to DDOT new lights been installed - lights appears to be scheduled to be taken out led cable from t-base to mh - exsting cable to light have been cut in mh - concrete dug up around base (VW) DA 4-11-12 @ 1250am K. D | High Pressure Sodium | 38.90337658000 | -77.01210139000
4/5/12 | 1082263 | 805 | KENNEDY ST | NW | 4/12/12 | 4M077 | 4M077DC | (Light out) | 4-10-12 Keith/G McDuffy - completed - iold pole disconnected by outside contractor - new poles being installed (VW) DA 4-5-12 @ 1111pm J .Brown pole #4m077 NC Underground | High Pressure Sodium | 38.95638695000 | -77.02437107000
4/4/12 | 1082222 | 3205 | HENSON RD | SE | 4/5/12 | 81789 | 88066 | (Light out) | DA 4-5-12 @ 200am B .Brown repaired pole #81789 Front 12-00087032- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84999072000 | -76.98289014000
4/3/12 | 1082111 | 0 | 8TH ST | NW | 4/4/12 | 22981 | 2M388 | (Light out) | DA 4-4-12 @ 345am C.ashton repaired pole #22981 | High Pressure Sodium | 38.90076702000 | -77.02288069000
4/3/12 | 1082095 | 4832 | NANNIE HELEN BURROUGHS AVE | NE | 4/3/12 | 71293DC | 7A223DC | (Light out) | DA 4-3-12 @ 1030pm T. Richards repaired pole #71293dc | High Pressure Sodium | 38.89895905000 | -76.93289413000
4/3/12 | 1082048 | 400 | RHODE ISLAND AVE | NW | 4/4/12 | 59988 | 5A180 | (Light out) | DA 4-4-12 @ 345am B. Brown repaired pole #59988 | High Pressure Sodium | 38.91371248000 | -77.01761756000
4/2/12 | 1082018 | 0 | H ST | NE | 4/2/12 | 68250DC | 68520 | (Bridge light out) | DA 4-2-12 @ 1020pm T. Richards repaired pole #68250dc | High Pressure Sodium | 38.87458286000 | -77.00571187000
3/29/12 | 1081735 | 3600 | P ST | NW | 4/12/12 | 21002 | 2G125 | (Light out) | 04-02 Hudson and Tom REFER to W/O # 1081734 VW - Walked down job checked pole base and MH. There is a new light working that has replaecd the old pole. (WP) DA 4-2-12 @ 325am C.ashton pole #21002 NC Underground no feed | High Pressure Sodium | 38.90864453000 | -77.07059706000
3/29/12 | 1081734 | 3600 | P ST | NW | 4/12/12 | 21003 | 2G126 | (Light out) | DA 4-12-12 C >ashton light found on and working 04-02 Hudson and Tom Walked down job checked pole base and MH. There is a new light working that has replaecd the old pole. (WP)DA 4-2-12 @ 335am C.ashton pole #21003 NC Underground no feed wire | High Pressure Sodium | 38.90874440000 | -77.07034165000
3/29/12 | 1081733 | 3600 | O ST | NW | 4/2/12 | 21093 | 2G154 | (Light out) | 04-02 Hudson and Tom Walked down job checked pole base and MH. There is a new light working that has replaecd the old pole. (WP)DA 4-2-12 @ 350am C.ashton pole #21093 NC Underground no feed wire | High Pressure Sodium | 38.90765947000 | -77.07043171000
3/29/12 | 1081732 | 3607 | O ST | NW | 4/2/12 | 21092 | 2G155 | (Light out) | DA 4-2-12 @ 320am T. Richards repaired pole #21092 | High Pressure Sodium | 38.90775240000 | -77.07075119000
3/29/12 | 1081729 | 3267 | P ST | NW | 5/10/12 | 21017 | 2G142 | (Light out) | 04-02 Hudson and Tom This job is under contract by capitol paving(202) 529-7225 and mc dean (202) 330-8409 (WP)DA 4-2-12 @ 215am C.Ashton pole #21017 NC Underground | High Pressure Sodium | 38.90886358000 | -77.06536598000
3/29/12 | 1081710 | 4878 | NANNIE HELEN BURROUGHS AVE | NE | 4/1/12 | 71291DC | 7A221DC | (Light out) | DA 4-1-12 @ 1050pm T. Richards repaired pole #71291dc | High Pressure Sodium | 38.89881397000 | -76.93206898000
3/29/12 | 1081709 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 4/3/12 | 71294DC | 7A226 | (Light out) | DA 4-3-12 light is on and working DA 4-1-12 @ 1100pm T. Richards repaired pole #71294dc | High Pressure Sodium | 38.89882951000 | -76.93342319000
3/29/12 | 1081693 | 900 | 3RD ST | SW | 4/5/12 | 68144 | 6A461 | (Light out) | DA 4-5-12 Light found on and working DA 4-2-12 @ 100am T. Richards all lights are on and working | High Pressure Sodium | 38.87851901000 | -77.00211175000
3/29/12 | 1081681 | 1765 | NEW YORK AVE | NE | 4/3/12 | 50060 | 5A051 | (Light out) | DA 4-3-12 light is on and working DA 3-30-12 @ 355am B .Brown repaired pole #50060 | High Pressure Sodium | 38.91711198000 | -76.97897966000
3/28/12 | 1081586 | 0 | EAST CAPITOL ST | NE |  | 63629 | 6M837 | (Light out) | BCM 3-29-2012 - I. Paraway traced wires to center island. feed was cut by 3rd party contractor. DA 3-29-12 @ 310am T Richards polle #63629 N/C Underground | High Pressure Sodium | 38.88956256000 | -76.97418443000
3/28/12 | 1081578 | 0000 | H ST | NE | 4/2/12 | 68248DC | 68248 | (Light out) | DA 4-2-12 @ 1010pm T. Richards repaired pole #68248dc 3-29-12 AL Young/R Fike - open - need big **boom** truck (VW) | High Pressure Sodium | 38.90004513000 | -77.00446924000
3/28/12 | 1081569 | 0 | 9TH ST | NW | 9/7/12 | 25436 | 2L559 | (Light out) | 3-30-12 AL Young/R Fike - there is a tempory pole that has traffic on it - mh is in middle of street you cannot run flex duct to temp pole - Brad Lewis the superintendent on site REFER to DDOT (VW) DA 3-28-12 @ 1130on C Ashton pole #25436 NC Undergro | High Pressure Sodium | 38.90407457000 | -77.02409965000
3/27/12 | 1081451 | 1475 | BRUCE PL | SE | 3/28/12 | 81731 | 88008 | (Light out) | DA 3-28-12 @ 340am T richards repaired pole #81731 | High Pressure Sodium | 38.85043302000 | -76.98303184000
3/25/12 | 1081275 | 0000 | MICHIGAN AVE | NE | 5/30/12 | 50071 | 2A058 | (Light out) | 5-22-12 Darryl/Damien made splices inside the manhole hole. See w.o.851703--Damien Smith on 2-5-10 Refer to DDOT streetlight and traffic share the same duct. DA 3-27-12 @ 255am T Richards pole #50071 NC Underground | High Pressure Sodium | 38.90029517000 | -77.03986681000
3/25/12 | 1081246 | 2512 | SHERIDAN RD | SE | 3/26/12 | 81366DC | 8M051 | (Light out) | G. Edwards completed on 3-26-12. Installed 400w hps lamp. | High Pressure Sodium | 38.85995179000 | -76.99345916000
3/21/12 | 1081091 | 2 | MASSACHUSETTS AVE | NE | 3/22/12 | 60928 | 6U602 | (Light out) | DA 3-21-12 @ 1035pm C.ashton repaired pole #60928 and repaired pole id tag | High Pressure Sodium | 38.89801466000 | -77.00755371000
3/21/12 | 1081042 | 0 | EAST CAPITOL ST | NE |  | 63629 | 6M837 | (Light out) | WBlack-3-22-12-will get on next MOT scheduling | High Pressure Sodium | 38.88956256000 | -76.97418443000
3/21/12 | 1081020 | 803 | T ST | NW | 3/22/12 | 13455 | 1L376 | (Light out) | 3-22-12 AL Young/Fike - completed installed 400w hps bulb (VW) | High Pressure Sodium | 38.91553002000 | -77.02328773000
3/21/12 | 1081017 | 0 | 7TH ST | NW | 3/22/12 | 14394 | 1M003 | (Light out) | DA 3-22-12 @ 1010pm C .Ashton repaired pole #14394 adjusted TLPC 3-22-12 AL Young/Fike - open - essesive traffice on a construction site corner - need to be done at night (VW) | High Pressure Sodium | 38.91567433000 | -77.02182460000
3/21/12 | 1081008 | 0 | H ST | NE | 3/22/12 | 68250DC | 68520 | (Light out) | WBlack-3-22-12-will get on next MOT scheduling | High Pressure Sodium | 38.87458286000 | -77.00571187000
3/21/12 | 1081007 | 1200 | 1ST ST | NE | 3/22/12 | 61243 | 6A273 | (Light out) | DA 3-21-12 @ 1045pm C Ashton repaired pole #61243 | High Pressure Sodium | 38.90637775000 | -77.00597499000
3/21/12 | 1080978 | 1530 | 11TH ST | NW | 3/21/12 | 25286 | 2U045 | (Light out) | DA3-21-12 @ 325am C.ashton repaired pole #25286 and installed pole id tag | High Pressure Sodium | 38.91105847000 | -77.02715860000
3/20/12 | 1080903 | 1765 | NEW YORK AVE | NE | 3/21/12 | 50060 | 5A051 | (Light out) | 3-21-12 Hudson/Tom - completed - installed 1-pc (VW) | High Pressure Sodium | 38.91711198000 | -76.97897966000
3/19/12 | 1080797 | 900 | 3RD ST | SW | 3/21/12 | 68144 | 6A461 | (Light out) | DA 3-21-12 @ 140am T Richards pole #68144 light is on and working previously repaired | High Pressure Sodium | 38.87851901000 | -77.00211175000
3/17/12 | 1080598 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 3/19/12 | 71294DC | 7A226 | (Light out) | Al Johnson repaired light using 1 400 watt high pressure sodium lamp-3/19/12 (KW) | High Pressure Sodium | 38.89882951000 | -76.93342319000
3/17/12 | 1080597 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 3/19/12 | 71270 | 71270DC | (Light out) | This pole is set up for demolition. Please check with Ddot. | High Pressure Sodium | 38.89827347000 | -76.92679095000
3/17/12 | 1080596 | 5403 | NANNIE HELEN BURROUGHS AVE | NE | 3/19/12 | 72648 | 7A191 | (Light out) | Al Johnson repaired light using 1 400 watt high pressure sodium lamp-3/19/12 (KW) | High Pressure Sodium | 38.89829839000 | -76.92250388000
3/14/12 | 1080407 | 3412 | 15TH ST | NE | 3/15/12 | 51211DC | 5A100DC | (Light out) | D 3-12-12 @ 108am B. Brown repaired pole #51211dc | Incandescent | 38.93257808000 | -76.98447612000
3/14/12 | 1080396 | 0 | PENNSYLVANIA AVE | NW | 3/15/12 | 23687 | 2G666 | (Light out) | 3-15-12 Darryl - complete - installed 400w hps bulb(VW) | High Pressure Sodium | 38.90280693000 | -77.05126474000
3/13/12 | 1080253 | 1000 | 3RD ST | SE | 3/15/12 | 68141 | 6A470 | (Light out) | DA 3-15-12 @ 400am T. Richards repaired pole #68141 | High Pressure Sodium | 38.87763332000 | -77.00211232000
3/13/12 | 1080252 | 900 | 3RD ST | SW | 3/15/12 | 68144 | 6A461 | (Light out) | DA 3-15-12 @ 140am T. Richards repaired pole #68144 | High Pressure Sodium | 38.87851901000 | -77.00211175000
3/10/12 | 1080091 | 3412 | DIX ST | NE | 3/12/12 | 74840 | 7A104 | (Light out) | DA 3-11-12 @ 1025pm T. Richards repaired pole #74840 | High Pressure Sodium | 38.89482686000 | -76.95696271000
3/8/12 | 1079931 | 0 | MONTANA AVE | NE | 3/9/12 | 59014DC | 59014 | (Light out) | DA 3-9-12 B. Brown repaired pole #59014dc | Mercury Vapor | 38.91668894000 | -76.97782076000
3/7/12 | 1079900 | 1950 | BENNING RD | NE | 3/8/12 | 59612DC | 5M317 | (Light out) | DA 3-7-12 @ 1005pm C. ashton repaired pole #59612dc adjusted TLPC | High Pressure Sodium | 38.89868854000 | -76.97411295000
3/4/12 | 1079721 | 0000 | OVERLOOK AVE | SW | 3/4/12 | 81834 | 88095 | (Light out) | DA 3-4-12 @ 1045pm T >Richards repaired pole #81834 | High Pressure Sodium | 38.83393831000 | -77.01328820000
3/4/12 | 1079653 | 0 | ANACOSTIA FWY | SE | 3/5/12 | 79467 | 7A131 | (Light out) | DA 3-5-12 @ 240am . Richards repaired pole #79467 | High Pressure Sodium | 38.88310417000 | -76.96392124000
3/1/12 | 1079560 | 1437 | LAWRENCE ST | NE | 3/2/12 | 52487DC | 5A158DC | (Light out) | 3-2-12 AL Young/Bunky complete - installed 100w hps bulb (VW) | High Pressure Sodium | 38.93179462000 | -76.98529938000
3/1/12 | 1079527 | 0 | CONNECTICUT AVE | NW | 3/2/12 | 38584 | 3E026 | (Light out) | DA 3-2-12 @ 1235am K .Dunton repaired pole #38584dc | High Pressure Sodium | 38.94397582000 | -77.06352631000
2/29/12 | 1079477 | 1272 | NEW HAMPSHIRE AVE | NW | 3/12/12 | 23851 | 2G759 | (Light out) | 3-12-12 AL Johnson/G Smith - completed - installed t-base 1-1/2 nut ground clip (VW) 3-6-12 G Edwards - open T-base nned to be replaced (VW) DA 3-5-12 @ 245am C.ashton pole #23851 needs base coveer West Side 12-00050590-Exposed wires at base of pole | High Pressure Sodium | 38.90689340000 | -77.04614952000
| 1079478 | 1262 | NEW HAMPSHIRE AVE | NW | 3/6/12 | 23852 | 2G757 | (Light out) | DA 3-6-12 @ 1230am C. Ashton repaired pole #23852 West Side 12-00050598-Light goes on and off. Probable loose wire. Also emits loud hum. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90669938000 | -77.04633627000
2/29/12 | 1079476 | 5900 | UTAH AVE | NW | 3/6/12 | 4B241DC | 4B241 | (Light out) | DA 3-6-12 @ 123am B. Brown repaired pole #4b241dc | High Pressure Sodium | 38.96717395000 | -77.06103400000
2/29/12 | 1079467 | 2108 | 18TH ST | NW | 3/5/12 | 11413 | 1G506 | (Light out) | DA 3-5-12 @ 335a C .aShton repaired pole #11413 | High Pressure Sodium | 38.91831567000 | -77.04154601000
2/28/12 | 1079377 | 0 | 7TH ST | NW | 4/16/12 | 25706 | 6A832 | (Light out) | 11-8-11 Darryl/Chris - traffic combo pole w/common duct - REFER to DDOt (VW) | High Pressure Sodium | 38.91270444000 | -77.02180700000
2/28/12 | 1079361 | 3200 | O ST | NW | 3/2/12 | 21110 | 2G173 | (Light out) | DA 3-2-12 @ 315am C .Aston repaired pole #21110 | High Pressure Sodium | 38.90787881000 | -77.06482911000
2/27/12 | 1079211 | 0 | 3RD ST | SW | 9/7/12 | 21552 | 6L629 | (Light out) | 3-8-12 Darryl/Damien - light was diconnected by Grundley Construction with the approval of DDOT contact person is Pat (240) 285-4347 (VW) 3-5-12 AL Young complete - mh is being discontinued call Mike Fudrowski (240) 372-7135 or Pat (240) 285-4347 o(V | High Pressure Sodium | 38.88594959000 | -77.01531492000
2/27/12 | 1079176 | 0 | KENILWORTH AVE | SE | 4/16/12 | 79497 | 7A150 | (Light out) | DA 2-26-12 T> Richards pole #79497 N/C Underground Ddot refers wo #1044669 | High Pressure Sodium | 38.88456308000 | -76.96344581000
2/27/12 | 1079175 | 5214 | NANNIE HELEN BURROUGHS AVE | NE |  | 72646 | 7A198 | (Light out) | DA 2-26-12 T .Richards pole #72646 N/C underground Ddot refer wo #1047474 | High Pressure Sodium | 38.89827561000 | -76.92455911000
2/27/12 | 1079174 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 3/2/12 | 72645 | 7S073 | (Light out) | DA 2-26-12 T .Richards pole #72645 N/C Underground Ddot refers wo #1047475 | High Pressure Sodium | 38.89826452000 | -76.92554310000
2/27/12 | 1079173 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 3/2/12 | 71270 | 71270DC | (Light out) | DA 2-26-12 T. Rchards pole #71270 N/C underground Ddot refers wo #1042337 | High Pressure Sodium | 38.89827347000 | -76.92679095000
2/27/12 | 1079172 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 3/2/12 | 71269 | 7A201 | (Light out) | DA 2-26-12 T. Richards pole #71269 N/C Underground refer to wo#1042382 Ddot refers | High Pressure Sodium | 38.89826963000 | -76.92624974000
2/26/12 | 1079101 | 900 | HALF ST | SE | 2/28/12 | 67434 | 6U343 | (Light out) | DA 2-28-12 @ 1105pm T. Richards repaired pole #67434 | High Pressure Sodium | 38.87873279000 | -77.00752418000
2/26/12 | 1079094 | 719 | 15TH ST | SE | 2/29/12 | 64363DC | 6A053 | (Light out) | 2-29-12 AL Young - completed - installed TLPC & 189 inc bulb (VW) DA 2-29-12 @ 100am T. Richards car still blocking accesss request for ladder DA 2-28-12 @ 325am could not access light due to car blocking pole | Incandescent | 38.88032991000 | -76.98412324000
2/23/12 | 1079018 | 5034 | NANNIE HELEN BURROUGHS AVE | NE | 2/24/12 | 71277 | 7A209 | (Light out) | 2-24-12 AL Young/Bunky - installed 400w hps bulb & pc - complete (VW) | High Pressure Sodium | 38.89827977000 | -76.92883394000
2/23/12 | 1079017 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 2/24/12 | 71294DC | 7A226 | (Light off/on) | 2-24-12 AL Young/Bunky - found ok- complete (VW) | High Pressure Sodium | 38.89882951000 | -76.93342319000
2/23/12 | 1079013 | 721 | ANACOSTIA AVE | NE | 3/1/12 | 72360DC | 7A483 | (Light off/on) | WBlack-TBuige-2-28-12-QC'd light is on DA 2-27-12 @ 405am T. Richards repaired pole #72360dc | High Pressure Sodium | 38.90238024000 | -76.95004900000
2/23/12 | 1078981 | 0 | BENNING RD | NE | 4/19/12 | 59614DC | 5M314DC | (Light off/on) | DA 3-7-12 @ 950pm C ,ashton adjusted TLPC light is on and working DA 2-27-12 @ 405am C. ashton pole #59614dc light is on and working previously repaired | High Pressure Sodium | 38.89848007000 | -76.97326349000
2/23/12 | 1078980 | 0 | BENNING RD | NE | 3/8/12 | 59613DC | 5M316DC | (Light off/on) | DA 3-7-12 @ 955pm C .aShton installed 250 lamp light is now on and working DA 2-27-12 @ 412am C. ashton pole #59613dc light is on and working installed pole id | High Pressure Sodium | 38.89856872000 | -76.97375901000
2/21/12 | 1078770 | 700 | MICHIGAN AVE | NE | 2/29/12 | 53648DC | 5U716 | (Light out) | WBlack-CFreeburger-2-28-12-QC'd light is on DA 2-22-12 @ 210am C .aShton repaired pole #53648dc | High Pressure Sodium | 38.93266695000 | -76.99717259000
2/20/12 | 1078684 | 3503 | B ST | SE | 2/22/12 | 76531 | 76531DC | (Light out) | Darell Dixon reported light was serviced on 2/21/12(KW) | High Pressure Sodium | 38.88720208000 | -76.95585811000
2/17/12 | 1078617 | 1338 | W ST | NW | 2/22/12 | 12065 | 1G572 | (Light out) | DA 2-22-12 @ 340am K Dunton repaired pole #12065 | High Pressure Sodium | 38.91924307000 | -77.03106855000
2/17/12 | 1078608 | 0000 | H ST | NE | 2/17/12 | 68242DC | 68242 | (Light out) | DA 2-16-12 @ 1140pm T .Richards repaired pole #68242dc | High Pressure Sodium | 38.90009857000 | -77.00808944000
2/15/12 | 1078484 | 1400 | SHIPPEN LN | SE | 2/17/12 | 81761 | 88038 | (Light out) | DA 2-17-12 @ 1205am K Simmons repaired pole #81761 | High Pressure Sodium | 38.84927406000 | -76.98311956000
2/14/12 | 1078341 | 777 | NORTH CAPITOL ST | NE | 3/14/12 | 68241DC | 68241 | (Light out) | DA 2-16-12 @ 1130pm T. Richards pole #68241dc N?C Underground - bare neturial needs to be repulled DA 2-16-12 T. Richards pole #68241dc needs big boom | High Pressure Sodium | 38.90010486000 | -77.00885876000
2/14/12 | 1078340 | 0000 | H ST | NE | 2/17/12 | 68255DC | 68255 | (Light out) | DA 2-16-12 @ 1110pm T. Richards repaired pole #68255dc DA 2-16-12 T. Richards pole #68255dc needs big boom | High Pressure Sodium | 38.90037863000 | -77.00528191000
2/14/12 | 1078339 | 0 | H ST | NE | 2/17/12 | 68250DC | 68520 | (Light out) | DA 2-16-12 T .Richards repaired pole #68250dc DA 2-16-12 T. Richards pole #68250dc needs big boom | High Pressure Sodium | 38.87458286000 | -77.00571187000
2/14/12 | 1078338 | 0 | H ST | NE | 3/5/12 | 68249DC | 68249 | (Light out) | DA 3-5-12 @ 135am T Richards pole #68249dc light is on and working 02-15-12 D. Dixon Voltage read 122v. @ fixture. Problem was burnt @ terminal strip where hot wire was connected (WP)DAD 2-16-12 T. Richards pole #68249dc NC to overhead open neturial 5 | High Pressure Sodium | 38.90004036000 | -77.00401332000
2/14/12 | 1078337 | 0000 | H ST | NE | 2/17/12 | 68248DC | 68248 | (Light out) | DA 2-16-12 @ 1150pm T. Richards repaired pole #68248dc DA 2-16-12 T. Richards pole #68248dc needs big boom | High Pressure Sodium | 38.90004513000 | -77.00446924000
2/12/12 | 1078103 | 700 | MICHIGAN AVE | NE | 2/14/12 | 53648DC | 5U716 | (Light out) | DA 2-13-12 @ 1135pm C. aShton repaired pole #53648dc | High Pressure Sodium | 38.93266695000 | -76.99717259000
2/10/12 | 1078030 | 2902 | BLADENSBURG RD | NE | 2/10/12 | 51236DC | 5A132DC | (Light out) | DA2-10-12 @ 125am K .Simmons repaired pole #51236dc and installed pole tag | High Pressure Sodium | 38.92743073000 | -76.96259421000
2/8/12 | 1077903 | 0 | INTERSTATE 395 | NW | 2/8/12 | 395-005N-4 | 395N234 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.87624339000 | -77.04138535000
2/8/12 | 1077888 | 0 | OVERLOOK AVE | SE | 2/14/12 | 81816 | 88089 | (Light out) | DA 2-14-12 @ 315am C .aShton pole #81816 light is on and working | High Pressure Sodium | 38.83181785000 | -77.01472372000
2/8/12 | 1077885 | 0 | RHODE ISLAND AVE | NE | 2/14/12 | 50104 | 56340 | (Light out) | DA 2-13-12 @ 1012pm B Brown repaired pole #50104 | High Pressure Sodium | 38.91934333000 | -77.00215180000
2/8/12 | 1077871 | 1025 | CONNECTICUT AVE | NW | 2/9/12 | 27214 | 2G832 | (Light out) | DA 2-8-12 @ 1135pm C .ashton repaired pole #27214 | High Pressure Sodium | 38.90319443000 | -77.03951645000
2/8/12 | 1077860 | 0 | INTERSTATE 395 | SW | 2/8/12 | 395-006S-6 | 395S233 | (Overhead guide sign light out) | I.Paraway repaired light - 2/8/12 | Mercury Vapor | 38.87915645000 | -77.03882245000
2/6/12 | 1077703 | 0 | 9TH ST | NW | 2/7/12 | 22543 | 2G978 | (Light out) | DA 2-7-12 @ 1240am C> ashton repaired pole #22543 | High Pressure Sodium | 38.89968310000 | -77.02386058000
2/5/12 | 1077647 | 0000 | DAVENPORT ST | NW | 2/6/12 | 30009DC | 3A246DC | (Light out) | DA 2-6-12 @ 340am K .Dunton pole #30009dc light is on and working previously repaired | Mercury Vapor | 38.95206814000 | -77.08071551000
2/5/12 | 1077614 | 1435 | MONROE ST | NE | 2/6/12 | 51218DC | 5A108DC | (Light out) | DA 2-6-12 @ 225am K .Simmons pole #51218dc light is on and working previously repaired | High Pressure Sodium | 38.93280994000 | -76.98477119000
2/2/12 | 1077543 | 2328 | 36TH ST | SE | 2/3/12 | 74819DC | 7A083DC | (Light out) | DA 2-3-12 @ 100am T. Richards repaired pole #74819dc | High Pressure Sodium | 38.86055239000 | -76.95626725000
2/2/12 | 1077536 | 0 | N ST | NW | 2/5/12 | 25583 | 6A791 | (Light out) | DA 2-5-12 @ 1035pm C Ashton repaired pole #25583 | High Pressure Sodium | 38.90719742000 | -77.02175566000
2/2/12 | 1077535 | 418 | NEW YORK AVE | NW | 2/3/12 | 60063 | 6A172 | (Light out) | DA 2-2-12 @ 1055pm T .Richards repaired pole #60063 | High Pressure Sodium | 38.90441345000 | -77.01718759000
2/2/12 | 1077494 | 1730 | 7TH ST | NW | 2/2/12 | 25649 | 6A840 | (Light out) | DA 2-2-12 @ 1010pm C .aShton repaired pole #25649 | High Pressure Sodium | 38.91354322000 | -77.02201499000
2/1/12 | 1077418 | 1357 | U ST | NW | 3/15/12 | 11720 | 1G519 | (Light out) | DA 3-15-12 K. Dunton ;ight is on and working 3-12-12 AL Young/Fike - completed - cleaned mh pumped out water removed burned out concentric - instlled 30' #10 cable and spliced in mh and base of pole (VW) 3-12-12 AL Johnson/G Smith - completed - insta | High Pressure Sodium | 38.91709765000 | -77.03113418000
1/31/12 | 1077311 | 1730 | 7TH ST | NW | 2/1/12 | 25649 | 6A840 | (Light out) | Light is on - Ronald Walton 2/1/12 | High Pressure Sodium | 38.91354322000 | -77.02201499000
1/31/12 | 1077275 | 2420 | WISCONSIN AVE | NW | 2/1/12 | 30147 | 3G067 | (Light out) | DA 2-1-12 @ 305am K Dunton repaired pole #30147 | High Pressure Sodium | 38.92145383000 | -77.07236458000
1/29/12 | 1077084 | 4514 | 13TH ST | NW | 1/31/12 | 4K422 | 4U131 | (Light out) | DA 1-31-12 @ 202am B .Brown repaired pole #4k422 | High Pressure Sodium | 38.94571765000 | -77.02978404000
1/27/12 | 1077019 | 0000 | DAVENPORT ST | NW | 1/31/12 | 30009DC | 3A246DC | (Light out) | DA 1-31-12 @ 1215am K .Dunton repaired pole #30009dc 12-00023141-across from the above address cwDesc: STREETLIGHT REPAIR | Mercury Vapor | 38.95206814000 | -77.08071551000
| 1076964 | 0 | BANGOR ST | SE | 1/31/12 | 74835DC | 7A098DC | (Light out) | DA 1-31-12 @ 400am T .Richards repaired pole #74835dc On NW Side of Bangor at 32nd St SE 12-00022055- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86055249000 | -76.96177449000
1/25/12 | 1076834 | 801 | D ST | NW | 1/26/12 | 60176 | 2M330 | (Light out) | DA 1-25-12 @ 1055pm K. Simmons repaired pole #60176 | High Pressure Sodium | 38.89474698000 | -77.02312090000
1/25/12 | 1076794 | 0 | INGRAHAM ST | NW | 1/26/12 | 4M357 | 4M358 | (Light out) | DA 1-25-12 @ 1130pm B. Brown repaired pole #4M357 | High Pressure Sodium | 38.95408720000 | -77.02592523000
1/24/12 | 1076633 | 711 | ANACOSTIA AVE | NE | 2/2/12 | 72358DC | 7A481 | (Light off/on) | DA 1-30-12 @ 1230am T >Richards repaired pole #72358dc | High Pressure Sodium | 38.90197539000 | -76.95056600000
1/24/12 | 1076632 | 711 | ANACOSTIA AVE | NE | 1/24/12 | 72358DC | 7A481 | (Light out) |  | High Pressure Sodium | 38.90197539000 | -76.95056600000
1/23/12 | 1076572 | 0 | 23RD ST | NW | 1/27/12 | 28317 | 2M272 | (Light out) | DA 1-27-12 C.Ashton repaired pole #28317 | High Pressure Sodium | 38.89349221000 | -77.05025102000
1/23/12 | 1076521 | 0 | R ST | NW | 1/26/12 | 25645 | 6A831 | (Light out) | DA -26-12 @ 435am C.Ashton repaired pole #25645 | High Pressure Sodium | 38.91269915000 | -77.02207113000
1/23/12 | 1076448 | 1000 | 1ST ST | NW | 1/27/12 | 61105 | 6A232 | (Light out) | DA 1-27-12 @ 150am T .Richards reattached fixture pole #61105 | High Pressure Sodium | 38.90337658000 | -77.01210139000
1/23/12 | 1076445 | 777 | NORTH CAPITOL ST | NE | 2/1/12 | 68241DC | 68241 | (Light out) | WBlack-CFreeburger-1-30-12-QC'd and light is on DA 1-25-12 @ 320am T. Richards pole 368241dc light is on and working - need big boom | High Pressure Sodium | 38.90010486000 | -77.00885876000
1/19/12 | 1076303 | 0 | SEDGWICK ST | NW | 1/25/12 | 30008DC | 3A368DC | (Light out) | DA 1-25-12 @ 135am K .Dunton repaired pole #30008dc | Incandescent | 38.94040143000 | -77.09254074000
1/18/12 | 1076187 | 0 | ANACOSTIA FWY | SE |  | 79480 | 7A144 | (Light out) | DA 1-24-12 @ 345am T ,Richards pole #79480 needs MOT | High Pressure Sodium | 38.88580800000 | -76.96248765000
1/18/12 | 1076186 | 0 | ANACOSTIA FWY | SE |  | 79479 | 7A143 | (Light out) | DA 1-24-12 @ 345am T ,Richards pole #79479 needs MOT | High Pressure Sodium | 38.88513632000 | -76.96276237000
1/18/12 | 1076112 | 2206 | 18TH ST | NW | 1/24/12 | 11411 | 1G502 | (Light out) | DA 1-19-12 @ 310am C.ashton pole #11411 - located behind constrution area 3rd party contractor | High Pressure Sodium | 38.91905896000 | -77.04152631000
1/17/12 | 1075932 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 1/17/12 | 71294DC | 7A226 | (Light out) | DA 1-16-12 @ 1140pm T Richards repaired pole #71294dc | High Pressure Sodium | 38.89882951000 | -76.93342319000
1/16/12 | 1075930 | 1500 | KEARNEY ST | NE | 1/27/12 | 59986 | 5A177 | (Light out) | 1-20-12 Darryl/Chris - pulled wire from MH to MH - 150' # 10 wire 2-#8 cbs 2- #2 c-clamps (VW) DA 1-16-12 @ 1130pm K. Simmons pole #59986 N/C underground18Jan 12. 19Jan 12 Needs MOT(WP) | High Pressure Sodium | 38.91401980000 | -77.01759054000
1/16/12 | 1075914 | 0 | NEW YORK AVE | NE | 1/18/12 | 50001 | 5A035 | (Light out) | DA 1-18-12 K .Simmons pole #50001 ned MOT and Big Boom | High Pressure Sodium | 38.91733557000 | -76.97140198000
1/16/12 | 1075902 | 18 | 3RD ST | SE | 1/19/12 | 6A003 | 6A003 | (Light out) | DA 1-19-12 @ 345am T Richards repaired pole #6A003 | Incandescent | 38.87723028000 | -77.00452085000
1/16/12 | 1075881 | 1300 | 11TH ST | SE | 1/20/12 | 67735 | 6L924 | (Light out) | DA 1-20-12 @ 245am T. Richards repaired pole #67735 (shorting cap) 1-19-12 AL Young - new fixture already installed (VW) | High Pressure Sodium | 38.87450805000 | -76.99165530000
1/16/12 | 1075879 | 1200 | 11TH ST | SE | 1/19/12 | 67740 | 6L938 | (Light out) | DA 1-19-12 @ 520am T. Richards pole #67740 light is on and woorking | High Pressure Sodium | 38.87633690000 | -76.99165150000
1/12/12 | 1075717 | 0 | WISCONSIN AVE | NW | 1/26/12 | 30135 | 3G009 | (Light off/on) | DA 1-20-12 @ 525am K Dunton repaired pole #30135 | High Pressure Sodium | 38.92744531000 | -77.07330577000
1/12/12 | 1075716 | 2418 | 18TH ST | NW | 1/18/12 | 11531 | 1G485 | (Light out) | DA 1-18-12 @ 320am C> AShton pole #11531 light was on upon arrival new bulb, fiture and wiring and voltage looks good | High Pressure Sodium | 38.92129769000 | -77.04231632000
1/11/12 | 1075677 | 400 | RHODE ISLAND AVE | NW | 1/26/12 | 59987 | 5A178 | (Light out) | 1-20-12 Darryl/Chris - pulled wire from MH to MH - 150' # 10 wire 2-#8 cbs 2- #2 c-clamps (VW) DA 1-16-12 @ 1115pm K .Simmons pole #59987 N/C underground | High Pressure Sodium | 38.91400893000 | -77.01743154000
1/11/12 | 1075658 | 1416 | BELMONT ST | NW | 1/12/12 | 12051 | 1A043 | (Light out) | DA 1-12-12 @ 1155pm C .Ashton repaired pole #12051 | High Pressure Sodium | 38.92062514000 | -77.03244172000
1/11/12 | 1075657 | 941 | T ST | NW | 1/12/12 | 13449 | 1L366 | (Light out) | DA 1-12-12 @ 150am C .ashton repaired pole #13449 | High Pressure Sodium | 38.91563302000 | -77.02547606000
1/11/12 | 1075655 | 600 | S ST | NW | 3/14/12 | 14129 | 1G581 | (Light out) | 3-14-12 J Lancaster - installed 220' #10 cable & 10' # 4 conduit (VW) 1-19-12 Darryl/Chris - heavy construction around light - appear to have a breakdown between MH & PBr efer to construction (VW) DA 1-12-12 @ 1040pm C .aShton pole #14129 N/C underg | High Pressure Sodium | 38.91414861000 | -77.02137785000
1/11/12 | 1075593 | 2828 | WISCONSIN AVE | NW | 1/11/12 | 30136 | 3G013 | (Light out) | DA 1-11-12 @ 410am K .Dunton repaired pole #30136 | High Pressure Sodium | 38.92695687000 | -77.07330485000
1/9/12 | 1075408 | 2400 | K ST | NW | 1/12/12 | 24648 | 2G665 | (Light out) | DA 1-12-12 @ 235am C .AShton repaired pole #24648 DA 1-10-12 Needs 400 powerdoor/ waiting on materials | High Pressure Sodium | 38.90268752000 | -77.05153812000
1/9/12 | 1075365 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 1/17/12 | 71295DC | 7A227 | (Light out) | DA 1-17-12 @ 1210am T, Richards repaired pole #71295dc | High Pressure Sodium | 38.89887350000 | -76.93373005000
1/8/12 | 1075317 | 600 | MICHIGAN AVE | NE | 1/8/12 | 53646DC | 5U708 | (Light out) |  | High Pressure Sodium | 38.93303755000 | -76.99623620000
1/8/12 | 1075296 | 1140 | CONNECTICUT AVE | NW | 1/12/12 | 24535 | 2U549 | (Light out) | DA 1-12-12 @ 220am C .ashton repaired pole #24535 DA 1-10-12 @ 210am C .Ahton pole #24535 Needs 400 powerdoor | High Pressure Sodium | 38.90503939000 | -77.04092719000
1/8/12 | 1075268 | 4930 | NANNIE HELEN BURROUGHS AVE | NE | 1/23/12 | 71279DC | 7A213 | (Light out) | DA 1-23-12 @ 205am K .Simmons repasired pole #781279dc DA 1-10-12 Needs 400pd / waiting on materials | High Pressure Sodium | 38.89845445000 | -76.92986688000
1/5/12 | 1075184 | 3310 | 15TH ST | NE | 1/9/12 | 51221DC | 5A117DC | (Light out) | DA 1-09-12 @ 1227am K. Simmons repaired pole #51221dc twin pole right side 12-00003435- cwDesc: STREETLIGHT REPAIR | Incandescent | 38.93137950000 | -76.98438250000
1/5/12 | 1075142 | 3310 | 15TH ST | NE | 1/9/12 | 51221DC | 5A117DC | (Light out) | DA 1-09-12 @ 1227am K. Simmons repaired pole #51221dc twin pole left side | Incandescent | 38.93137950000 | -76.98438250000
1/5/12 | 1075136 | 2800 | BLADENSBURG RD | NE | 1/8/12 | 51241DC | 5A137DC | (Light out) | DA 1-08-12 @ 1030pm K. Simmons repaired pole #51241dc | High Pressure Sodium | 38.92590222000 | -76.96446844000
1/5/12 | 1075049 | 3008 | SHERMAN AVE | NW | 1/8/12 | 12818 | 1G417 | (Light out) | DA 1-08-12 @ 1010pm C. Ashton repaired pole #12818 12-00002463- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92802282000 | -77.02621999000
1/4/12 | 1074900 | 777 | NORTH CAPITOL ST | NE | 1/4/12 | 68241DC | 68241 | (Light out) | DA 1-04-12 @ 1256am T. Richards repaired pole #68241dc | High Pressure Sodium | 38.90010486000 | -77.00885876000
1/4/12 | 1074899 | 0000 | H ST | NE | 1/4/12 | 68245DC | 68245 | (Light out) | DA 1-04-12 @ 1256am T .Richards repaired pole #68245dc | High Pressure Sodium | 38.90004161000 | -77.00602574000
1/3/12 | 1074858 | 901 | 9TH ST | NW | 1/6/12 | 22987 | 2G988 | (Light out) | DA 1-05-12 @ 1110pm C. AShton repaired pole #22987 disconnected christams lights in front of photocell | High Pressure Sodium | 38.90092176000 | -77.02415354000
1/3/12 | 1074804 | 0000 | H ST | NE | 1/4/12 | 68243DC | 68243 | (Light out) | DA 1-04-12 @ 1256am T> Richards repaired pole #68243dc DA 1-03-12 @ 420am T> Richards pole #68243dc need big boom | High Pressure Sodium | 38.90008908000 | -77.00731064000
12/30/11 | 1074709 | 650 | MASSACHUSETTS AVE | NW | 1/9/12 | 22465 | 6A979 | (Light out) | 1-9-2012 WMAYNARD QC'D LIGHT IS ON 1-3-12 Darryl/Chris - pulled cable from tb to mh - installed 60' #10 wire 4- #8 copper butt splices & tape(VW) DA 12-30-11 @ 230am CaShton pole #22465 light had voltage on neutrial upon aarival - bare neutrial refer | High Pressure Sodium | 38.90204075000 | -77.02130668000
12/30/11 | 1074705 | 0 | 7TH ST | NW | 12/30/11 | 22409 | 6M688 | (Light out) | DA 12-30-11 @ 220am C. ashton repaired pole #22409 removed ddot tape | High Pressure Sodium | 38.90199325000 | -77.02201951000
12/30/11 | 1074703 | 0 | NEW YORK AVE | NW | 12/30/11 | 22911 | 2L053 | (Light out) | DA 12-30-11 @ 145am C. ashton repaired pole #22911 twin light right side | High Pressure Sodium | 38.90141042000 | -77.02582476000
12/28/11 | 1074603 | 0 | NEW YORK AVE | NW | 1/3/12 | 22947 | 2L030 | (Light off/on) | WBlack-1-2-12- same as WO#1074482 light is still on | High Pressure Sodium | 38.90115976000 | -77.02723326000
12/28/11 | 1074602 | 0 | NEW YORK AVE | NW | 12/30/11 | 22911 | 2L053 | (Light out) | DA 12-30-11 @ 145am C.ashton repaired pole #22911 twin light left side | High Pressure Sodium | 38.90141042000 | -77.02582476000
12/28/11 | 1074601 | 0 | NEW YORK AVE | NW | 1/2/12 | 22914 | 2L029 | (Light out) | DA 1-02-12 @ 1010pm C .aShton repaired pole #22914 Twin light left side | High Pressure Sodium | 38.90105629000 | -77.02684066000
12/28/11 | 1074597 | 0 | NEW YORK AVE | NW |  | 22947 | 2L030 | (Light off/on) |  | High Pressure Sodium | 38.90115976000 | -77.02723326000
12/28/11 | 1074487 | 7051 | SPRING PL | NW | 12/29/11 | 4H523DC | 4H523 | (Light out) | DA 12-28-11 @ 1138pm B Brown repaired pole #4h523dc Alley 11-00396483-The streetlight that is out is located on Spring Place NW, directly behind the Gables Apartment Building (7035 Blair Road NW). The ID number is 4H523DC cwDesc: STREETLIGHT REPAIR | Incandescent | 38.97594098000 | -77.01865986000
12/28/11 | 1074482 | 0 | NEW YORK AVE | NW | 12/28/11 | 22947 | 2L030 | (Light out) | DA 12-28-11 @ 400am C .AShton repaired pole #22947 | High Pressure Sodium | 38.90115976000 | -77.02723326000
12/27/11 | 1074456 | 1225 | 18TH ST | NW | 12/29/11 | 26763 | 2U514 | (No current) | D. Dixon completed on 11-29-11. Installed 40FT no#10 and made splices. | High Pressure Sodium | 38.90700407000 | -77.04161752000
12/27/11 | 1074440 | 4502 | NANNIE HELEN BURROUGHS AVE | NE | 12/29/11 | 71304DC | 7A241 | (Light off/on) | DA 12-29-11 @ 1225am T. Richards repaired pole #71304dc | High Pressure Sodium | 38.89991666000 | -76.93777979000
12/27/11 | 1074424 | 4406 | NANNIE HELEN BURROUGHS AVE | NE | 12/29/11 | 71307DC | 7A242 | (Light out) | DA 12-29-11 @ 1215am T> Richards repaired pole #71307dc | High Pressure Sodium | 38.90023779000 | -76.93819749000
12/27/11 | 1074366 | 432 | K ST | NW | 12/28/11 | 60466 | 6A124 | (Light out) | DA 12-28-11 @ 1215am C. aShton repaired pole #60466 | High Pressure Sodium | 38.90245237000 | -77.01710005000
12/22/11 | 1074288 | 1000 | NEW YORK AVE | NW | 4/16/12 | 22948 | 2L032 | (Light out) | 1-6-12 Darryl/Chris - REFER to DDOt traffic pole w/common duct (VW) Da 12-28-11 @ 350am C .aShton pole #22948 new wire has been pulled new fixture and bulbs everything above ground is good refer to fault crew to check for underground problems | High Pressure Sodium | 38.90132896000 | -77.02684244000
12/21/11 | 1074189 | 0 | NEW YORK AVE | NE | 12/21/11 | 50001 | 5A035 | (Light out) | WBlack-will setup for next MOT | High Pressure Sodium | 38.91733557000 | -76.97140198000
12/20/11 | 1074121 | 301 | 4TH ST | SW | 1/9/12 | 21580 | 6L636 | (Light off/on) | 1-9-2012 WMAYNARD QC'D LIGHT IS ON DA 12-22-11 @ 1025pm C .ashton repaired pole #21580 | High Pressure Sodium | 38.88593815000 | -77.01743975000
12/20/11 | 1074120 | 931 | 7TH ST | NW | 12/22/11 | 22458 | 6M673 | (Light out) | DA 12-21-11 @ 1125pm C .ashton repaired pole #22458 repulled old wire | High Pressure Sodium | 38.90144435000 | -77.02181926000
12/20/11 | 1074084 | 1601 | 18TH ST | NW | 4/16/12 | 26773 | 2M145 | (Light out) | H.Lancaster on 4-6-10 Traffic and SL share the same conduit. DA 12-23-11 @ 135am C .AShton repaired pole #26773 DA 12-21-11 @ 1250am C .ashton pole #26773 teardrop fixture removed and took to shop for repairs reading 120volts | High Pressure Sodium | 38.91132223000 | -77.04173550000
12/20/11 | 1074080 | 0 | INTERSTATE 695 | SE | 12/22/11 | 695-003W-5 | 695E612 | (Overhead guide sign light out) | Reset Breakers | High Pressure Sodium | 38.88055777000 | -77.00245051000
12/20/11 | 1074079 | 0 | INTERSTATE 695 | SE | 12/22/11 | 695-001W-9 | 695W613 | (Overhead guide sign light out) | Reset Breaker | High Pressure Sodium | 38.88110666000 | -77.00656804000
12/20/11 | 1074077 | 0 | 9TH ST | SW |  | 395-041S-3 | 09SS607 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88325163000 | -77.02403832000
12/20/11 | 1074076 | 0000 | INTERSTATE 395 | SW | 12/21/11 | 395-029N-4 | 12XN601 | (Overhead guide sign light out) | Checked and lights are on. 12/20/11 @ 3:22 pm | High Pressure Sodium | 38.88338049000 | -77.02687753000
12/20/11 | 1074052 | 2400 | 14TH ST | NW | 12/21/11 | 12048 | 1A046 | (Light out) | DA 12-21-11 @ 335am C .aShton taped wires pole #12048 | High Pressure Sodium | 38.92087041000 | -77.03196022000
12/20/11 | 1074041 | 0000 | SUITLAND PKY | SE | 12/20/11 | 83281 | 82381 | (Light out) | mistake | High Pressure Sodium | 38.86351812000 | -77.00055997000
12/20/11 | 1074029 | 0 | NEW YORK AVE | NE | 12/20/11 | 50005 | 5A039 | (Light out) | DA 12-19-11 @ 1030pm T. Richards repaired pole #50005 | High Pressure Sodium | 38.91734425000 | -76.96859446000
12/19/11 | 1074018 | 0 | KENILWORTH AVE | SE | 12/20/11 | 79496 | 7A149 | (Light out) | DA 12-20-11 @ 1210am T .Richards repaired pole #79496 | High Pressure Sodium | 38.88522570000 | -76.96311007000
12/19/11 | 1073992 | 4651 | BENNING RD | SE | 12/22/11 | 75822 | 75822DC | (Light out) |  | High Pressure Sodium | 38.87611644000 | -76.93130301000
12/18/11 | 1073815 | 5109 | NANNIE HELEN BURROUGHS AVE | NE |  | 71270 | 71270DC | (Light out) |  | High Pressure Sodium | 38.89827347000 | -76.92679095000
12/18/11 | 1073814 | 4502 | NANNIE HELEN BURROUGHS AVE | NE | 12/20/11 | 71304DC | 7A241 | (Light out) | DA 12-20-11 @ 250am B Brown repaired pole #71304dc DA 12-19-11 @ 228am B .Brown pole #71304dc need 400 powerdoor | High Pressure Sodium | 38.89991666000 | -76.93777979000
12/15/11 | 1073680 | 0 | V ST | NW | 12/15/11 | 14234 | 1U032 | (Light out) | DA 12-15-11 @ 345am C .Ahton repaired pole #14234 | High Pressure Sodium | 38.91785794000 | -77.02308568000
12/14/11 | 1073595 | 2700 | WISCONSIN AVE | NW | 12/14/11 | 30140 | 3G033 | (Light out) | DA 12-14-11 @ 1205am K .Dunton repaired pole #30140 | High Pressure Sodium | 38.92473706000 | -77.07330419000
12/13/11 | 1073498 | 3033 | BLADENSBURG RD | NE | 12/14/11 | 58720DC | 5A172DC | (Light out) | DA 12-14-11 @ 1247am K. Simmons repaired pole #58720dc | Incandescent | 38.92960546000 | -76.95868010000
12/12/11 | 1073463 | 0 | EAST CAPITOL ST | NE | 12/13/11 | 63634 | 6M824 | (Light out) | DA 12-12-11 @ 1010pm T. Richards repaired pole #63634 twin pole | High Pressure Sodium | 38.89007149000 | -76.97454092000
12/12/11 | 1073420 | 3028 | BLADENSBURG RD | NE | 12/13/11 | 51232DC | 5A128DC | (Light out) | dS 12-13-11 @ 415am K. Simmons repaired pole #51232dc | High Pressure Sodium | 38.92838717000 | -76.96142018000
12/12/11 | 1073405 | 3700 | MILITARY RD | NW | 12/13/11 | 32716DC | 3E023 | (Light out) | Damien Smith completed on 12-13-11. Made splices on the secondary. DA 12-13-11 @ 1225am K. Dunton pole #32716dc N/C To Overhead | High Pressure Sodium | 38.96062593000 | -77.07197706000
12/11/11 | 1073379 | 0000 | 22ND ST | SE | 12/11/11 | 68335 | 6M814 | (Light out) | DA 12-11-11 @ 1025pm T .Richards repaired pole #68335 | High Pressure Sodium | 38.88810813000 | -76.97400907000
12/11/11 | 1073360 | 6950 | MAPLE ST | NW | 12/22/11 | 4H590DC | 4L605 | (Light off/on) | DA 12-22-11 Wesley light is on and working DA 12-13-11 @ 524am B .Brown repaired pole #4h590dc | High Pressure Sodium | 38.97397272000 | -77.01544302000
12/11/11 | 1073322 | 3150 | PENNSYLVANIA AVE | SE |  | 78553DC | 7E102DC | (Light out) | DA 12-13-11 @ 220pm T. Richards pole #78553dc more than a simple light repair refer to Ddot | High Pressure Sodium | 38.86970517000 | -76.96157266000
12/11/11 | 1073319 | 3945 | PENNSYLVANIA AVE | SE | 12/15/11 | 78518DC | 7E149DC | (Light out) | DA 12-15-11 @ 130am T. Richards repaired pole #78518dc redirected photocell | High Pressure Sodium | 38.86392263000 | -76.94743025000
12/11/11 | 1073309 | 0 | EAST CAPITOL ST | NE | 12/13/11 | 63634 | 6M824 | (Light out) | DA 12-12-11 @ 1010pm T. Richards repaired pole #63634 | High Pressure Sodium | 38.89007149000 | -76.97454092000
| 1073275 | 806 | 7TH ST | NW | 12/15/11 | 22423 | 6M660 | (Light out) | DA 12-15-11 @ 1100pm C .Ashton repaired pole #22423 tightened wires 11-00380476-The Chinese style streetlight poles are out at night (After 8pm). cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90012937000 | -77.02201557000
12/9/11 | 1073264 | 1731 | 7TH ST | NW | 12/12/11 | 25708 | 6A842 | (Light out) | See w.o.1072520 --12-8-11 Hudson/Tom - check pole base, tried routing duct but, there is a break pulled out concentrc wire REFER to construction (VW) See w.o. 1069349 10-31-11 Darryl/Chris - tractor trailer blocking MH - cannot access will return next | High Pressure Sodium | 38.91370731000 | -77.02182415000
12/9/11 | 1073263 | 1718 | 7TH ST | NW | 12/12/11 | 25707 | 6A836 | (Light out) | DA 12-12-11 @ 1220am C. Ashton repaired pole #25707 | High Pressure Sodium | 38.91317833000 | -77.02182199000
12/9/11 | 1073259 | 0 | CONNECTICUT AVE | NW | 12/12/11 | 38584 | 3E026 | (Light out) | DA 12-12-11 @ 310am K. Dunton pole #38584 light is on and working 11-00380275-the metal streetlight is across the street from 4225 Connecticut Av NW, possible shortage blinking on and off cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.94397582000 | -77.06352631000
12/9/11 | 1073257 | 0 | M ST | NW | 12/16/11 | 23730 | 2U534 | (Light out) | DA 12-09-11 @ 1245am K .Dunton pole #23730 relocated TLPC away from lights | High Pressure Sodium | 38.90557436000 | -77.04154706000
12/6/11 | 1073125 | 1300 | 11TH ST | SE | 12/13/11 | 67735 | 6L924 | (Light out) | DA 12-12-11 @ 100am T. Richards converted pole #67735 from mv to hps cutoff (short cap) 12/13/11 Edwards Found OK (WP) | High Pressure Sodium | 38.87450805000 | -76.99165530000
12/4/11 | 1072907 | 0 | BENNING RD | NE | 12/22/11 | 59614DC | 5M314DC | (Light off/on) | CFREEBURGER QC'D LIGHT IS ON DA 12-11-11 @ 1105pm K. Simmons repaired pole #59614dc | High Pressure Sodium | 38.89848007000 | -76.97326349000
12/1/11 | 1072746 | 832 | UPSHUR ST | NW | 12/5/11 | 4J745 | 4G332 | (Light out) | DA 12-05-11 @ 39am B/ Brown repaired pole #4j745 | High Pressure Sodium | 38.94182944000 | -77.02466826000
12/1/11 | 1072705 | 715 | ANACOSTIA AVE | NE | 12/6/11 | 72359DC | 7A482 | (Light out) | DA 12-06-11 @ 220am T. Richards repaired pole #72359dc removed birds nest | High Pressure Sodium | 38.90218502000 | -76.95030078000
12/1/11 | 1072699 | 5800 | NANNIE HELEN BURROUGHS AVE | NE |  | 79661 | 72656 | (Light out) | DeVon Smith on 11-22-10 Refer to DDOT. Per Brenda Kenney on 11-17-10 in DDOT meeting, Severn is no longer reasonable for any streetlights on NANNIE HELEN BURROUGHS AVE. Fort Mayor are installing new lights from Eastern Ave to Minnesota Ave. DA 12-05-11 @ | High Pressure Sodium | 38.89830700000 | -76.91763472000
12/1/11 | 1072696 | 4918 | 49TH PL | NE | 12/2/11 | 71283DC | 7A215 | (Light out) | DA 12-02-11 @ 450am T, richards repaired pole #71283dc | High Pressure Sodium | 38.89857711000 | -76.93088757000
11/30/11 | 1072573 | 0 | RICHARDSON PL | NW | 11/30/11 | 59924 | 5A412 | (Light out) | DA 11-30-11 @ 1245am KSimmons closed open lens pole #59924 | High Pressure Sodium | 38.91306930000 | -77.01662788000
11/29/11 | 1072520 | 1731 | 7TH ST | NW | 2/7/12 | 25708 | 6A842 | (Light out) | DA 2-7-12 C .Ashton pole #25708 light is on and working J. Lancaster completed on 2-2-12. 4 hot links Installed 10FT of conduit ran 150FT of cable and made splices inside manhole. 12-8-11 Hudson/Tom - check pole base, tried routing duct but, there is | High Pressure Sodium | 38.91370731000 | -77.02182415000
11/28/11 | 1072281 | 1001 | NEW HAMPSHIRE AVE | NW | 12/1/11 | 23862 | 2G674 | (Light out) | DA 12-01-11 @ 1215am C. Ashton repaired pole #23862 | High Pressure Sodium | 38.90308383000 | -77.04974132000
11/28/11 | 1072276 | 3600 | P ST | NW | 11/29/11 | 21002 | 2G125 | (Light out) | DA 11-29-11 @ 340am C. ashton repaired pole #21002 | High Pressure Sodium | 38.90864453000 | -77.07059706000
11/27/11 | 1072186 | 0 | 7TH ST | NW | 11/28/11 | 22430 | 2A186 | (Light out) | DA 11-27-11 @ 1110pm C .aShton adjusted TLPC pole #22430 | High Pressure Sodium | 38.89710115000 | -77.02201609000
11/27/11 | 1072177 | 0 | H ST | NW | 11/28/11 | 22569 | 2M434 | (Light out) | DA 11-28-11 @ 1230am C.ashton repaired pole #22569 | High Pressure Sodium | 38.89973622000 | -77.02284281000
11/26/11 | 1072127 | 1731 | 7TH ST | NW | 12/1/11 | 25708 | 6A842 | (Light out) | See w.o. 1069349 10-31-11 Darryl/Chris - tractor trailer blocking MH - cannot access will return next day (VW) DA 11-30-11 @ 1010pm C. AShton pole #25708 N/C Underground 11-00368118- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91370731000 | -77.02182415000
11/26/11 | 1072117 | 3408 | 15TH ST | NE | 11/28/11 | 51212DC | 5A101DC | (Light out) | DA 11-28-11 @ 515am K. Simmons repaired pole #51212dc Alley 11-00367971-Light poles #5B006DC and 5212DC in alley and in front of resident are blown out and need to be replaced immediately. cwDesc: STREETLIGHT REPAIR | Incandescent | 38.93231561000 | -76.98445505000
11/22/11 | 1071995 | 2911 | RHODE ISLAND AVE | NE | 11/28/11 | 52505DC | 5A166DC | (Light out) | DA 11-28-11 @ 255am K. Simmons repaired pole #52505dc | High Pressure Sodium | 38.93345368000 | -76.96676649000
11/22/11 | 1071988 | 100 | 3RD ST | SE | 11/28/11 | 6A002 | 6A002 | (Light out) | DA 11-28-11 @ 210am T. Richards repaired pole #6A002 | Incandescent | 38.87703665000 | -77.00445216000
11/22/11 | 1071920 | 0 | BRANDYWINE ST | NW | 11/22/11 | 3A230DC | 3A230 | (Light out) | DA 11-21-11 @ 1045pm K .Dunton ran 30ft wire pole #3a230dc | High Pressure Sodium | 38.94974018000 | -77.08081828000
11/21/11 | 1071905 | 700 | 1ST ST | NE | 11/23/11 | 68284 | 6U596 | (Light out) | DA 11-23-11 @ 1245am T .Richards pole #68284 light is on and working na 11-00364385- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89900607000 | -77.00720264000
11/21/11 | 1071859 | 3101 | PENNSYLVANIA AVE | SE | 12/1/11 | 78557DC | 7E098DC | (Light off/on) | T. Buige light on 11-30-11 DA 11-22-11 @ 1226am K. Simmons adjusted TLPC pole #78557dc | High Pressure Sodium | 38.87018089000 | -76.96274548000
11/21/11 | 1071838 | 1211 | 7TH ST | NW | 11/21/11 | 25661 | 6A790 | (Light out) | DA 11-21-11 @ 1055pm C. Ashton repaired pole #25661 | High Pressure Sodium | 38.90712952000 | -77.02201691000
11/21/11 | 1071836 | 0 | NEW YORK AVE | NW | 11/23/11 | 22947 | 2L030 | (Light out) | DA 11-22-11 @ 1200am C. Ashton repaired pole #22947 | High Pressure Sodium | 38.90115976000 | -77.02723326000
11/21/11 | 1071742 | 3223 | SHERMAN AVE | NW | 11/21/11 | 12872 | 1L273 | (Light out) | DA 11-21-11 @ 1025pm C. Ashton repaired pole #12872 FRONT 11-00363343-POLE # 40 METAL POLE LIGHT HAS BEEN OUT SINCE SATURDAY 11-19-11 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93042323000 | -77.02636750000
11/20/11 | 1071615 | 3945 | PENNSYLVANIA AVE | SE |  | 78518DC | 7E149DC | (Light out) | DA 11-23-11 @ 1218am K .Simmons refer to Ddot light is in ft myers construction site | High Pressure Sodium | 38.86392263000 | -76.94743025000
11/20/11 | 1071614 | 1735 | PENNSYLVANIA AVE | SE |  | 78542DC | 7E117DC | (Light out) | DA 11-23-11 @ 1210am K .Simmons refer to Ddot in ft myers construction area | High Pressure Sodium | 38.86796881000 | -76.95734397000
11/18/11 | 1071580 | 0 | BRANDYWINE ST | NW | 11/21/11 | 3A230DC | 3A230 | (Light out) | DA 11-21-11 @ 420am K. dunton repaired pole #3a230dc | High Pressure Sodium | 38.94974018000 | -77.08081828000
11/17/11 | 1071526 | 2902 | BLADENSBURG RD | NE | 11/17/11 | 50099 | 5A085 | (Light out) | DA 11-17-11 @ 1057pm K .Simmons pole #50099 @ this location id on checked aand working - duplicate pole tag located at new york ave. going to check this location as well | High Pressure Sodium | 38.92725738000 | -76.96243723000
11/16/11 | 1071362 | 2400 | 14TH ST | NW | 11/18/11 | 12048 | 1A046 | (Light out) | DA 11-18-11 @ 130am C. AShton repaired pole #12048 | High Pressure Sodium | 38.92087041000 | -77.03196022000
11/16/11 | 1071352 | 700 | 1ST ST | NE | 11/17/11 | 68284 | 6U596 | (Light out) | DA 11-17-11 @ 145am T. Richards repaired pole #68284 | High Pressure Sodium | 38.89900607000 | -77.00720264000
11/16/11 | 1071328 | 5350 | CALL PL | SE | 11/16/11 | 75597 | 75597DC | (Light out) | DA 11-16-11 @ 135am T Richards repaired pole #75597 | Incandescent | 38.88403430000 | -76.92511243000
11/14/11 | 1071208 | 1835 | WILTBERGER ST | NW | 1/24/12 | 29508 | 1M012 | (Light out) | DA 11-15-11 @ 400am C. Ashton pole is behind construction fence unable to reach light | High Pressure Sodium | 38.91528456000 | -77.02091849000
11/14/11 | 1071187 | 5322 | ASTOR PL | SE | 11/16/11 | 75569 | 75569DC | (Light out) | DA 11-16-11 @ 1255am T. Richards repaired pole #75569 | High Pressure Sodium | 38.88655037000 | -76.92533812000
11/14/11 | 1071127 | 807 | V ST | NW | 11/15/11 | 14237DC | 1U041 | (Light out) | DA 11-15-11 @ 100am C. sahton repaired pole #14237dc | Incandescent | 38.91856611000 | -77.02346139000
11/13/11 | 1071070 | 3817 | GEORGIA AVE | NW | 4/12/12 | 4J341 | 4G253 | (Light out) | DA 11-18-11 @ 1250am B. Brown refer to Ddot all new poles are being installed from 3500 Georgia ave/ Newton st to 4400 georgia ave/ allison st | High Pressure Sodium | 38.93827040000 | -77.02448591000
11/10/11 | 1070954 | 0 | RHODE ISLAND AVE | NW | 11/10/11 | 59997 | 5A189 | (Light out) | DA 11-10-11 @ 238am K. Simmons repaired pole #59997 | High Pressure Sodium | 38.91491231000 | -77.01415169000
11/9/11 | 1070929 | 1827 | WILTBERGER ST | NW | 1/24/12 | 29507 | 1M014 | (Light out) | 1-12-12 REFER to DDOT - construction crews has SEA Containers blocking access (VW) 11-16-11 Hudson/Tom - found hand tried routing from light and handbox, found 2 breaks in duct - REFER to construction (VW) 11-14-11 Hudson/Tom -unable to access MH due | High Pressure Sodium | 38.91496601000 | -77.02091840000
11/8/11 | 1070840 | 2902 | BLADENSBURG RD | NE |  | 50099 | 5A085 | (No current) | 11-8-11 Darryl/Chris - traffic combo pole w/common duct also, pole have camera on it REFER to DDOt (VW) | High Pressure Sodium | 38.92725738000 | -76.96243723000
11/8/11 | 1070781 | 1500 | SOUTH CAPITOL ST | SE | 11/10/11 | 67031 | 68527 | (Light out) | DA 11-10-11 @ 1235am T. Richards reaire pole #67031 T. Richards 11-09-11 request for map | High Pressure Sodium | 38.87196145000 | -77.00889032000
11/8/11 | 1070776 | 0 | INTERSTATE 395 | SW | 11/8/11 | 395-028S-4 | 395S603 | (Overhead guide sign light out) | 11-8-11I Paraway repaired pole (VW) | High Pressure Sodium | 38.88448494000 | -77.01260002000
11/8/11 | 1070775 | 0 | 9TH ST | SW | 11/11/11 | 395-041S-3 | 09SS607 | (Overhead guide sign light out) | 11-11-11 I Paraway - replaced 1-100w hps fixture (VW) | High Pressure Sodium | 38.88325163000 | -77.02403832000
11/8/11 | 1070774 | 0 | INTERSTATE 395 | SW | 11/10/11 | 395-025N-3 | 395N606 | (Overhead guide sign light out) | BCM - 11-10-11 - I. Paraway repaired light | High Pressure Sodium | 38.88300627000 | -77.01273300000
11/8/11 | 1070773 | 0 | INTERSTATE 395 | SW | 12/7/11 | 395-022N-9 | 395N612 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88233608000 | -77.01846985000
11/8/11 | 1070772 | 0 | INTERSTATE 695 | SE | 11/10/11 | 695-010E-5 | SEWE603 | (Overhead guide sign light out) | BCM. 11-10-11 - I. Paraway replaced fixture. Light on | High Pressure Sodium | 38.87707700000 | -76.98352340000
| 1070736 | 3649 | BANGOR ST | SE | 11/10/11 | 79428DC | 7A092DC | (Light out) | DA 11-10-11 @ 345am T. Richards repaired pole #79428dc 11-00350998-alley light out a long time, it is the last light in the alley behind her house. Costumer will try to call back with pole # cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.86044995000 | -76.95364320000
11/7/11 | 1070673 | 300 | 2ND ST | SW | 11/8/11 | 21595 | 6A370 | (Light out) | Da 11-08-11 @ 500am C .ashton repaired pole #21595 | High Pressure Sodium | 38.88562046000 | -77.01373008000
11/7/11 | 1070628 | 0 | ANACOSTIA FWY | NE | 11/7/11 | 79490 | 7A159 | (Light out) | DA 11-07-11 @ 145am T. Richards repaired pole #79490 | High Pressure Sodium | 38.88986353000 | -76.95869496000
11/5/11 | 1070500 | 0 | NEW YORK AVE | NE |  | 50005 | 5A039 | (Light out) | WBlack-11-7-11-TRichards completed on a duplicate ticket yesterday. | High Pressure Sodium | 38.91734425000 | -76.96859446000
11/5/11 | 1070499 | 0 | NEW YORK AVE | NE |  | 50002 | 5A036 | (Light out) | WBlack-11-7-11-TRichards completed on a duplicate ticket yesterday. | High Pressure Sodium | 38.91735721000 | -76.97069936000
11/5/11 | 1070498 | 0 | NEW YORK AVE | NE |  | 50001 | 5A035 | (Light out) |  | High Pressure Sodium | 38.91733557000 | -76.97140198000
11/5/11 | 1070477 | 1011 | NORTH CAPITOL ST | NW | 11/10/11 | 60044 | 6A234 | (Light out) | DA 11-10-11 @ 202am K. Simmons repaired pole #60044 | High Pressure Sodium | 38.90382567000 | -77.00893584000
11/3/11 | 1070345 | 0 | M ST | NW | 11/3/11 | 23730 | 2U534 | (Light out) | DA 11-03-11 C. Ashton repaired pole #23730 | High Pressure Sodium | 38.90557436000 | -77.04154706000
11/2/11 | 1070332 | 650 | 7TH ST | NW | 11/2/11 | 22459 | 6M677 | (Light out) | DA 11-02-11 @ 1055pm C. AShton repaired pole #22459 | High Pressure Sodium | 38.90166168000 | -77.02182085000
11/2/11 | 1070293 | 800 | 11TH ST | NW | 11/4/11 | 23378 | 2L020 | (Light out) | DA 11-04-11 @ 335am C .ashton repaired pole #23378 | High Pressure Sodium | 38.90015315000 | -77.02690628000
11/2/11 | 1070288 | 801 | I ST | NW | 11/7/11 | 22485 | 2M185 | (Light out) | DA 11-07-11 @ 100am C .ashton repaired pole #22485 | High Pressure Sodium | 38.90094807000 | -77.02328194000
11/2/11 | 1070287 | 1301 | 7TH ST | NW | 11/2/11 | 25697 | 6A797 | (Light out) | DA 11-02-11 @ 1025pm C .ashton repaired pole #25697 | High Pressure Sodium | 38.90780670000 | -77.02182162000
11/2/11 | 1070286 | 931 | 7TH ST | NW | 11/2/11 | 22458 | 6M673 | (Light out) | DA 11-02-11 @ 1040pm C. AShton repaired pole #22458 | High Pressure Sodium | 38.90144435000 | -77.02181926000
11/2/11 | 1070285 | 650 | 7TH ST | NW | 11/18/11 | 22459 | 6M677 | (Light off/on) | DA 11-07-11 @ 200am C. ashton pole #22459 light is on ands working T.BUIGE- 11/17/11- QC'D LIGHT IS ON | High Pressure Sodium | 38.90166168000 | -77.02182085000
11/2/11 | 1070283 | 0 | 7TH ST | NW | 11/18/11 | 22415 | 6M676 | (Light off/on) | DA 11-08-11 155am C. AShton repaired pole #22415 T.BUIGE- 11/17/11- QC'D LIGHT IS ON | High Pressure Sodium | 38.90118128000 | -77.02201316000
11/2/11 | 1070282 | 931 | 7TH ST | NW | 11/3/11 | 22414 | 6M678 | (Light out) | DA 10-03-11 @ 315am C. AShton repaired pole #22414 and installed new pole id tag | High Pressure Sodium | 38.90128473000 | -77.02201329000
11/2/11 | 1070281 | 806 | 7TH ST | NW | 11/8/11 | 22423 | 6M660 | (Light out) | DA 11-7-11 @ 210am C, ashton repaired opole #22423 repaired wires in t base | High Pressure Sodium | 38.90012937000 | -77.02201557000
11/2/11 | 1070280 | 825 | 7TH ST | NW | 11/7/11 | 22420 | 6M666 | (Light out) | DA 11-07-11 @ 250am C. AShton repaired pole #22420 | High Pressure Sodium | 38.90039135000 | -77.02201360000
11/2/11 | 1070279 | 707 | 7TH ST | NW | 11/7/11 | 22446 | 6M639 | (Light out) | DA 11-07-11 @ 310am C. Ashton repaired pole #22446 | High Pressure Sodium | 38.89882117000 | -77.02182001000
11/2/11 | 1070224 | 901 | 9TH ST | NW | 11/2/11 | 22987 | 2G988 | (Light out) | DA 11-02-11 @ 210am C. Ashton repaired pole #22987 twin pole right side | High Pressure Sodium | 38.90092176000 | -77.02415354000
11/2/11 | 1070223 | 901 | 9TH ST | NW | 11/2/11 | 22987 | 2G988 | (Light out) | DA 11-02-11 @ 210am C. Ashton repaired pole #22987 twin pole left side | High Pressure Sodium | 38.90092176000 | -77.02415354000
11/1/11 | 1070181 | 2400 | 14TH ST | NW | 11/2/11 | 12048 | 1A046 | (Light out) | DA 11-02-11 @ 1255am C. AShton adjusted photocell pole #12048 | High Pressure Sodium | 38.92087041000 | -77.03196022000
11/1/11 | 1070172 | 0 | 13TH ST | NW | 11/2/11 | 4K425 | 4U138 | (Light out) | DA 11-02-11 @ 243am B. Brown repaired pole #4k425 | High Pressure Sodium | 38.94497938000 | -77.02978632000
10/30/11 | 1069971 | 0 | 1ST ST | NE | 10/31/11 | 61239 | 6A264 | (Light out) | DA 10-31-11 @ 420am T. Richards repaired pole #61239 | High Pressure Sodium | 38.90515476000 | -77.00581203000
| 1069965 | 2139 | WISCONSIN AVE | NW | 10/31/11 | 30155 | 3G097 | (Light out) | DA 10-31-11 @ 1150pm C. Ashton installed 118 globe 11-00342500-20459 cwDesc: STREETLIGHT REPAIR | Incandescent | 38.91871515000 | -77.07035274000
10/28/11 | 1069947 | 0 | 7TH ST | NW | 4/13/12 | 25706 | 6A832 | (Light out) | 11-8-11 Darryl/Chris - traffic combo pole w/common duct - REFER to DDOt (VW) 10-31-11 Darryl/Chris - tractor trailer blocking MH - cannot access will return next day (VW) DA 10-30-11 @ 1030pm C. Ashton pole #25706 N/C underground | High Pressure Sodium | 38.91270444000 | -77.02180700000
10/28/11 | 1069946 | 0 | 7TH ST | NW | 11/8/11 | 25706 | 6A832 | (Light out) | 11-8-11 Darryl/Chris - REFRE to W/O #1069947 -traffic combo pole w/common duct - REFER to DDOt (VW) 10-31-11 Darryl/Chris - tractor trailer blocking MH - cannot access will return next day (VW) DA 10-30-11 @ 1030pm C. Ashton pole #25706 N/C unde | High Pressure Sodium | 38.91270444000 | -77.02180700000
10/28/11 | 1069945 | 0 | 7TH ST | NW | 11/8/11 | 25706 | 6A832 | (Light out) | 11-8-11 Darryl/Chris - REFRE to W/O #1069947 -traffic combo pole w/common duct - REFER to DDOt (VW) 10-31-11 Darryl/Chris - tractor trailer blocking MH - cannot access will return next day (VW) DA 10-30-11 @ 1030pm C. Ashton pole #25706 N/C underg | High Pressure Sodium | 38.91270444000 | -77.02180700000
10/28/11 | 1069925 | 0 | 7TH ST | NW | 11/8/11 | 25706 | 6A832 | (Light out) | 11-8-11 Darryl/Chris - REFRE to W/O #1069947 -traffic combo pole w/common duct - REFER to DDOt (VW) 10-31-11 Darryl/Chris - tractor trailer blocking MH - cannot access will return next day (VW) DA 10-30-11 @ 1030pm C. Ashton pole #25706 N/C underg | High Pressure Sodium | 38.91270444000 | -77.02180700000
10/28/11 | 1069909 | 0 | KENNEDY ST | NW | 10/28/11 | 4M070 | 4M070DC | (Light out) | 10-28-11 Bobby W - repaired pole (VW) | High Pressure Sodium | 38.95645469000 | -77.02220865000
10/25/11 | 1069623 | 2251 | WISCONSIN AVE | NW | 10/31/11 | 30163 | 3G078 | (Light off/on) | CFreeburger-10-27-11-QC'd and light is on DA 10-25-11 @ 1145pm K .Dunton repaired pole #30163 | High Pressure Sodium | 38.92025119000 | -77.07138809000
10/25/11 | 1069602 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 10/27/11 | 71275 | 7A206 | (Light out) | DA 10-27-11 @ 155am T. Richards repaired pole #71275 | High Pressure Sodium | 38.89829113000 | -76.92838596000
10/25/11 | 1069601 | 5403 | NANNIE HELEN BURROUGHS AVE | NE |  | 72648 | 7A191 | (Light out) | DeVon Smith on 11-22-10 Refer to DDOT. Per Brenda Kenney on 11-17-10 in DDOT meeting, Severn is no longer reasonable for any streetlights on NANNIE HELEN BURROUGHS AVE. Fort Mayor are installing new lights from Eastern Ave to Minnesota Ave. DA 10-27-11 @ | High Pressure Sodium | 38.89829839000 | -76.92250388000
10/25/11 | 1069600 | 5516 | NANNIE HELEN BURROUGHS AVE | NE | 10/28/11 | 72651 | 7A184 | (Light out) | DA 10-28-11 @ 1220am T. Richards repaired pole #72651 DA 10-27-11 @ 230am T. Richards pole #72651 need 400 powerdoor | High Pressure Sodium | 38.89830423000 | -76.92065348000
10/24/11 | 1069462 | 0 | K ST | NW | 10/25/11 | 22402 | 6A100 | (Light out) | DA10-25-11 @ 300am C .ashton repaired pole #22402 FRONT 11-00334936-STREET LIGHT HAS BEEN OUT FOR A WHILE cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90245268000 | -77.01971021000
10/24/11 | 1069448 | 611 | K ST | NW | 10/24/11 | 22404 | 6A973 | (Light out) | DA 10-24-11 @ 350am C. ashton repaired pole #22404 | High Pressure Sodium | 38.90245457000 | -77.02040204000
10/24/11 | 1069441 | 0 | MASSACHUSETTS AVE | NW | 10/24/11 | 22464 | 6A978 | (Light out) | DA 10-24-11 @ 255am C. AShton repaired pole #22464 | High Pressure Sodium | 38.90214093000 | -77.02159297000
10/24/11 | 1069440 | 650 | MASSACHUSETTS AVE | NW | 10/24/11 | 22465 | 6A979 | (Light out) | DA 10-24-11 @ 240am C. aShton repaired pole #22465 | High Pressure Sodium | 38.90204075000 | -77.02130668000
10/23/11 | 1069409 | 2487 | MINNESOTA AVE | SE | 10/24/11 | 80100 | 78575 | (Light out) | DA 10-23-11 @ 1135pm K. Simmons repaired pole #80100 | High Pressure Sodium | 38.87343340000 | -76.97095551000
10/23/11 | 1069395 | 1000 | 4TH ST | SE | 10/25/11 | 67542 | 6A434 | (Light out) | 10-25-11 REFER to W/O #1062985 DA 10-25-11 @ 115am T. Richards pole #67542 N/C Underround 0 volts | High Pressure Sodium | 38.87830526000 | -77.00064838000
10/23/11 | 1069384 | 0 | SOUTH DAKOTA AVE | NE | 10/25/11 | 58222DC | 5M216DC | (Light out) | DA 10-25-11 @ 400am K .Simmons repaired pole #58222dc | High Pressure Sodium | 38.92523014000 | -76.96540308000
10/23/11 | 1069383 | 0000 | BLADENSBURG RD | NE | 10/25/11 | 50102 | 5A088 | (Light out) | DA 10-24-11 @ 1156pm K Simmons repaired pole #50102 | High Pressure Sodium | 38.92799454000 | -76.96153011000
10/23/11 | 1069382 | 2820 | BLADENSBURG RD | NE | 10/25/11 | 50094 | 5A080 | (Light out) | DA 10-24-11 @ 1146pm K Simmons repaired pole #50094 | High Pressure Sodium | 38.92604672000 | -76.96392000000
10/23/11 | 1069349 | 1731 | 7TH ST | NW | 12/21/11 | 25708 | 6A842 | (Light out) | J. Lancaster completed on 12-21-11. Installed 240FT of No#10 cable, 40FT of No#8 cable and made splices inside manhole. DA 10-24-11 @ 205am C. Ashton pole #25708 N/C @ Base 11/1/2011 H. Lancaster sniffed vault, tried routing from both the pole base and | High Pressure Sodium | 38.91370731000 | -77.02182415000
| 1069321 | 627 | K ST | NW | 10/24/11 | 22406 | 6A976 | (Light out) | DA 10-24-11 @ 400am C. Ashton pole #22406 light found on and working Front 11-00333826-CALLER GAVE 3 POLE ID 22407, 22405, 22406 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90245551000 | -77.02105961000
| 1069322 | 639 | NEW YORK AVE | NW | 10/24/11 | 25975 | 6A087 | (Light out) | DA 10-24-11 @ 310am C. Ashton repaired pole #25975 Front 11-00333829-3 STREET POLES WITH THE SAME NO. 25975 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90309208000 | -77.02099074000
| 1069318 | 0 | K ST | NW | 10/27/11 | 22403 | 6A076 | (Light out) | DA 10-27-11 2 150am C. AShton pole #22403 light is on and working Front 11-00333823-5 STREETLIGHTS ARE OUT....IN SAME BLOCK...CALLER HAS GIVE POLE NO. FOR ALL LIGHTS THAT ARE OUT 22403, 22504,22502, 22501, AND 22730 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90260529000 | -77.02008282000
10/21/11 | 1069288 | 0 | 13TH ST | NW | 10/24/11 | 12572 | 1G529 | (Light out) | DA 10-24-11 @ 1230am C. AShton repaired pole #12572 DA 1-21-11 2 520am C. AShton pole #12572 needs 400 powerdoor | High Pressure Sodium | 38.91713413000 | -77.02951570000
10/20/11 | 1069164 | 0000 | INTERSTATE 395 | SW | 10/21/11 | 395-044E-6 | 695E616 | (Overhead guide sign light out) | E. Paraway 10/21/11 | High Pressure Sodium | 38.88228476000 | -77.01218684000
10/18/11 | 1068996 | 1218 | CONNECTICUT AVE | NW | 4/16/12 | 24532 | 2U519 | (Light out) | See W.O. 1005752 Refer to DDOT traffic combo pole. Streetlight and traffic light share the same duct. DA 10-19-11 @ 1235am C. Ashton pole #24532 N/C @ base | High Pressure Sodium | 38.90651643000 | -77.04185036000
10/17/11 | 1068860 | 2902 | BLADENSBURG RD | NE | 11/8/11 | 50099 | 5A085 | (Light out) | CFreeburger-11-7-11-QC'd light is on 11-1-11 Darryl/Chris - light working properly - (120v) at fixture (VW) 10-25-11 Al Young - unable to locate pole (VW) DA 10-20-11 @ 310am K .Simmons pole #50099 N/ C Underground - has 100 volts @ base | High Pressure Sodium | 38.92725738000 | -76.96243723000
10/17/11 | 1068813 | 0 | NEW YORK AVE | NE | 10/19/11 | 50005 | 5A039 | (Light out) | WBlack-10-18-11-scheduled for MOT | High Pressure Sodium | 38.91734425000 | -76.96859446000
10/17/11 | 1068812 | 0 | NEW YORK AVE | NE | 10/19/11 | 50001 | 5A035 | (Light out) | WBlack-10-18-11-scheduled for MOT | High Pressure Sodium | 38.91733557000 | -76.97140198000
10/16/11 | 1068687 | 600 | 1ST ST | NE | 10/19/11 | 60927 | 6U601 | (Light out) | DA 10-19-11 @ 1235am T. Richards repaired pole #60927 | High Pressure Sodium | 38.89824861000 | -77.00746947000
10/13/11 | 1068600 | 0 | CONNECTICUT AVE | NW | 10/17/11 | 24530 | 2U507 | (Light out) | DA 10-17-11 @ 350am C. aShton repaired pole #24530 NW Corner 11-00323355-Light pole was struck by vehicle, extensive damage to pole. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90717116000 | -77.04221131000
10/13/11 | 1068552 | 3520 | P ST | NW | 10/19/11 | 21004 | 2G127 | (Light off/on) | TBuige-10-18-11-QC'd and light is on DA 10-13-11 @ 1045pm C. Ashton repaired pole #21004 | High Pressure Sodium | 38.90865340000 | -77.07005766000
10/13/11 | 1068548 | 3338 | P ST | NW | 2/14/13 | 21010 | 2G137 | (Light out) | DA 10-17-11 @ 300am C. AShton pole #21010 is located behind constrution can not access | High Pressure Sodium | 38.90871624000 | -77.06742500000
10/12/11 | 1068393 | 4608 | EASY PL | SE | 10/14/11 | 75826 | 75826DC | (Light out) | DA 10-14-11 @ 105am T. Richards repaired pole #75826 | Incandescent | 38.87603875000 | -76.93343049000
10/12/11 | 1068382 | 4202 | BENNING RD | NE | 10/18/11 | 73867DC | 73867 | (Light out) | DA 10-18-11 @ 150am T Richards repaired pole #73867dc | High Pressure Sodium | 38.89298310000 | -76.94251439000
10/11/11 | 1068268 | 2500 | SHERMAN AVE | NW | 2/14/13 | 14218 | 1G468 | (Light out) | DA 10-12-11 @ 1205am T. Richards pole #14218 could not access light behind construction site - no avaliable info | High Pressure Sodium | 38.92144233000 | -77.02516708000
10/11/11 | 1068267 | 0 | SHERMAN AVE | NW | 10/17/11 | 12586 | 1G459 | (Light out) | 10-16-11 TBuige-QC'd light is now on DA 10-11-11 @ 1150pm T. ichards repaired pole #12586 | High Pressure Sodium | 38.92223537000 | -77.02543083000
10/11/11 | 1068254 | 5928 | GEORGIA AVE | NW | 10/12/11 | 4E220 | 4A828 | (Light out) | DA 10-12-11 @ 310am B. Brown repaired pole #4e220 | High Pressure Sodium | 38.96245901000 | -77.02779791000
10/9/11 | 1068094 | 627 | K ST | NW | 10/20/11 | 22406 | 6A976 | (Light out) | DA 10-20-11 @ 110am C .aShton installed 400 hps lamp and power door light is on 10-10-11 D Dixon/C Russell - wire burnt loose in t-base - pulled 100' #10 wire, 50' #6 bare copper 2 #8 cbs & tape (VW) | High Pressure Sodium | 38.90245551000 | -77.02105961000
10/6/11 | 1067907 | 1116 | U ST | NW | 10/7/11 | 13285 | 1G538 | (Light out) | DA 10-7-11 @ 545am C .ashton repaired pole #13285 | High Pressure Sodium | 38.91692228000 | -77.02795959000
| 1067795 | 2112 | SHEPHERD ST | NE | 10/7/11 | 51207DC | 52007DC | (Light out) | DA 10-7-11 @ 442a K Simmons repaired pole #51207dc Front 11-00314707- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93988228000 | -76.97467521000
10/5/11 | 1067791 | 1900 | 37TH ST | NW | 10/7/11 | 36891 | 30482 | (Light out) | DA 10-7-11 @ 425am C .Ashton repaired pole #36891 West Side 11-00313819-the user entered the address: 1936 37th St Nw, Washington, DC to see more details visit: http://seeclickfix.com/issues/130495 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91672906000 | -77.07292654000
10/5/11 | 1067686 | 4017 | GEORGIA AVE | NW | 10/10/11 | 4J345 | 4G277 | (Light out) | DA 10-9-11 @ 1147pm B. Brown repaired pole #4j345 | High Pressure Sodium | 38.94036991000 | -77.02500450000
10/5/11 | 1067667 | 3321 | IDAHO AVE | NW | 10/7/11 | 38888DC | 3U416 | (Light out) | DA 10-7-11 @ 105aam K Dunton reconnected overhead feed pole #38888dc(crimper) DA 10-6-11 @ 140am C. Ashton pole #38888dc needs big boom to access light | Mercury Vapor | 38.93408385000 | -77.07471732000
10/4/11 | 1067596 | 4600 | NORTH CAPITOL ST | NE | 10/10/11 | 4R756 | 4A797 | (Light out) | 10-10-11 S Manning - found ok (VW) | High Pressure Sodium | 38.94744567000 | -77.00873504000
10/4/11 | 1067576 | 1217 | CONNECTICUT AVE | NW | 10/4/11 | 27223 | 2U520 | (Light out) | DA 10-4-11 @ 230am C .Ashton repaired pole #27223 | High Pressure Sodium | 38.90639779000 | -77.04139143000
10/4/11 | 1067575 | 2418 | 18TH ST | NW | 10/12/11 | 11531 | 1G485 | (Light out) | TBuige-10-10-11-QC'd and found light is on DA 10-4-11 @ 145am C. aShton repaired pole #11531 | High Pressure Sodium | 38.92129769000 | -77.04231632000
10/3/11 | 1067486 | 0 | ANACOSTIA FWY | SE | 10/3/11 | 79466 | 7A130 | (Light out) | 10/03/2011 I. Paraway G. McDuffie Replaced 400HPS lamp (WP) | High Pressure Sodium | 38.88384591000 | -76.96362320000
10/2/11 | 1067404 | 4235 | 9TH ST | NW | 10/12/11 | 4K017 | 4G319 | (Light out) | TBuige-10-10-11-QC'd and found light is on 10-6-11 Darryl/Chris - wires wew not connected in MH or TBase - connected wires 3 #8 copper butt splices & tape (VW) DA 10-6-11 @ 315am K. Dunton pole #4k017 N/C Underground 0 volts | High Pressure Sodium | 38.94272297000 | -77.02520204000
10/2/11 | 1067395 | 0 | 13TH ST | NW | 10/6/11 | 4K425 | 4U138 | (Light out) | DA 10-6-11 @ 200am K. Dunton repaired pole #4k425 | High Pressure Sodium | 38.94497938000 | -77.02978632000
10/2/11 | 1067367 | 3850 | GEORGIA AVE | NW | 4/16/12 | 4J355 | 4G260 | (Light out) | BCM - 4/16/2012 - LIGHT ON - DA 10-5-11 @ 555am K. Dunton pole #4J355 N/C underground | High Pressure Sodium | 38.93855929000 | -77.02474527000
| 1067336 | 2311 | 33RD ST | SE | 10/5/11 | 74837DC | 7A101DC | (Light out) | DA 10--11 @ 410am T. richards repaired pole #74837dc Alley 11-00308430-the light has been out for weeks-I called on the phone and misplaced the no. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.86135172000 | -76.96056260000
9/29/11 | 1067257 | 5600 | 2ND ST | NE | 10/5/11 | 4P472DC | 4U160 | (Light out) | DA 10-2-11 @ 1022pm K Simmons repaired pole #4p472dc | High Pressure Sodium | 38.95826310000 | -77.00300671000
9/28/11 | 1067077 | 126 | 3RD ST | SE | 10/3/11 | 6A001 | 6A001 | (Light out) | DA 0-3-1 @ 530am T. Richards repaired pole #6a001 | Incandescent | 38.87684494000 | -77.00438348000
9/28/11 | 1067062 | 0 | NEW YORK AVE | NW | 9/28/11 | 22951 | 2L065 | (Light out) | DA 9-28-11 @ 1055pm C Ashton repaired pole #22951 | High Pressure Sodium | 38.90154741000 | -77.02618337000
9/27/11 | 1066851 | 3408 | WISCONSIN AVE | NW | 9/27/11 | 38772 | 3U402 | (Light out) | DA 9-27-11 @ 1240am K> Dunton repaired pole #38772 | High Pressure Sodium | 38.93510623000 | -77.07282513000
9/26/11 | 1066775 | 3859 | PENNSYLVANIA AVE | SE | 9/29/11 | 77881DC | 7E010 | (Light out) | DA 9-29-11 @ 310am T. Richards repaired pole #77881dc | High Pressure Sodium | 38.86525460000 | -76.95024453000
| 1066724 | 635 | T ST | NW | 10/12/11 | 14389 | 1M006 | (Light out) | TBuige-10-10-11-QC'd and found light is on 10-3-11 Al Young/G Smith - checked power (125v) light is ok (VW) DA 9-27-11 @ 630am K. Dunton pole #14389 N/C Underground North Side 11-00302624-I called about this last week and it is still not fixed. Thank | High Pressure Sodium | 38.91563319000 | -77.02130285000
9/25/11 | 1066690 | 1245 | H ST | NE |  | 62349 | 6S118 | (Light out) |  | High Pressure Sodium | 38.90011568000 | -76.98878114000
9/25/11 | 1066689 | 1224 | H ST | NE |  | 62348 | 6S114 | (Light out) |  | High Pressure Sodium | 38.90011721000 | -76.98943529000
9/25/11 | 1066688 | 1210 | H ST | NE |  | 62333 | 6S165 | (Light out) |  | High Pressure Sodium | 38.90029723000 | -76.98978110000
9/25/11 | 1066687 | 1232 | H ST | NE |  | 62332 | 6S161 | (Light out) |  | High Pressure Sodium | 38.90029650000 | -76.98911501000
9/24/11 | 1066670 | 1301 | 20TH ST | NW | 9/27/11 | 24830 | 2A017 | (Light out) | DA 9-27-11 @ 235am C Ashton repaired pole #24830 Alley 11-00301614-Please fix as soon as possible. Very dark and difficult to see parking at night. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.90756285000 | -77.04480461000
9/22/11 | 1066541 | 2418 | 18TH ST | NW | 9/29/11 | 11531 | 1G485 | (Light out) | TBuige-9-29-11-QC'd and light is on DA 9-28-11 @ 425am C Ashton pole #11531 light is on and working voltage is good | High Pressure Sodium | 38.92129769000 | -77.04231632000
9/21/11 | 1066462 | 1117 | NEW HAMPSHIRE AVE | NW | 9/22/11 | 23864 | 2G713 | (Light out) | DA 9-21-11 @ 1135pm C AShton repaired pole #23864 | High Pressure Sodium | 38.90423833000 | -77.04840189000
9/21/11 | 1066420 | 911 | T ST | NW | 9/27/11 | 13452 | 1L371 | (Light out) | DA 9-27-11 @ 610am K. Dunton repaired pole #13452 | High Pressure Sodium | 38.91552640000 | -77.02455445000
9/21/11 | 1066386 | 2902 | BLADENSBURG RD | NE | 9/25/11 | 50099 | 5A085 | (Light out) | DA 9-25-11 @ 1030pm K Simmons repaired pole #50099 | High Pressure Sodium | 38.92725738000 | -76.96243723000
9/21/11 | 1066385 | 2800 | BLADENSBURG RD | NE | 9/25/11 | 50097 | 5A083 | (Light out) | DA 9-25-11 @ 1013pm K. Simmons repaired pole #50097 | High Pressure Sodium | 38.92677841000 | -76.96302397000
9/21/11 | 1066312 | 3636 | GEORGIA AVE | NW | 9/22/11 | 12965 | 1G222 | (Light out) | DA 9-22-11 @ 315am C Ashton pole #12965 light found okay | High Pressure Sodium | 38.93515126000 | -77.02421018000
9/21/11 | 1066305 | 800 | 44TH ST | NE | 10/17/11 | 71311DC | 7A245 | (Light out) | 10-17-11 Damien/Bobby - we are not responsible for lights on N H B Ave (VW) 10-5-11 Damien - pole equipment need to be transferred (VW) DA 9-27-11 @ 1020pm T. Richards pole #71311dc NC To Overhead | High Pressure Sodium | 38.90055492000 | -76.93897667000
9/21/11 | 1066304 | 4406 | NANNIE HELEN BURROUGHS AVE | NE | 9/27/11 | 71307DC | 7A242 | (Light out) | DA 9-27-11 @ 605am T> Richards repaired pole #71307dc | High Pressure Sodium | 38.90023779000 | -76.93819749000
9/21/11 | 1066295 | 0732 | 19TH ST | NE | 9/22/11 | 70075 | 7A057 | (Light off/on) | DA 9-22-11 @ 20am T. Richards pole #70075 needs an arm and fixture refer to 1065891 | High Pressure Sodium | 38.89841600000 | -76.97655870000
9/21/11 | 1066276 | 1215 | CONNECTICUT AVE | NW | 9/21/11 | 24533 | 2U523 | (Light out) | DA 9-21-11 @ 235am C. Ashton repaired pole #24533 | High Pressure Sodium | 38.90616068000 | -77.04157912000
9/21/11 | 1066255 | 2721 | PENNSYLVANIA AVE | SE | 9/21/11 | 78571DC | 7E082 | (Light out) | DA 9-21-11 @ 1230am T. Richards repaired pole #78571dc | High Pressure Sodium | 38.87220266000 | -76.96783710000
9/20/11 | 1066174 | 1117 | NEW HAMPSHIRE AVE | NW | 9/20/11 | 23864 | 2G713 | (Light out) | DA 9-20-11 C .ahton pole #23864 needs 400 powerdoor | High Pressure Sodium | 38.90423833000 | -77.04840189000
9/20/11 | 1066161 | 900 | U ST | NW | 9/22/11 | 13983 | 1G551 | (Light out) | DA 9-22-11 @ 3330am C. Ashton repaired pole #13983 | High Pressure Sodium | 38.91713116000 | -77.02591861000
| 1066112 | 2139 | WISCONSIN AVE | NW | 9/20/11 | 30155 | 3G097 | (Light out) | DA 9-19-11 @ 1245am C. AShton repaired pole #30155 needs 118 globe Front 11-00294585- cwDesc: STREETLIGHT REPAIR | Incandescent | 38.91871515000 | -77.07035274000
9/19/11 | 1066003 | 1101 | NEW HAMPSHIRE AVE | NW | 9/19/11 | 23859 | 2G712 | (Light out) |  | High Pressure Sodium | 38.90420020000 | -77.04868539000
9/16/11 | 1065889 | 5065 | E ST | SE | 9/16/11 | 70032 | 7A017 | (Light out) | DA 9-15-11 @ 1215am T. Richards repaired pole #70032 | High Pressure Sodium | 38.88238947000 | -76.92997311000
9/14/11 | 1065798 | 741 | 51ST ST | SE | 9/16/11 | 75475 | 75475DC | (Light out) | DA 9-15-11 @ 1155pm T/ Richards pole #75475 light is on and working Alley 11-00289942- cwDesc: ALLEYLIGHT REPAIR | Incandescent | 38.87911825000 | -76.93033276000
9/14/11 | 1065763 | 3346 | PENNSYLVANIA AVE | SE | 9/15/11 | 78541DC | 7E112 | (Light out) | DA 9-15-11 @ 125am T. Richards new teardrop fixture on wood pole not turned over yet - light is on and working | High Pressure Sodium | 38.86849478000 | -76.95872334000
9/14/11 | 1065734 | 0 | M ST | NW | 9/16/11 | 23718 | 2G720 | (Light out) | DA 9-15-11 @ 1130pm C. AShton repaired pole #23718 | High Pressure Sodium | 38.90536068000 | -77.04765891000
9/14/11 | 1065731 | 1215 | CONNECTICUT AVE | NW | 9/19/11 | 24533 | 2U523 | (Light out) | DA 9-19-11 @ 1210am C .aShton pole #24533 needs 400 fixture | High Pressure Sodium | 38.90616068000 | -77.04157912000
9/14/11 | 1065727 | 0 | SHERMAN AVE | NW | 9/15/11 | 12586 | 1G459 | (Light out) | DA 9-15-11 @ 530am C. AShton pole #12586 N/C @ Base09/15/2011 S. Manning Installed pole tag Complete(WP) | High Pressure Sodium | 38.92223537000 | -77.02543083000
9/14/11 | 1065688 | 1100 | 1ST ST | NE | 10/11/11 | 61235 | 6S233 | (Light out) | CFreeburger-10-10-11-QC'd and found light is on 10-5-11 Darryl/Chris - cable missing between MH 450' /0 rlw cable 150' #6 bare copper 5 copper butt splices & tape (VW) 9-22-11 Darryl/Chris - cable missing between poles (VW) DA 9-20-11 @ 405am K. Dunt | High Pressure Sodium | 38.90411117000 | -77.00597136000
9/13/11 | 1065475 | 2114 | 14TH ST | SE | 9/13/11 | 80524 | 8M023 | (Light out) | DA 9-12-11 @ 1035pm K. Simmons repaired pole #80524 adjusted tlpc | High Pressure Sodium | 38.86496135000 | -76.98572542000
9/12/11 | 1065380 | 3408 | WISCONSIN AVE | NW | 9/15/11 | 38772 | 3U402 | (Light out) | DA 9-14-11 @ 505am K Dunton pole #38772 needs 400 powerdoor | High Pressure Sodium | 38.93510623000 | -77.07282513000
9/8/11 | 1065080 | 5318 | B ST | SE | 9/13/11 | 75567 | 75567DC | (Light out) | DA 9-13-11 @ 500am T/ Richards pole #75567 power restored | High Pressure Sodium | 38.88634623000 | -76.92538243000
9/8/11 | 1065079 | 5318 | B ST | SE | 9/14/11 | 75566 | 75566DC | (Light out) | DA 9-13-11 @ 1115pm T. Richards pole #75566 light is on and working previously repaired | High Pressure Sodium | 38.88629607000 | -76.92512862000
9/8/11 | 1065078 | 5314 | B ST | SE | 9/13/11 | 75565 | 75565DC | (Light out) | DA 9-13-11 @ 500am T. Richards pole #75565 power restored | High Pressure Sodium | 38.88626314000 | -76.92486984000
9/8/11 | 1065077 | 5335 | B ST | SE | 9/13/11 | 75564 | 75564DC | (Light out) | DA 9-13-11 @ 500am T> Richards repaired pole #75564 | High Pressure Sodium | 38.88622800000 | -76.92459483000
| 1064971 | 5335 | B ST | SE | 9/13/11 | 75564 | 75564DC | (Light out) | DA 9-13-11 @ 340m T. Richards repaired pole #75564d 11-00280435-3 to 4 alley lights are out and the caller is reporting the area is dangerous without lighting. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.88622800000 | -76.92459483000
9/6/11 | 1064830 | 1200 | ALLISON ST | NW | 9/13/11 | 4K102 | 4U137 | (Light out) | DA 9-13-11 @ 154am R. Warren repaired pole #4k102 | High Pressure Sodium | 38.94501678000 | -77.02957418000
9/3/11 | 1064673 | 1500 | KEARNEY ST | NE | 9/7/11 | 59986 | 5A177 | (Light out) | DA 9-7-11 @ 317am K. Simmons repaired pole #59986 Block 11-00276976-There are multiple street lights out on at the intersection on 15th and Kearny. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91401980000 | -77.01759054000
| 1064674 | 0 | RHODE ISLAND AVE | NW | 9/7/11 | 59997 | 5A189 | (Light out) | DA 9-7-11 @ 300am K. Simmons repaired pole #59997 West Bound 11-00276978- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91491231000 | -77.01415169000
| 1064611 | 2418 | 18TH ST | NW | 9/9/11 | 11531 | 1G485 | (Light out) | DA 9-9-11 @ 339am R. Warren repaired pole #11531 11-00274685-street light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92129769000 | -77.04231632000
8/30/11 | 1064267 | 300 | D ST | SW | 9/9/11 | 21636 | 6A364 | (Light out) | DA 9-8-11 @ 1030pm C. Ashton repaired pole #21636 | High Pressure Sodium | 38.88513641000 | -77.01402907000
8/30/11 | 1064243 | 5318 | B ST | SE | 9/12/11 | 75567 | 75567DC | (Light out) | 9-6-11 Chris/Bunky - no current - overhead (VW) 09/12/2011 Greenfield, Woodland Installed 120' #6 Triplex Made secondary taps and tree trimming(WP) | High Pressure Sodium | 38.88634623000 | -76.92538243000
8/30/11 | 1064242 | 5318 | B ST | SE | 9/12/11 | 75566 | 75566DC | (Light out) | 9-1-11 Al Johnson- no power - missing 100' cable VW) 9-6-11 Chris/Bunky - no current - overhead (VW Greenfield, Woodland Installed 120' #6 Triplex Made secondary taps and tree trimming(WP)) | High Pressure Sodium | 38.88629607000 | -76.92512862000
8/30/11 | 1064236 | 5314 | B ST | SE | 9/12/11 | 75565 | 75565DC | (Light out) | 9-1-11 Al Johnson- no power - missing 100' cable VW) 9-6-11 Chris/Bunky - no current - overhead (VW) Greenfield, Woodland Installed 120' #6 Triplex Made secondary taps and tree trimming(WP) | High Pressure Sodium | 38.88626314000 | -76.92486984000
8/30/11 | 1064235 | 5335 | B ST | SE | 9/12/11 | 75564 | 75564DC | (Light out) | 9-1-11 Al Johnson- no power - missing 100' cable VW) 9-6-11 Chris/Bunky - no current - overhead (VW Greenfield, Woodland Installed 120' #6 Triplex Made secondary taps and tree trimming(WP)) | High Pressure Sodium | 38.88622800000 | -76.92459483000
8/30/11 | 1064199 | 0 | EASTERN AVE | NE | 9/9/11 | 52362DC | 5L678 | (Light out) | DA 9-9-11 @ 532am K. Simmons repaired pole #52362dc DA 9-5-11 @ 1112pm K. Simmons pole #52362dc Needs 250hps fixture (unable to install due to heavy Rain) | High Pressure Sodium | 38.94352462000 | -76.97396934000
8/30/11 | 1064172 | 2206 | 18TH ST | NW | 8/31/11 | 11411 | 1G502 | (Light out) | 8-31-11 Chris - reconnected NWP to fixture (VW) | High Pressure Sodium | 38.91905896000 | -77.04152631000
8/29/11 | 1064045 | 300 | EASTERN AVE | NE | 9/2/11 | 70026 | 72855 | (Light out) | DA 9-2-11 @ 311am R. Warren pole #70026 light found on and working | High Pressure Sodium | 38.89394625000 | -76.91101330000
8/29/11 | 1063933 | 3301 | P ST | NW | 9/1/11 | 21014 | 2G141 | (Light out) | DA 91-11 @ 1228am C. Ashton repaired pole #21014 | High Pressure Sodium | 38.90874337000 | -77.06631235000
8/29/11 | 1063908 | 3142 | 15TH PL | SE | 8/31/11 | 81711 | 87988 | (Light out) | 08/31/2011 Darrell Dixon 150HPS bulb (WP) | High Pressure Sodium | 38.85043840000 | -76.98195701000
8/29/11 | 1063903 | 4500 | SHERIDAN RD | SE | 8/31/11 | 81357DC | 8U648 | (Light out) | DA 8-31-11 @ 1205am K. Simmons repaired pole #81357dc | High Pressure Sodium | 38.85751979000 | -76.99325240000
8/29/11 | 1063901 | 4500 | SHERIDAN RD | SE | 8/31/11 | 81359DC | 8U644 | (Light out) | DA 8-31-11 @ 1235am K. Simmons repaired pole #81359dc repaired wire in powerdoor | High Pressure Sodium | 38.85817131000 | -76.99317521000
8/26/11 | 1063790 | 635 | T ST | NW | 9/27/11 | 14389 | 1M006 | (Light out) | 9-23-11 hudson/Jason - same as W/O # 1065953 (VW) DA 9-1-11 @ 1055pm C. Ashton installed 400hps lamp, fixture, TLPC - pole still only reading 70v HN, 70v HG, 0v NG refer to fault crew | High Pressure Sodium | 38.91563319000 | -77.02130285000
8/26/11 | 1063739 | 0000 | MONTANA AVE | NE | 8/26/11 | 50075 | 5A060 | (Light out) | DA 8-26-11 @ 144am K. Simmons repaired pole #50075 | High Pressure Sodium | 38.91680835000 | -76.97824997000
8/25/11 | 1063694 | 815 | 6TH ST | NW | 9/13/11 | 60542 | 6M707 | (Light out) | 9-12-11 Hudson/Jason -need MH clean up (VW) 9-7-11 AL Young/Bunky - see below comments (VW) 8-29-11 DArryl Dixon - N/C - bad nuetral need MH clean out (VW)09/13/2011 Hudson Lancaster MH cleaned out, found pipe, rodded duct, respliced wire in pole ba | High Pressure Sodium | 38.90031850000 | -77.01979505000
8/25/11 | 1063663 | 0 | C ST | SW | 8/25/11 | 21788 | 6A353 | (Light out) | DA 8-25-11 @ 340am C.ashton reattached globe pole#21788 | High Pressure Sodium | 38.88598753000 | -77.01505038000
8/23/11 | 1063519 | 5222 | LOUGHBORO RD | NW | 8/26/11 | 34484 | 3M077 | (Light out) | DA 8-26-11 @ 245am K .Dunton repaired pole #34484 (NSV) | High Pressure Sodium | 38.93581153000 | -77.10697579000
8/23/11 | 1063499 | 3901 | ALABAMA AVE | SE | 8/25/11 | 78524DC | 7E137 | (Light off/on) | DA 8-25-11 @ 105am T. Richards pole #78524dc light is on and working DA 8-24-11 @ 155am T. Richards repaired pole #78524dc | High Pressure Sodium | 38.86548351000 | -76.95124229000
8/23/11 | 1063454 | 0 | O ST | NW | 8/23/11 | 24475 | 2G771 | (Light out) | DA 8-23-11 @ 215am C. AShton repaired pole #24475 | High Pressure Sodium | 38.90841495000 | -77.04472917000
8/22/11 | 1063328 | 0 | RHODE ISLAND AVE | NW | 8/24/11 | 25203 | 2M199 | (Light out) | DA 8-24-11 @ 1010pm C. Ashton pole #25203 light is on and working 8-24-11 Darryl/Chris -pulled cable from MH to fixture 200' #10 wire, 50' bare copper 4 #8 cbs & tape (VW) DA 8-22-11 @ 205am C. Ashton pole #25203 N/C Underground | High Pressure Sodium | 38.91231053000 | -77.02236616000
8/22/11 | 1063327 | 0 | 8TH ST | NW | 8/22/11 | 25202 | 6A829 | (Light out) | DA 8-22-11 @ 150am C. aShton repaired pole #25202 | High Pressure Sodium | 38.91242134000 | -77.02206576000
8/18/11 | 1063156 | 5000 | NANNIE HELEN BURROUGHS AVE | NE |  | 71278DC | 7A212 | (Light out) | DA 8-19-11 @ 1230am T. Richards pole #71278dc N/C to Overhead 1 volt | High Pressure Sodium | 38.89843573000 | -76.92937719000
8/18/11 | 1063154 | 704 | NANNIE HELEN BURROUGHS AVE | NE |  | 71274DC | 71274 | (Light out) | DA 8-19-11 @ 1220am T. Richards pole #71274dc N/C to Overhead 1 volt | High Pressure Sodium | 38.89844116000 | -76.92783425000
8/18/11 | 1063125 | 5000 | NANNIE HELEN BURROUGHS AVE | NE | 1/26/12 | 71278DC | 7A212 | (Light out) | DA 8-19-11 @ 1230am T. Richards pole #71278dc N/C to Overhead 1 volt 11-00255970-4-5 streetlights are out on on Nannie Helen Burrough Ave, NE between 51st and 50th sts, NE cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89843573000 | -76.92937719000
| 1063119 | 815 | 6TH ST | NW | 8/19/11 | 60542 | 6M707 | (Light out) | DA 8-19-11 @ 345am K. Dunton repaired pole #60542 Front 11-00255381-street light is out at this location cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90031850000 | -77.01979505000
8/18/11 | 1063102 | 1000 | M ST | SE | 8/18/11 | 67368 | 6L953 | (Light out) | DA 8-18-11 @ 150am T. Richards repaired pole #67368 | High Pressure Sodium | 38.87639604000 | -76.99069757000
8/18/11 | 1063101 | 0 | H ST | NW | 8/18/11 | 22739 | 2G965 | (Light out) | DA 8-18-11 @ 235am C .ashton repaired pole #22739 twin light right side | High Pressure Sodium | 38.89969019000 | -77.02607864000
8/18/11 | 1063100 | 0 | H ST | NW | 8/18/11 | 22739 | 2G965 | (Light out) | DA 8-18-11 @ 235am C. ashton repaired pole #22739 twin light left side | High Pressure Sodium | 38.89969019000 | -77.02607864000
8/17/11 | 1062985 | 1000 | 4TH ST | SE | 1/26/12 | 67542 | 6A434 | (Light out) | 9-2-11 REFER to DDOT (VW) DA 8-18-11 @ 130am T. Richards pole #67542 N/C Underground 0 volts Hudson . New construction in area. Pole are being replaced. New MH/ volts are being installed and took pictures of the area. 08/18/2011 (WP) | High Pressure Sodium | 38.87830526000 | -77.00064838000
8/16/11 | 1062836 | 4300 | GEORGIA AVE | NW | 8/19/11 | 4K516 | 4G310 | (Light out) | 8-19-11 AL Johnson - removed 28' pole w/ t-base, 8' arm, fixture and lamp - discontinued (VW) DeVon Smith on 8-18-11. (Temp) streetlight pole arm and fixture needs to be removed. DA 8-17-11 @ 334am R. Warren pole #4K516 pole has been hit an damaged - | High Pressure Sodium | 38.94386006000 | -77.02614886000
8/14/11 | 1062651 | 0 | H ST | NW | 8/15/11 | 22621 | 2G970 | (Light out) | DA 8-15-11 @ 1010pm C. Ashton could not locate pole #22621 @ this address | High Pressure Sodium | 38.89990649000 | -77.02521079000
8/14/11 | 1062647 | 700 | H ST | NW | 8/15/11 | 22425 | 6M656 | (Light out) | DA 8-15-11 @ 135am C .AShton repaired pole #22425 | High Pressure Sodium | 38.89969708000 | -77.02201582000
8/14/11 | 1062645 | 1123 | 5TH ST | NW | 8/25/11 | 29176 | 6M767 | (Light out) | 8-17-11 Hudson/Jason - could not locate pole (VW) DA 8-16-11 @ 325am C. AShton pole #29176 N/C @ Base Could not locate pole Hudson Lancaster 08/24/2011 (WP) 08/25/2011 Pulled out burnt wire from duct in MH going up pole. Put in new wire. Check light | High Pressure Sodium | 38.90490674000 | -77.01826674000
8/11/11 | 1062542 | 457 | MASSACHUSETTS AVE | NW | 8/26/11 | 60481 | 6A195 | (Light out) | 8-26-11 G Smith/R Fike - Removed 28' pole w/ 400 hps fix, 8' arm & TBase - need restoration - (VW) 8-12-11 Darryl/Chris - new twin-20 400hps fixtureshave been installed 2' away from fixture with n/c - lights working (VW) DA 8-11-11 @ 1025pm C .Ashton po | High Pressure Sodium | 38.90073307000 | -77.01753805000
8/11/11 | 1062535 | 1000 | M ST | SE | 8/12/11 | 67367 | 6L939 | (Light out) | DA 8-12-11 @ 335am T. Richards pole #67367 N/C underground - duplicate ticket refer to wo #1052191 | High Pressure Sodium | 38.87641377000 | -76.99123690000
8/11/11 | 1062415 | 3128 | SHERMAN AVE | NW | 8/11/11 | 12867 | 1L264 | (Light out) | DA 8-11-11 @ 130am C. AShton repaired pole #12867 | High Pressure Sodium | 38.92970603000 | -77.02645797000
8/10/11 | 1062343 | 0 | 13TH ST | NW | 8/10/11 | 4K495 | 4U126 | (Light out) | DA 8-10-11 @ 146am R. Warren repaired pole #4k495 | High Pressure Sodium | 38.94627780000 | -77.02960126000
8/10/11 | 1062339 | 0 | WASHINGTON AVE | SW | 8/10/11 | 21663 | 6A382 | (Light out) | DA 8-10-11 @ 220am C. Ashton repaired pole #21663 | High Pressure Sodium | 38.88671906000 | -77.01325730000
8/9/11 | 1062263 | 5327 | EAST CAPITOL ST | NE | 8/10/11 | 73590 | 73590DC | (Light out) | 8-10-11 N Woodland - installed 250w hps lamp PC (VW) | High Pressure Sodium | 38.88965012000 | -76.92461303000
8/9/11 | 1062234 | 1535 | TANNER PL | SE | 8/9/11 | 81804 | 88081 | (Light out) | DA 8-9-11 @ 241am K. Simons repaired pole #81804 | High Pressure Sodium | 38.84753691000 | -76.98065162000
8/8/11 | 1062167 | 0 | EAST CAPITOL ST | NE | 8/9/11 | 73516 | 73516DC | (Light out) | DA 8-9-11 @ 145am T. Richards repaired pole #73516 | High Pressure Sodium | 38.88988897000 | -76.92617008000
8/8/11 | 1062161 | 5507 | NANNIE HELEN BURROUGHS AVE | NE | 8/15/11 | 72638DC | 7A187 | (Light off/on) | WBlack-8-14-11-MJohnson QC'd the asset and found the light to be on DA 8-10-11 @ 1235am T. Richards repaired pole #72638dc | High Pressure Sodium | 38.89848022000 | -76.92182881000
8/8/11 | 1062159 | 4308 | NANNIE HELEN BURROUGHS AVE | NE | 8/10/11 | 71312DC | 7A246 | (Light out) | DA 8-10-11 @ 1205am T. Richards repaired pole #71312dc | High Pressure Sodium | 38.90072786000 | -76.93937809000
8/4/11 | 1061984 | 0 | 14TH ST | NW | 8/9/11 | 13019 | 1G015 | (Light out) | 8-9-11 AL Johnson/G Edwards - replaced T-Base (VW) 8-8-11 AL johnson/ G Edwards - places no parking signs for 8-9-11 (VW) | High Pressure Sodium | 38.92900455000 | -77.03255621000
8/3/11 | 1061890 | 2222 | WISCONSIN AVE | NW | 8/3/11 | 30162 | 3G082 | (Light out) | DA 8-3-11 @ 325am C. Ashton repaired pole #30162 | High Pressure Sodium | 38.91993778000 | -77.07113468000
8/2/11 | 1061836 | 3128 | SHERMAN AVE | NW | 8/4/11 | 12867 | 1L264 | (Light out) | DA 8-4-11 @ 322am R. Warren repaired pole #12867 | High Pressure Sodium | 38.92970603000 | -77.02645797000
8/2/11 | 1061832 | 1099 | L ST | NW | 2/7/12 | 27357 | 2M407 | (Light out) | 10-10-11 S Manning - need to be re-GPS (VW) 9-6-11 S Manning need to be re-GPS 8-26-11 S Manning - PLEASE SEE BELOW COMMENTS (VW) 8-9-11 S Manning -see comments below (VW) 8-8-11 S Manning - all new poles that need to obe re GPS (VW) DA 8-8-11 @ 2 | High Pressure Sodium | 38.90350563000 | -77.03182310000
8/1/11 | 1061801 | 3430 | BAKER ST | SE | 8/2/11 | 74763DC | 7A077DC | (Light out) | DA 8-2-11 @ 300am T. Richards repaired pole #74763dc SIDE 11-00235580-WOODEN POLE LIGHT HAS BEEN OUT FOR THREE DAYS cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85946884000 | -76.95655830000
8/1/11 | 1061774 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 8/2/11 | 71275 | 7A206 | (Light out) | DA 8-2-11 @ 1240sm T. Richards repaired pole #71275 | High Pressure Sodium | 38.89829113000 | -76.92838596000
7/31/11 | 1061727 | 5575 | SOUTH DAKOTA AVE | NE | 8/1/11 | 4P773DC | 4P773 | (Light out) | DA 8-1-11 @ 1218am R. Warren repaired pole #4p773dc | High Pressure Sodium | 38.95786955000 | -77.00157634000
7/28/11 | 1061627 | 0 | MACARTHUR BLVD | NW | 7/29/11 | 33891 | 3A375 | (Light out) | DA 7-29-11 @ 320am K .Dunton repaired pole #33891 | High Pressure Sodium | 38.92881945000 | -77.10590630000
7/26/11 | 1061438 | 4811 | NORTH CAPITOL ST | NW | 7/29/11 | 4R751 | 4A792 | (Light out) | DA 7-28-11 @ 302am R. Warren pole #4r751 N/C underground Respliced hot wire and neutral checked light and is okay Hudson Lancaster 07/29/2011 (WP) | High Pressure Sodium | 38.94920682000 | -77.00886682000
7/26/11 | 1061400 | 60 | M ST | SE | 7/29/11 | 67424 | 6L599 | (Light out) | 7-29-11 Damien/Young - made splice on hotwire in t-base (VW) | High Pressure Sodium | 38.87659105000 | -77.00715580000
7/26/11 | 1061328 | 0 | ANACOSTIA FWY | SE | 7/27/11 | 79470 | 7A134 | (Light out) | 7-27-11I Paraway - installed 400hps lamp, short cap (VW) | High Pressure Sodium | 38.88120301000 | -76.96478109000
7/25/11 | 1061289 | 1535 | TANNER PL | SE | 7/29/11 | 81804 | 88081 | (Light out) | DA 7-29-11 @ 310am K .Simmons repaired pole #81804 7-26-11 Darryl/Chris street blocked (VW) | High Pressure Sodium | 38.84753691000 | -76.98065162000
7/24/11 | 1061146 | 2400 | 14TH ST | NW | 7/28/11 | 12048 | 1A046 | (Light out) | DA 7-28-11 @ 1230am C .ashton repaired pole #12048 | High Pressure Sodium | 38.92087041000 | -77.03196022000
7/22/11 | 1061064 | 4801 | NORTH CAPITOL ST | NW | 8/11/11 | 4R752 | 4A793 | (Light out) | 7-25-11 Ronnie Fike/V Ham - removed28' pole w/8' arm, 400w hps fixture & 15" T-Base (VW) DA 7-25-11 @ 235am K. Simmons pole has been hit needs new pole , t base ,arm and fixture pole #4R752 NA 11-00223728-ENTIRE LIGHT PIECE HAS FALLEN FROM LAMP POST. | High Pressure Sodium | 38.94885643000 | -77.00884149000
7/21/11 | 1060963 | 0 | P ST | NW | 7/21/11 | 25809 | 6U459 | (Light out) | DA 7-21-11 @ 30am C .ashton repaired pole #25809 | High Pressure Sodium | 38.90959101000 | -77.02381355000
7/20/11 | 1060868 | 0 | 22ND ST | NW | 7/20/11 | 23904 | 2G784 | (Light out) | DA 7-19-11 @ 1150pm C .Ashton repaired pole #23904 | High Pressure Sodium | 38.90422508000 | -77.04874413000
7/19/11 | 1060851 | 0 | 22ND ST | NW | 7/21/11 | 23904 | 2G784 | (Light out) | DA 7-21-11 @ 142am C .aShton pole #23904 light is on and working previously repaired Front 11-00220039-on metal pole cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90422508000 | -77.04874413000
7/18/11 | 1060706 | 2418 | 18TH ST | NW | 7/18/11 | 11531 | 1G485 | (Light out) | already open work order | High Pressure Sodium | 38.92129769000 | -77.04231632000
7/18/11 | 1060705 | 2407 | 18TH ST | NW | 7/18/11 | 11533 | 1G491 | (Light out) | DA 7-18-11 @ 250am C. aShton repaired pole #11533 adjusted TLpc | High Pressure Sodium | 38.92063969000 | -77.04213470000
7/14/11 | 1060518 | 3300 | O ST | NW | 7/20/11 | 21106 | 2G177 | (Light dim) | DA 7-20-11 @ 1200am C .Ashton pole #21106 light is on and working 120HG, 120HN, o NG DA 7-18-11 @ 200am C .AShtn repaired pole #21106 | High Pressure Sodium | 38.90770069000 | -77.06613582000
7/14/11 | 1060514 | 3200 | O ST | NW | 7/20/11 | 21107 | 2G184 | (Light off/on) | DA 7-20-11 @ 1215am C> ashton pole #21107 light is on and working DA 7-18-11 @ 215am C .AShtion repaired pole #21107 | High Pressure Sodium | 38.90790096000 | -77.06601474000
7/12/11 | 1060314 | 3719 | GEORGIA AVE | NW | 7/13/11 | 4J339 | 4G241 | (Light out) | DA 7-13-11 @ 410am R. Warren repaired pole #4J339 | High Pressure Sodium | 38.93725736000 | -77.02432870000
7/12/11 | 1060277 | 721 | KENNEDY ST | NW | 7/12/11 | 4M073 | 4M073DC | (Light out) | DA 7-12-11 @ 312am K. Simmons repaired pole #4m073 | High Pressure Sodium | 38.95641506000 | -77.02340733000
7/11/11 | 1060227 | 3356 | PENNSYLVANIA AVE | SE |  | 78539DC | 7E120DC | (Light out) | DA 7-14-11 @ 335am T. Richards pole #78539dc new teardrop fixtur installed not turned over yet | High Pressure Sodium | 38.86758817000 | -76.95639801000
7/11/11 | 1060226 | 3356 | PENNSYLVANIA AVE | SE |  | 78538DC | 7E121DC | (Light out) | DA 7-14-11 @ 335am T. Richards pole #78538dc new teardrop fixtur installed not turned over yet | High Pressure Sodium | 38.86749330000 | -76.95617036000
| 1060192 | 2801 | ALLENDALE PL | NW | 7/12/11 | 30001DC | 3A362DC | (Light out) | DA 7-12-11 @ 205am K. dunton repaired pole #30001dc Alley 11-00209030-wooden pole cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.94852561000 | -77.05516647000
7/7/11 | 1060016 | 3200 | SHERMAN AVE | NW | 7/13/11 | 12868 | 1L270 | (Light out) | Refer to W.O. 1055719 DA 7-13-11 @ 240am C. Ashton pole #12868 N/C underground Front 11-00206209- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93019378000 | -77.02654196000
7/6/11 | 1059935 | 4400 | GEORGIA AVE | NW | 7/12/11 | 4K024 | 4G309 | (Light dim) | DA 7-11-11 @ 140am R. Warren repaired pole #4k024 | High Pressure Sodium | 38.94410262000 | -77.02599601000
7/6/11 | 1059930 | 900 | 3RD ST | SE | 7/11/11 | 67530 | 6A454 | (Light out) | 7-11-11 Hudson/Jason - wires pulled out of pole due to new 16' pole being installed already energized (VW) DA 7-11-11 @ 1215am t. Richards pole #67530 N/C Underground - No wire Underground (pole May be geting removed due to new poles recently installe | High Pressure Sodium | 38.87919095000 | -77.00197695000
7/6/11 | 1059906 | 3813 | GEORGIA AVE | NW | 3/29/12 | 4J356 | 4G254 | (Light out) | 7-13-11 Hudson/Jason - found wire burnt off - rodded duct and scoped wire - found break 5'from MH, 19' from base -cut wires to make area safe drew illustration -REFER to construction (VW) DA 7-11-11 @ 350am R. WArren pole #4j356 N/C Underground - 0 v | High Pressure Sodium | 38.93795290000 | -77.02466878000
7/6/11 | 1059903 | 4503 | 13TH ST | NW | 7/11/11 | 4K424 | 4U135 | (Light out) | DA 7-11-11 @ 106amm R. Warren repaired pole #4K424 | High Pressure Sodium | 38.94516217000 | -77.02962224000
7/5/11 | 1059799 | 1000 | NEW YORK AVE | NW | 7/6/11 | 22912 | 2L064 | (Light out) | DA 7-6-11 @ 220am C. aShton repaired pole #22912 | High Pressure Sodium | 38.90130097000 | -77.02614564000
7/5/11 | 1059748 | 3200 | SHERMAN AVE | NW | 7/6/11 | 12868 | 1L270 | (Light out) | Refer to W.O. 1055719 DA 7-6-11 @ 250am K. Simmons pole #12868 N/C Underground -Alley- 11-00201712 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93019378000 | -77.02654196000
7/3/11 | 1059719 | 1435 | NEWTON ST | NW | 7/7/11 | 13913 | 1G072 | (Light out) | DA 7-7-11 @ 355am K. Dunton pole #13912 light is on and working 11-00201135 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93143118000 | -77.03279918000
| 1059660 | 1506 | TOBIAS DR | SE | 7/4/11 | 81795 | 88072 | (Light out) | DA 7-3-11 @ 1032pm K. Simmons repaired pole #81795 Front 11-00197765 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85006986000 | -76.98182599000
6/30/11 | 1059575 | 2418 | 18TH ST | NW | 7/1/11 | 11531 | 1G485 | (Light out) | Same as W.O.1058012 DA 7-1-11 @ 321am K. Simmons pole #11531 N/C Underground - 0 volts | High Pressure Sodium | 38.92129769000 | -77.04231632000
6/30/11 | 1059554 | 300 | 2ND ST | SW | 7/3/11 | 21596 | 6A367 | (Light out) | DA 7-3-11 @ 1010pm C ,AShton repaired pole #21596 | High Pressure Sodium | 38.88535568000 | -77.01355056000
6/29/11 | 1059496 | 2702 | WISCONSIN AVE | NW | 7/4/11 | 30175 | 3G030 | (Light out) | DA 7-4-11 @ 1224am R .Warren repaired pole #30175 | High Pressure Sodium | 38.92501826000 | -77.07307257000
6/29/11 | 1059461 | 33 | PATTERSON ST | NE |  | 61267 | 6U241 | (Light out) | 7-8-11 No SL feed, Secondary or Primary SL Man holes - REFER to DDOt - to resolve problem WCS construction is responsible for lights in work zone 7-8-11 waiting on Wayne Rickard to get in contact with the contractor DA 6-30-11 @ 425am T. Richards pol | High Pressure Sodium | 38.90640945000 | -77.00861364000
6/29/11 | 1059453 | 800 | 11TH ST | NE | 1/26/12 | 68604 | 6S174 | (Light out) | DA 6-30-11 @ 1250am T .Richards not our light - new light 3rd party refer to Ddot | High Pressure Sodium | 38.90029795000 | -76.99137671000
6/28/11 | 1059360 | 0 | BRANDYWINE ST | NW | 7/6/11 | 3A230DC | 3A230 | (Light off/on) | DA 7-6-11 @ 1115pm K. Dunton pole #3a230dc light is on and working DA 7-4-11 @ 345am R> Warren repaired pole #3a230dc | High Pressure Sodium | 38.94974018000 | -77.08081828000
6/28/11 | 1059324 | 0 | 7TH ST | NW | 7/1/11 | 22452 | 6M651 | (Light out) | DA 7-1-11 @ 340am C >aShton repaired pole #22452 Front 11-00194903 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89955549000 | -77.02182020000
6/28/11 | 1059297 | 0 | U ST | NW | 6/29/11 | 13288 | 1G548 | (Light out) | DA 6-29-11 @ 304am K .Simmons repaired pole #13288 | High Pressure Sodium | 38.91691836000 | -77.02612231000
6/27/11 | 1059292 | 3200 | SHERMAN AVE | NW | 7/5/11 | 12868 | 1L270 | (Light out) | Same as W.O.1055719 DA 6-30-11 @ 1200am K. Simmons pole #12868 N/C Underground - 0 volts South bound 11-00194653 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93019378000 | -77.02654196000
6/27/11 | 1059221 | 1409 | LAWRENCE ST | NE | 6/28/11 | 52486DC | 5A157DC | (Light out) | DA 6-28-11 @ 101am K. Simmons repaired pole #52486dc | High Pressure Sodium | 38.93177342000 | -76.98574118000
6/27/11 | 1059210 | 3318 | O ST | NW | 7/1/11 | 21104 | 2G167 | (Light out) | DA 7-1-11 @ 1245am C. Ashton repaired pole #21104 | High Pressure Sodium | 38.90783844000 | -77.06675984000
6/26/11 | 1059157 | 100 | 3RD ST | SE | 6/27/11 | 6A002 | 6A002 | (Light out) | DA 6-27-11 @ 410am T> Richards repaired pole #6A002 | Incandescent | 38.87703665000 | -77.00445216000
6/26/11 | 1059151 | 1000 | NEW YORK AVE | NW | 4/13/12 | 22948 | 2L032 | (Light out) | 7-8-11 Darryl Dixon - bad nuetral - Traffic combo pole w/common duct REFER to DDOT(vw) DA 6-26-11 @ 1032pm C .,Ashton pole #22948 - Neutrial underground has current and burnt up needs new underground feed | High Pressure Sodium | 38.90132896000 | -77.02684244000
6/26/11 | 1059146 | 0 | 8TH ST | NW | 1/24/12 | 22981 | 2M388 | (Light out) | DA 6-27-11 @ 1040pm C, Ashton pole #22981 Tardrop fixture not on list refer to Ddot | High Pressure Sodium | 38.90076702000 | -77.02288069000
6/22/11 | 1058990 | 2206 | 18TH ST | NW | 6/27/11 | 11411 | 1G502 | (Light out) | DA 6-27-11 @ 354am K> Simmons pole #11411 N/C underground - 0 volts 60' #8 Bare Copper 120' #10 Cable 4#8 Copper butt splices 1#12 Lng Tape D. Dixon 06/27/2011 | High Pressure Sodium | 38.91905896000 | -77.04152631000
6/22/11 | 1058989 | 2418 | 18TH ST | NW | 6/30/11 | 11531 | 1G485 | (Light out) | Same as W.O. 1058012 DA 6-28-11 @ 344am K. Simmons pole #11531 N/C underground - bare neutrial and no hot wire underground 6-23-11 Darryl/B Woodland unable to access due to construction in area (VW) | High Pressure Sodium | 38.92129769000 | -77.04231632000
6/22/11 | 1058928 | 3400 | P ST | NW | 6/23/11 | 21008 | 2G133 | (Light out) | DA 6-23-11 @ 335am C. AShton pole #21008 light is on and working 6-22-11 Darryl Dixon - pulled new wire from MH to fixture - no ground in MH - need cover for base installed 150 hps kit, lamp, NWP, 100 #10 wire, 80' #8 bare copper & 1 #8 cbs (VW) DA 6 | High Pressure Sodium | 38.90870135000 | -77.06807646000
6/22/11 | 1058917 | 3709 | NEWARK ST | NW | 6/22/11 | 38995DC | 3U392 | (Light out) | DA 6-22-11 @ 240am K. Dunton repaired pole #38995dc | High Pressure Sodium | 38.93463018000 | -77.07313515000
6/22/11 | 1058914 | 3709 | NEWARK ST | NW | 6/22/11 | 38994DC | 3U394 | (Light out) | DA 6-22-11 @ 230am K. Dunton repaired pole #38994dc | High Pressure Sodium | 38.93488284000 | -77.07368761000
6/21/11 | 1058885 | 900 | 4TH ST | SE | 6/22/11 | 67536 | 6A429 | (Light out) | 6-22-11 V Ham/Al JOhnson - light located in work zone (VW) | High Pressure Sodium | 38.87918965000 | -77.00064880000
6/21/11 | 1058881 | 457 | MASSACHUSETTS AVE | NW | 6/22/11 | 60481 | 6A195 | (Light out) | 6-22-11 AL Johnson/V Ham -pole has not been turned over to Chester yet (VW) | High Pressure Sodium | 38.90073307000 | -77.01753805000
6/21/11 | 1058864 | 1301 | 20TH ST | NW | 6/22/11 | 24830 | 2A017 | (Light out) | DA 6-22-11 @ 1215am C. AShton pole #24830 light found on and working bulb daed and good NW Corner 11-00186789- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90756285000 | -77.04480461000
6/21/11 | 1058835 | 2218 | WISCONSIN AVE | NW | 6/21/11 | 30161 | 3G086 | (Light out) | DA 6-21-11 @ 320am C .aShton repaired pole #30161 | High Pressure Sodium | 38.91961236000 | -77.07085524000
6/20/11 | 1058725 | 2611 | POMEROY RD | SE | 6/20/11 | 81350DC | 8U661 | (Light out) | DA 6-20-11 @ 1042pm K. Simmons repaired pole #81350dc | High Pressure Sodium | 38.85565774000 | -76.99249822000
6/20/11 | 1058679 | 3200 | SHERMAN AVE | NW | 6/21/11 | 12868 | 1L270 | (Light out) | Refer to W.O.1055719 5-17-11 Damien/Young - breakdown REFER to construction - light works -temp- (VW) DA 6-21-11 @ 210am C .ashton pole #12868 N/C Underground - neutrial needs grounded West Side11-00184397-the streetlight in front of 3212 sherman av | High Pressure Sodium | 38.93019378000 | -77.02654196000
6/20/11 | 1058659 | 1200 | 11TH ST | SE | 6/20/11 | 67740 | 6L938 | (Light out) | 6-17-11 Frank/Ronnie - installed TLP 400hps lamp (VW) | High Pressure Sodium | 38.87633690000 | -76.99165150000
6/18/11 | 1058589 | 5730 | UTAH AVE | NW | 1/25/12 | 4B242DC | 4B242 | (Light out) | DA 6-20-11 @ 1252am R. Warren repaired pole #4b242dc Side 11-00184217-A new light pole was installed last year across the street. Now there are two light fixtures (one new, the other one old attached to an utility pole). I am requesting that the old one | Mercury Vapor | 38.96701403000 | -77.06072007000
6/17/11 | 1058555 | 0 | MONROE ST | NE | 6/17/11 | 56155DC | 5U724 | (Light out) | DA 6-17-11 @ 401am K. Simmons repaired pole #56155dc | High Pressure Sodium | 38.93229394000 | -76.99724081000
6/16/11 | 1058496 | 1435 | NEWTON ST | NW | 6/17/11 | 13913 | 1G072 | (Light out) | DA 6-17-11 @ 205am C .aShton pole #13913 light is on and working 11-00180294-PLEASE REPLACE LIGHT BULB cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93143118000 | -77.03279918000
6/15/11 | 1058467 | 0 | K ST | SE |  | 67658 | 6A445 | (Light out) | 6-17-11 @ 410am T .Richards pole #67658 N/C underground / Construction area buildign new houseing complex (EWA) no con. info 6-16-11 Greg Edwards/G Smith - intersection under construction by others (VW) | High Pressure Sodium | 38.87835686000 | -77.00087371000
6/15/11 | 1058458 | 0 | 7TH ST | NW | 1/24/12 | 22430 | 2A186 | (Light out) | DA 6-16-11 @ 1220am C. AShton pole #22430 refer to Ddot teardrop fixture not on list | High Pressure Sodium | 38.89710115000 | -77.02201609000
6/15/11 | 1058412 | 0 | 12TH ST | NW | 6/15/11 | 13984 | 1G536 | (Light out) | DA 6-15-11 @ 320am C. AShton repaired pole #13984 | High Pressure Sodium | 38.91686452000 | -77.02815086000
6/14/11 | 1058281 | 2811 | PENNSYLVANIA AVE | SE |  | 78569DC | 7E084DC | (Light out) | DA 6-16-11 @ 1225am T. Richards pole #78569dc New teardrop refer to Ddot 6-15-11 Ronnie Fike - Ft Myers contractor (VW) | High Pressure Sodium | 38.87190486000 | -76.96697603000
6/14/11 | 1058263 | 2407 | 18TH ST | NW | 6/14/11 | 11533 | 1G491 | (Light out) | DA 6-14-11 @ 310am C> Ashton repaired pole #11533 adjusted TLPC | High Pressure Sodium | 38.92063969000 | -77.04213470000
6/13/11 | 1058184 | 900 | UPSHUR ST | NW | 6/13/11 | 4J744 | 4G330 | (Light out) | DA 6-13-11 @ 406am R. Warren repaired pole #4j744 | High Pressure Sodium | 38.94182164000 | -77.02494834000
6/10/11 | 1058050 | 232 | CARROLL ST | NW | 6/10/11 | 4H568DC | 4H568 | (Light out) | 6-10-11 Ronnie/Woodland - reattached power door plug (VW) | High Pressure Sodium | 38.97499707000 | -77.01542228000
6/9/11 | 1058012 | 2418 | 18TH ST | NW | 8/8/11 | 11531 | 1G485 | (Light out) | DA 8-8-11 @ 1250am K. Dunton pole #11531 light is on and working J. Lancaster completed on 8-5-11. Installed 130 FT of number 10# cable and one manhole frame and cover. K. Greenfield on 6-30-11. (Surface Cut) 6-14-11 Darryl Dixon - Breadown - REFER t | High Pressure Sodium | 38.92129769000 | -77.04231632000
6/9/11 | 1058008 | 3200 | SHERMAN AVE | NW | 6/10/11 | 12868 | 1L270 | (Light out) | Refer to W.O.1055719 5-17-11 Damien/Young - breakdown REFER to construction - light works -temp- (VW) DA 6-10-11 @ 150am K .Dunton pole #12868 N/C Underground - 0 volts | High Pressure Sodium | 38.93019378000 | -77.02654196000
6/9/11 | 1057937 | 1435 | NEWTON ST | NW | 6/10/11 | 13913 | 1G072 | (Light out) | DA 6-10-11 @ 115am K. Dunton repaired pole #13913 Front 11-00171704- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93143118000 | -77.03279918000
6/8/11 | 1057884 | 3712 | HAYES ST | NE |  | 72375DC | 7A505 | (Light out) | 6-8-11 Keith/Chris -- REFER to Richard- two fuses are open from PEPCO transformer on pole causing all lights to be out (VW) DA 6-8-11 @ 324am T> Richards pole #72375dc N/C To Overhead - Open Neutrial | High Pressure Sodium | 38.90389671000 | -76.95126641000
6/8/11 | 1057883 | 3722 | HAYES ST | NE |  | 72374DC | 7A503 | (Light out) | 6-8-11 Keith/Chris - REFER to Richard-two fuses are open from PEPCO transformer on pole causing all lights to be out (VW) DA 6-8-11 @ 324am T> Richards pole #72374dc N/C To Overhead - Open Neutrial | High Pressure Sodium | 38.90352892000 | -76.95082496000
6/7/11 | 1057859 | 3614 | GEORGIA AVE | NW | 6/7/11 | 12967 | 1G216 | (Light out) | DA 6-7-11 @ 1030pm C .ashton repaired pole #12967 | High Pressure Sodium | 38.93461487000 | -77.02416127000
6/7/11 | 1057858 | 3532 | GEORGIA AVE | NW | 6/7/11 | 12969 | 1G210 | (Light out) | DA 6-7-11 @ 1015pm C Ashton repaired pole #12969 | High Pressure Sodium | 38.93411676000 | -77.02407525000
6/7/11 | 1057782 | 236 | RHODE ISLAND AVE | NW | 6/8/11 | 59993 | 5A185 | (Light out) | DA 6-8-11 @ 315am K. Simmons repaired pole #59993 Block 11-00169148- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91439745000 | -77.01561600000
6/5/11 | 1057638 | 900 | UPSHUR ST | NW | 6/8/11 | 4J744 | 4G330 | (Light out) | DA 6-7-11 @ 200mm R. Warren pole #4j744 refer to day crew - temp wires | High Pressure Sodium | 38.94182164000 | -77.02494834000
6/5/11 | 1057618 | 1827 | WILTBERGER ST | NW | 6/8/11 | 29507 | 1M014 | (Light out) | 6-8-11 REFER to W/O 1053311 DA 6-7-11 @ 1100pm C. Ashton pole #29507 N/C @ Base - 0 Volts 6-6-11 AL Johnson - unable to service due to construction area (VW) | High Pressure Sodium | 38.91496601000 | -77.02091840000
6/2/11 | 1057502 | 1100 | 3RD ST | SE | 6/9/11 | 68140 | 6A471 | (Light out) | DA 6-9-11 @ 324am T. Richards pole #68140 light is on and working DA 6-6-11 @ 1136pm T. Richards repaired pole #68140 ( short cap) DA 6-6-11 @ 1254am T Richards - Bad address | High Pressure Sodium | 38.87742931000 | -77.00197636000
6/2/11 | 1057480 | 0 | ADAMS MILL RD | NW | 6/3/11 | 10279 | 1A037 | (Light out) | Refer to w.o.1055722 5-11-11 Hudson - pumped volt - unable to find SL wire in volt - rodded duct - stop at base of pole 3' in REFER back to construction - no fixture on pole DA 6-3-11 @ 1225am C. Ashton pole #10279 low voltage suggest underground crews | High Pressure Sodium | 38.92930708000 | -77.04392190000
6/2/11 | 1057474 | 4200 | 13TH ST | NW | 6/3/11 | 4J609 | 4U151 | (Light out) | 6/3/2011 Fike/Crockett - Replaced 150w hps lamp and photocell | High Pressure Sodium | 38.94196034000 | -77.02962652000
5/30/11 | 1057157 | 2500 | SHERIDAN RD | SE | 6/1/11 | 81355DC | 8U651 | (Light out) | DA 6-1-11 @ 1125pm K. Simmons repaired pole #81355dc | High Pressure Sodium | 38.85700461000 | -76.99333460000
| 1057089 | 5214 | NANNIE HELEN BURROUGHS AVE | NE | 1/26/12 | 72646 | 7A198 | (Light out) | DA 5-30-11 @ 1130pm T .Richards pole #72646 is in construction zone could not access due to Jersey wall blocking access installed red and white tape refer to Ddot 11-00156173- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89827561000 | -76.92455911000
5/26/11 | 1057075 | 0 | L ST | SE | 1/24/12 | 67701 | 6A438 | (Light out) | DA 5-31-11 @ 306am T. Richards pole #67701- #3rd party contractor refer to Ddot | High Pressure Sodium | 38.87758258000 | -77.00088038000
5/26/11 | 1056988 | 3400 | O ST | NW | 5/26/11 | 21100 | 2G166 | (Light out) | DA 5-25-11 @ 1145pm C, Ashton repaired pole #21100 | High Pressure Sodium | 38.90771415000 | -77.06801859000
| 1056969 | 3311 | P ST | NW | 5/26/11 | 21013 | 2G138 | (Light out) | DA 5-25-11 @ 1120pm C. Ashton repaired pole #21013 closer to 33rd Street, NW 11-00153277- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90883614000 | -77.06643273000
5/25/11 | 1056950 | 1000 | M ST | SE | 5/26/11 | 67376 | 6L940 | (Light out) | 5-26-11 Ronnie/Frank - installed 400hps lamp & PC (VW) | High Pressure Sodium | 38.87660025000 | -76.99171847000
5/24/11 | 1056838 | 1101 | BRENTWOOD RD | NE | 6/3/11 | 56627DC | 5A243 | (Light out) | Pole tag is inside t-base. 5-27-11 Damien/Young - newly installed metal pole 12' - pole tag need to be transfered (VW) DA 5-26-11 @ 259am K. Simmons pole #56627dc - there is just a pole @ this location no arm. fixture or anything | High Pressure Sodium | 38.91905056000 | -76.99181423000
5/24/11 | 1056780 | 1000 | NEW YORK AVE | NW | 6/3/11 | 22948 | 2L032 | (Light out) | Da 5-26-11 @ 330am C. Ashton pole #22948 light is on and working 90 volts HN, 91 HG DA 5-6-11 refer to wo #1055700 Complete DA 5-24-11 @ 200am C .AShton pole #22948 N/C low voltage - 97volts HG, 97volts HN and 0volts NG - light has new wire and fixture | High Pressure Sodium | 38.90132896000 | -77.02684244000
5/23/11 | 1056749 | 900 | K ST | SE | 5/24/11 | 67675 | 6U345 | (Light out) | DA 5-24-11 @ 1206am T. Richards secured T Base Door pole #67675 11-00150442-Numerous streetlights have no/missing/ panels at the base of the lights and internal wires are exposed. The street lights are the older lights (silver color - not black) along | High Pressure Sodium | 38.87846883000 | -77.00757395000
5/22/11 | 1056653 | 5524 | SOUTHERN AVE | SE | 5/23/11 | 75510 | 75510DC | (Light out) | 5-23-11AL Young - installed 400hps lamp (VW) | High Pressure Sodium | 38.88359254000 | -76.92141921000
| 1056611 | 1512 | TOBIAS DR | SE | 5/23/11 | 81714 | 87991 | (Light out) | DA 5-23-11 @ 216am K. Simmons repaired pole #81714 Alley 11-00147874-alley light out at this location....please repair cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.85019660000 | -76.98144001000
5/19/11 | 1056545 | 1512 | TOBIAS DR | SE | 5/19/11 | 81714 | 87991 | (Light out) | DA 5-19-11 @ 1023pm K. Simmons repaired pole #81714 | High Pressure Sodium | 38.85019660000 | -76.98144001000
5/19/11 | 1056510 | 0 | WASHINGTON AVE | SW | 5/19/11 | 21666 | 6A385 | (Light out) | DA 5-19-11 @ 355am C. aShton repaired pole #21666 lef side | High Pressure Sodium | 38.88613925000 | -77.01249287000
5/18/11 | 1056432 | 1100 | 3RD ST | SE |  | 68140 | 6A471 | (Light out) | 5-19-11 Frank/Ronnie - installed PC & 400hps lamp (VW) | High Pressure Sodium | 38.87742931000 | -77.00197636000
5/18/11 | 1056431 | 0 | L ST | SE | 5/19/11 | 67701 | 6A438 | (Light out) | 5-19-11 Frank/Ronnie - installed 400w hps lamp (VW) | High Pressure Sodium | 38.87758258000 | -77.00088038000
5/18/11 | 1056430 | 300 | I ST | SE | 5/19/11 | 67652 | 6A428 | (Light out) | 5-19-11 Frank/Ronnie - installed 150hps lamp (VW) | High Pressure Sodium | 38.87923404000 | -77.00083843000
5/18/11 | 1056427 | 1000 | M ST | SE |  | 67367 | 6L939 | (Light out) | REFER to WO #1052191 DA 5-19-11 @ 344am T. richards pole #67367 N/C Underground - 0 volts | High Pressure Sodium | 38.87641377000 | -76.99123690000
5/16/11 | 1056218 | 0 | H ST | NE | 1/26/12 | 62340 | 6S187 | (Light out) | DA 5-17-11 @ 334am T. Richards pole #62340 Temp pole refer to Ddot | High Pressure Sodium | 38.90029917000 | -76.99390863000
5/16/11 | 1056217 | 1308 | H ST | NE | 1/26/12 | 62330 | 6S154 | (Light out) | DA 5-17-11 @ 348am T. Richards pole #62330 Temp pole refer to Ddot | High Pressure Sodium | 38.90029744000 | -76.98780787000
5/16/11 | 1056215 | 0 | H ST | NE | 1/26/12 | 62327 | 6S140 | (Light out) | DA 5-17-11 @ 400am T .Richards pole #62327 Temp pole refer to ddot | High Pressure Sodium | 38.90029795000 | -76.98565875000
5/13/11 | 1056140 | 0 | NEW HAMPSHIRE AVE | NW | 5/17/11 | 23850 | 2G760 | (Light out) | DA 5-17-11 @ 125am C .Ashton pole #23850 light is on and working previously repaired NE Corner 11-00139698-(accross the street from address at the Duke Ellington Park island) T-base is missing the access panel. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90716866000 | -77.04587425000
| 1056142 | 2000 | M ST | NW | 5/16/11 | 23722 | 2A077 | (Light out) | DA 5-16-11 @ 120am C .Ashton installed T Base Door pole #23722 Front 11-00139731-t-base is missing access panel. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90574768000 | -77.04540447000
5/13/11 | 1056136 | 0 | NEW HAMPSHIRE AVE | NW | 5/16/11 | 23850 | 2G760 | (Light out) | DA 5-16-11 @ 135am C .AShton installed T Base door pole #23850 NW Corner 11-00139684-t-base is missing access panel cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90716866000 | -77.04587425000
5/10/11 | 1055954 | 0 | 13TH ST | NW | 5/15/11 | 4K415 | 4U118 | (Light out) | BCM - C. FREEBURGER - LIGHT IS ON DA 5-12-11 @ 405am R> Warren repaired pole #4k415 | High Pressure Sodium | 38.94728139000 | -77.02961900000
5/10/11 | 1055895 | 0 | NEW YORK AVE | NE | 5/10/11 | 50004 | 5A038 | (Light out) | DA 5-10-11 @ 419am K. Simmons repaired pole #50004 | High Pressure Sodium | 38.91736785000 | -76.96929432000
5/10/11 | 1055894 | 0 | NEW YORK AVE | NE | 5/10/11 | 50011 | 5A045 | (Light out) | DA 5-10-11 @ 408am K. Simmons repaired pole #50011 | High Pressure Sodium | 38.91707776000 | -76.96424700000
5/10/11 | 1055892 | 0 | NEW YORK AVE | NE | 5/10/11 | 58770 | 5A047 | (Light out) | DA 5-10-11 @ 353am K. Simmons repaired pole #58770 | High Pressure Sodium | 38.91700054000 | -76.96267103000
5/10/11 | 1055891 | 1333 | NEW HAMPSHIRE AVE | NW | 5/23/11 | 24482 | 2G772 | (Light out) | DA 5-23-11 @ 250am C. Ashton pole #24482 light found okay 124v HG, 123v HN, 0v NG DA 5-10-11 @ 215am ran 120ft wire pole #24482 - N/C @ Base needs underground neturial and ground wire | High Pressure Sodium | 38.90845645000 | -77.04444043000
5/9/11 | 1055862 | 0 | K ST | NW | 5/10/11 | 22407 | 6A081 | (Light out) | DA 5-10-11 @ 1235am C. Ashton repaired pole #22407 SW Corner 11-00133497-Caller is requesting for the street light at this location to be repair... cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90260339000 | -77.02144707000
5/9/11 | 1055852 | 1100 | CONNECTICUT AVE | NW | 5/12/11 | 24537 | 2U557 | (Light out) | DA 5-12-11 @355am C. AShton repaired pole #24537 | High Pressure Sodium | 38.90429111000 | -77.04049306000
5/8/11 | 1055773 | 809 | INTERSTATE 295 | NE | 5/10/11 | 79474 | 7A138 | (Light out) | DA 5-10-11 @ 334am K. Simmons repaired pole #79474 | High Pressure Sodium | 38.88176234000 | -76.96414383000
5/8/11 | 1055759 | 0 | INTERSTATE 295 | SE | 5/10/11 | 82155 | 8L759 | (Light out) | DA 5-10-11 @ 1207am K. simmons repaired pole #82155 | High Pressure Sodium | 38.86418702000 | -76.99473194000
5/8/11 | 1055758 | 0 | KENILWORTH AVE | SE | 4/16/12 | 79497 | 7A150 | (Light out) | BCM - 5-8-2011 - NEED HELP TO MOVE JERSEY WALLS TO GET BOOM TRUCK IN ORDER TO PULL WIRE FROM HANDHOLD OF POLE. | High Pressure Sodium | 38.88456308000 | -76.96344581000
5/8/11 | 1055756 | 0 | NEW YORK AVE | NE | 5/9/11 | 50005 | 5A039 | (Light out) | DA 5-9-11 @ 320am K. Simmons repaired pole #50005 | High Pressure Sodium | 38.91734425000 | -76.96859446000
5/8/11 | 1055753 | 10 | G ST | NE | 5/20/11 | 68285 | 6U597 | (No current) | DA 5-20-11 @ 139am T. Richards pole #68285 light is on and working 5-9-11 D dixon - no feed wire between MH & T-Base - pulled new cable 125' # 10 4-#8 cbs & tape (VW) | High Pressure Sodium | 38.89884737000 | -77.00730725000
5/7/11 | 1055749 | 3200 | SHERMAN AVE | NW | 6/10/11 | 12868 | 1L270 | (Light out) | Refer to W.O.1055719 5-17-11 Damien/Young - breakdown REFER to construction - light works -temp- (VW) 5-20-11 Darryl/Chris -NEED MOT MH in middle of street (VW) 5-17-11 Damien/Young - REFER to W/O #1055719 same pole - (VW) DA 5-12-11 @ 1125 | High Pressure Sodium | 38.93019378000 | -77.02654196000
5/6/11 | 1055722 | 0 | ADAMS MILL RD | NW | 8/30/11 | 10279 | 1A037 | (Light out) | 7-19-11 J Lancaster/M Patterson - installed 6 hotlinks 1-hanbox 20' # 10 cable (VW) 5-11-11 Hudson - pumped volt - unable to find SL wire in volt - rodded duct - stop at base of pole 3' in REFER back to construction - no fixture on pole (VW) DA | High Pressure Sodium | 38.92930708000 | -77.04392190000
5/6/11 | 1055719 | 3200 | SHERMAN AVE | NW | 9/18/11 | 12868 | 1L270 | (Light out) | J. Lancaster completed on 9-17-11. Installed 2FT of conduit, 120 FT of No#10 cable and made splices inside manhole. | High Pressure Sodium | 38.93019378000 | -77.02654196000
5/6/11 | 1055694 | 1000 | NEW YORK AVE | NW | 5/26/11 | 22948 | 2L032 | (Light out) | Da 5-26-11 @ 330am C. Ashton pole #22948 light is on and working 90 volts HN, 91 HG DA 5-6-11 refer to wo #1055700 Complete DA 5-5-11 C .AShton upon arrival pole #22948 pole to ground reading 38 volts - ran wire - when left pole to ground reading 0 volt | High Pressure Sodium | 38.90132896000 | -77.02684244000
5/5/11 | 1055651 | 300 | 3RD ST | SW | 5/10/11 | 21553 | 6A350 | (Light out) | DA 5-10-11 @ 1010pm C. Ashton pole #21553 lightis on and working , bulb dated | High Pressure Sodium | 38.88545367000 | -77.01510975000
5/5/11 | 1055562 | 0 | SHERMAN AVE | NW | 4/16/12 | 12527 | 12503 | (Light out) | On 5-5-11. (Refer to DDOT) Streetlight and traffic are sharing the same conduit need to run new wires from manhole to t-base. DA 5-5-11 @ 305am R. Warren pole #12527 N/C Low current - 63 volts ground to bare neturial | High Pressure Sodium | 38.92696258000 | -77.02586411000
5/3/11 | 1055375 | 0 | K ST | NW | 5/4/11 | 22403 | 6A076 | (Light out) | DA 5-3-11 @ 1125pm C .Ashton repaired pole #22403 North Side 11-00125866- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90260529000 | -77.02008282000
5/3/11 | 1055373 | 0 | 7TH ST | NW | 5/3/11 | 25657 | 6U469 | (Light out) | DA 5-3-11 @ 410am C. Ashton repaired pole #25657 | High Pressure Sodium | 38.90912247000 | -77.02201738000
5/3/11 | 1055371 | 1911 | 7TH ST | NW | 5/3/11 | 13408 | 1A132 | (Light out) | DA 5-3-11 @ 340am C .Ashton repaired pole #13408 | High Pressure Sodium | 38.91592081000 | -77.02201748000
5/3/11 | 1055359 | 1000 | H ST | NW | 5/3/11 | 22618 | 2G962 | (Light out) | DA 5-3-11 @ 125am C. Ashton repaired pole #22618 | High Pressure Sodium | 38.89990719000 | -77.02660550000
5/3/11 | 1055358 | 0 | H ST | NW | 5/3/11 | 22622 | 2G972 | (Light out) | DA 5-3-11 @ 115am C. AShton repaired pole #22622 ( construction area) | High Pressure Sodium | 38.89990526000 | -77.02482158000
5/3/11 | 1055353 | 617 | K ST | NW | 5/3/11 | 22405 | 6A079 | (Light out) | DA 5-3-11 @ 1225am C >aShton repaired pole #22405 | High Pressure Sodium | 38.90260409000 | -77.02085120000
| 1055335 | 1000 | NEW YORK AVE | NW | 5/6/11 | 22948 | 2L032 | (Light out) | DA 5-6-11 @ 1030pm C. Ashton repaired pole #22948 left side twin light Front 11-00125159-on wooden pole cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90132896000 | -77.02684244000
5/2/11 | 1055329 | 3170 | BLADENSBURG RD | NE | 5/6/11 | 51230DC | 5A126DC | (Light out) | DA 5-6-11 @ 117am R. Warren repaired pole #51230dc | High Pressure Sodium | 38.92882531000 | -76.96080667000
5/2/11 | 1055327 | 3258 | 15TH PL | SE | 5/5/11 | 81753 | 88030 | (Light out) | N. Woodland 5/5/11 | High Pressure Sodium | 38.84756122000 | -76.98229152000
5/2/11 | 1055303 | 2800 | BLADENSBURG RD | NE | 5/5/11 | 50098 | 5A084 | (Light out) | AL YOUNG 5/5/11 | High Pressure Sodium | 38.92696727000 | -76.96279437000
5/1/11 | 1055243 | 1840 | 7TH ST | NW | 5/1/11 | 13410 | 1A129 | (Light out) | DA 5-1-11 @ 1040pm C .Ashton repaired pole #13410 | High Pressure Sodium | 38.91493095000 | -77.02201297000
5/1/11 | 1055234 | 0000 | MILITARY RD | NW | 5/3/11 | 4A001 | 4R210 | (Light out) | DA 5-3-11 @ 1258am R. Warren repaired pole #4A001 | High Pressure Sodium | 38.94895547000 | -77.02961274000
5/1/11 | 1055232 | 423 | KENNEDY ST | NW | 5/3/11 | 4M060 | 4M060DC | (Light off/on) | DA 5-3-11 @ 1206am R. Warren pole #4m060 light is on and working DA 5-2-11 @ 108am R Warren repaired pole #4m060 | High Pressure Sodium | 38.95655029000 | -77.01872469000
5/1/11 | 1055217 | 1700 | 3RD ST | NW | 5/4/11 | 59992 | 5A183 | (Light out) | DA 5-4-11 @ 1231am K. Simmons repaired pole #59992 | High Pressure Sodium | 38.91426862000 | -77.01583923000
5/1/11 | 1055202 | 1100 | 3RD ST | SE | 5/6/11 | 68140 | 6A471 | (Light out) | DA 5-4-11 @ 1228am T .Richards request for map | High Pressure Sodium | 38.87742931000 | -77.00197636000
5/1/11 | 1055201 | 300 | I ST | SE | 5/4/11 | 67652 | 6A428 | (Light out) | DA 5-3-11 @ 1135pm T. Richards repaired pole #67652 repaired loose connection in conversion kit | High Pressure Sodium | 38.87923404000 | -77.00083843000
5/1/11 | 1055200 | 200 | I ST | SE | 1/26/12 | 67650 | 6A426 | (Light out) | 5-18-11 Damien Smith - REFER to DDOT - Contractor is installing new poles - DDOT is aware of this situation (VW) DA 5-4-11 @ 1201am T. Richards pole #67650 N/C underground - 0 volts | High Pressure Sodium | 38.87923749000 | -77.00159557000
4/28/11 | 1055116 | 126 | 3RD ST | SE | 5/2/11 | 6A001 | 6A001 | (Light out) | DA 5-2-11 @ 128am t. Richards repaired pole #6A001 | Incandescent | 38.87684494000 | -77.00438348000
4/28/11 | 1055106 | 921 | 4TH ST | NE | 5/2/11 | 61438 | 6A299 | (Light out) | DA 5-2-11 @ 315am T. Richards repaired pole #61438 | High Pressure Sodium | 38.90192178000 | -77.00064462000
4/28/11 | 1055090 | 0 | WISCONSIN AVE | NW | 4/29/11 | 30180 | 3G006 | (Light out) | DA 4-29-11 @ 150am K .Dunton repaired pole #30180 | High Pressure Sodium | 38.92762077000 | -77.07306785000
4/28/11 | 1055073 | 1255 | NEW HAMPSHIRE AVE | NW | 4/29/11 | 23872 | 2G756 | (Light out) | DA 4-29-11 @ 150am C. AShton repaired pole #23872 | High Pressure Sodium | 38.90653518000 | -77.04624591000
4/28/11 | 1055063 | 1211 | CONNECTICUT AVE | NW | 5/2/11 | 27222 | 2U526 | (Light out) | DA 5-2-11 @ 155am C .AShton repaired pole #27222 | High Pressure Sodium | 38.90611590000 | -77.04122309000
4/28/11 | 1055034 | 7051 | SPRING PL | NW | 4/28/11 | 4H522DC | 4H522 | (Light out) | DA 4-28-11 @ 159am R .Warren repaired pole #4h522dc | Incandescent | 38.97614004000 | -77.01896257000
4/26/11 | 1054848 | 1400 | S ST | NW | 1/24/12 | 26184 | 2A080 | (Light out) | H. Lancaster on 4-27-11. Traffic combo pole setting on temp. foundation. DA 4-27-11 @ 1205am C. Ashton pole #26184 N/C Underground 0 volts (contruction in area) | High Pressure Sodium | 38.91415171000 | -77.03212341000
4/26/11 | 1054819 | 1300 | MAINE AVE | SW | 5/16/11 | 66532 | 6M444 | (Light out) | DA 4-29-11 @ 119am T. Richards pole #66532 N/C Underground - Damaged feed, wire is burnt in t base, wires to short to splice, needs new wire pulled from man hole DA 4-27-11 @ 351am T. Richards - Request for Map reconnected feed in base tnstalled groun | High Pressure Sodium | 38.88170964000 | -77.02793900000
4/26/11 | 1054801 | 0 | EASTERN AVE | NE | 4/28/11 | 52382DC | 5L703 | (Light out) | Michael Craig completed on 4-27-11. Installed 250 lens. DA 4-26-11 @ 1219am K. Simmons repaired pole #52382dc (needs cobra lens) | High Pressure Sodium | 38.93906027000 | -76.96826153000
4/25/11 | 1054710 | 0 | NEW YORK AVE | NE | 1/24/12 | 56832 | 5M053 | (Light out) | 5-3-11 Hudson/Jason - was unable to work in area due to Cherry Hill contractor working at site - Installing new SL. Durant G. Walters 410-799-2316 DA 4-25-11 @ 258am K. Dunton pole #56832 N/C Underground | High Pressure Sodium | 38.91324438000 | -76.99169504000
4/24/11 | 1054682 | 3230 | PENNSYLVANIA AVE | SE | 2/7/12 | 78549DC | 7E106 | (Light out) | DA 4-27-11 @ 323am T. richards installed red and white tape refer to ddot 3-30-11 REFER to DDOT - Fort Myers Construction working on new lights - not Severn responsibility | High Pressure Sodium | 38.86896025000 | -76.95979555000
4/24/11 | 1054673 | 3300 | PENNSYLVANIA AVE | SE | 2/2/12 | 78544DC | 7E115DC | (Light out) | DA 4-25-11 @ 405am K .Dunton pole #78544dc No access to light due to construction on pennsylvania Ave | High Pressure Sodium | 38.86824545000 | -76.95800685000
4/24/11 | 1054672 | 3300 | PENNSYLVANIA AVE | SE | 2/2/12 | 78544DC | 7E115DC | (Light out) | DA 4-25-11 @ 405am K .Dunton pole #78544dc No access to light due to construction on pennsylvania Ave | High Pressure Sodium | 38.86824545000 | -76.95800685000
4/24/11 | 1054671 | 3144 | PENNSYLVANIA AVE | SE | 4/25/11 | 78554DC | 7E101DC | (Light out) | DA 4-25-11 @ 400am K .Dunton pole #78554dc light is on and working | High Pressure Sodium | 38.86981292000 | -76.96183892000
4/24/11 | 1054670 | 3458 | PENNSYLVANIA AVE | SE | 2/2/12 | 78532DC | 7E127DC | (Light out) | DA 4-25-11 @ 405am K .Dunton pole #78532dc No access to light due to construction on pennsylvania Ave | High Pressure Sodium | 38.86670538000 | -76.95424005000
4/24/11 | 1054669 | 3458 | PENNSYLVANIA AVE | SE | 2/2/12 | 78531DC | 7E128DC | (Light out) | DA 4-25-11 @ 405am K .Dunton pole #78531dc No access to light due to construction on pennsylvania Ave. | High Pressure Sodium | 38.86657755000 | -76.95392452000
4/24/11 | 1054668 | 2000 | FORT DAVIS ST | SE | 4/25/11 | 78523DC | 7E142 | (Light out) | DA 4-25-11 @ 155am K .Dunton repaired pole #78523dc | High Pressure Sodium | 38.86502980000 | -76.95013502000
4/24/11 | 1054667 | 3935 | PENNSYLVANIA AVE | SE | 2/2/12 | 78519DC | 7E147DC | (Light out) | DA 4-25-11 @ 230am K .Dunton pole #78519dc No access to light due to construction on pennsylvania Ave. | High Pressure Sodium | 38.86423333000 | -76.94818049000
4/23/11 | 1054648 | 509 | KENNEDY ST | NW | 4/25/11 | 4M065 | 4M065DC | (Light out) | DA 4-25-11 @ 407am R .Warren installed t base door pole #4m065 11-00115153-T-Plate for streetlight in front of location is exposed. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.95650364000 | -77.02039698000
4/22/11 | 1054600 | 0 | EAST CAPITOL ST | NE | 4/22/11 | 63634 | 6M824 | (Light out) | DA 4-22-11 @ 206am T .Richards closed open lens pole #63634 | High Pressure Sodium | 38.89007149000 | -76.97454092000
| 1054565 | 509 | KENNEDY ST | NW | 4/25/11 | 4M065 | 4M065DC | (Light out) | DA 4-25-11 @ 407am R .Warren installed new t base door pole #4m065 refer to wo #1054648 11-00113602- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.95650364000 | -77.02039698000
4/21/11 | 1054553 | 300 | I ST | SE | 4/21/11 | 67652 | 6A428 | (Light out) | DA 4-21-11 @ 1048pm T. Richards repaired pole #67652 | High Pressure Sodium | 38.87923404000 | -77.00083843000
4/21/11 | 1054534 | 900 | UPSHUR ST | NW | 4/22/11 | 4J744 | 4G330 | (Light out) | DA 4-22-11 @ 1205am R .Warren pole #4j744 light is on and working | High Pressure Sodium | 38.94182164000 | -77.02494834000
4/21/11 | 1054533 | 832 | UPSHUR ST | NW | 4/22/11 | 4J745 | 4G332 | (Light out) | DA 4-22-11 @ 1205am R .Warren pole #4j745 light is on and working | High Pressure Sodium | 38.94182944000 | -77.02466826000
4/21/11 | 1054532 | 901 | VARNUM ST | NW | 4/22/11 | 4K190 | 4G320 | (Light out) | DA 4-22-11 @ 1214am R. Warren repaired pole #4k190 | High Pressure Sodium | 38.94289398000 | -77.02535229000
4/20/11 | 1054415 | 611 | 22ND ST | NW | 4/22/11 | 28290 | 2M437 | (Light out) | DA 4-21-11 @ 1225am C ,ashton pole 328290 pole is gone Completed on 4-21-11. Whiting turner Construction Company is going to install temp outside lighting in replacement of missing 28FT pole inside construction project. DA 4-21-11 @ 1240am C. Ashto | High Pressure Sodium | 38.89769965000 | -77.04891041000
4/19/11 | 1054261 | 4500 | EAST CAPITOL ST | SE | 4/16/12 | 70052 | 7A035 | (Light out) | DeVon Smith 7-13-09 Refer to Dc Traffic pole combo pole. DA 4-22-11 @ 1206am T. Richards pole #70052 N/C Underground traffic combo pole 4-20-11 AL Young - unable to locate pole not on SEC (VW) | High Pressure Sodium | 38.88960932000 | -76.93729068000
4/18/11 | 1054159 | 600 | MICHIGAN AVE | NE | 4/19/11 | 53649DC | 5U721 | (Light out) | DA 4-19-11 @ 1210am K Simmons repaired pole #53649dc | High Pressure Sodium | 38.93248081000 | -76.99750323000
4/18/11 | 1054156 | 806 | RHODE ISLAND AVE | NE | 4/19/11 | 56388DC | 5A274 | (Light out) | DA 4-18-1 @ 1138pm K .Simmons repaired pole #56388dc | High Pressure Sodium | 38.92176361000 | -76.99420034000
4/18/11 | 1054153 | 0 | MONROE ST | NE | 4/19/11 | 56158DC | 5U701 | (Light out) | DA 4-19-11 @ 1217am K. Simmons repaired pole #56158dc | High Pressure Sodium | 38.93224016000 | -76.99626172000
4/18/11 | 1054124 | 3400 | SHERMAN AVE | NW | 4/19/11 | 13070 | 1L297 | (Light out) | DA 4-19-11 @ 145am K. Dunton repaired pole #13070 | High Pressure Sodium | 38.93240466000 | -77.02663265000
4/17/11 | 1053994 | 18 | 3RD ST | SE | 4/18/11 | 6A003 | 6A003 | (Light out) | DA 4-18-11 # 331am T. Richards repaired pole #6a003 | Incandescent | 38.87723028000 | -77.00452085000
4/14/11 | 1053758 | 0 | 23RD ST | NW | 4/14/11 | 24656 | 2G673 | (Light out) | DA 4-13-11 @ 1150pm C. Ashton repaired pole #24656 | High Pressure Sodium | 38.90314639000 | -77.05003724000
4/12/11 | 1053593 | 4832 | NANNIE HELEN BURROUGHS AVE | NE | 4/14/11 | 71293DC | 7A223DC | (Light out) | DA 4-13-11 @ 1111pm T. Richards repaireed pole #71293dc DA 4-13-11 @ 325am K .Dunton one side of Nannie Helen is closed needs big boom to reach fixture | High Pressure Sodium | 38.89895905000 | -76.93289413000
4/11/11 | 1053479 | 1100 | 11TH ST | SE | 4/12/11 | 67613 | 6L941 | (Light out) | DA 4-12-11 @ 109am T Richards repaired pole #67613 | High Pressure Sodium | 38.87665520000 | -76.99137008000
4/10/11 | 1053413 | 0 | ANACOSTIA FWY | SE | 4/15/11 | 79482 | 7A151 | (Light out) | DA 4-14-11 @ 1045pm T .Richards repaired pole #79482 | High Pressure Sodium | 38.88927741000 | -76.95876088000
4/10/11 | 1053412 | 0 | ANACOSTIA FWY | SE | 4/25/11 | 79478 | 7A142 | (Light out) | DA 4-14-11 @ 1039pm T .Richards pole #79478 N/C Underground 0 Volts | High Pressure Sodium | 38.88446501000 | -76.96303530000
4/10/11 | 1053411 | 0 | OVERLOOK AVE | SW | 4/15/11 | 81840 | 88101 | (Light out) | DA 4-14-11 @ 1010pm T. Richards pole #81840 needs to be rebuilt @ Shop will return to reinstall | High Pressure Sodium | 38.83216740000 | -77.01463184000
4/10/11 | 1053397 | 0 | N ST | NW | 4/11/11 | 23794 | 2G762 | (Light out) | DA 4-11-11 @ 150am C .AShton repaired pole #23794 | High Pressure Sodium | 38.90721658000 | -77.04551420000
4/10/11 | 1053387 | 1840 | 7TH ST | NW | 4/11/11 | 13410 | 1A129 | (Light out) | 4-7-11 S Manning - replaced TLP (VW) | High Pressure Sodium | 38.91493095000 | -77.02201297000
4/10/11 | 1053386 | 1541 | 7TH ST | NW | 4/13/11 | 25702 | 6A814 | (Light off/on) | DA 4-13-11 @ 240am C. aShton pole #25702 light is on and working DA 4-11-11 @ 1045pm C. Ashton repaired pole #25702 | High Pressure Sodium | 38.91080483000 | -77.02182504000
4/8/11 | 1053311 | 1827 | WILTBERGER ST | NW | 6/23/11 | 29507 | 1M014 | (Light out) | J. Lancaster completed on 6-23-11 Installed 280FT of No#10 cable, one handbox, 140 FT of conduit and made splices inside manhole. | High Pressure Sodium | 38.91496601000 | -77.02091840000
4/5/11 | 1053026 | 3458 | PENNSYLVANIA AVE | SE | 2/7/12 | 78532DC | 7E127DC | (Light out) | DA 4-8-11 @ 250am T> Richard light has been referred to ddot DA 4-7-11 @ 134am T. Richards pole #78532dc new teardrop fixture installed on old pole not turned over yet | High Pressure Sodium | 38.86670538000 | -76.95424005000
4/5/11 | 1053008 | 2720 | WISCONSIN AVE | NW | 4/6/11 | 30138 | 3G023 | (Light out) | DA 4-6-11 @ 400am K. Dunton repaired pole #30138 | High Pressure Sodium | 38.92584443000 | -77.07330461000
3/31/11 | 1052726 | 2400 | SHERMAN AVE | NW | 1/23/12 | 12585 | 1G465 | (Light out) | DA 4-1-11 @ 415am K. Dunton pole #12585 no access to light part of the ongoing sherman ave project - road construction | High Pressure Sodium | 38.92169397000 | -77.02539372000
3/31/11 | 1052709 | 0 | K ST | NW | 4/1/11 | 24658 | 2G677 | (Light out) | DA 4-1-11 @ 1255am C .ashton repaired pole #24658 | High Pressure Sodium | 38.90256507000 | -77.04931783000
3/30/11 | 1052654 | 1748 | EAST CAPITOL ST | NE | 4/6/11 | 63712 | 6A501 | (Light out) | DA 4-6-11 @ 139am T .Richards pole #63712 light is on and working 4-5-11 Darryl Dixon - voltage tested 122volts at fixture (VW) DA 3-30-11 @ 1024pm T. Richards pole #63712 weak bare neturial underground | High Pressure Sodium | 38.88973040000 | -76.97991030000
3/30/11 | 1052577 | 1700 | R ST | NW | 3/31/11 | 26234 | 2M134 | (Light out) | DA 3-31-11 @ 215am C. Ashton repaired pole #26234 adjusted TLPC SE Corner 11-00088583-Streetlight on South East Corner of 18th and R St NW is inoperative. Pole ID: 26234 cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91256978000 | -77.04156816000
3/30/11 | 1052566 | 1300 | CONNECTICUT AVE | NW | 3/30/11 | 24529 | 2U503 | (Light out) | DA 3-30-11 @ 130am C .Ashton repaired pole #24529 | High Pressure Sodium | 38.90750360000 | -77.04239843000
3/29/11 | 1052525 | 617 | FERN PL | NW | 4/4/11 | 4D593DC | 4D893DC | (Light off/on) | DA 4-4-11 @ 1113pm R. Warren pole #4D593 light is on and working Metal pole DA 3-31-11 @ 152am R. Warren pole #4d593dc light is on but dim- refer to fault crew to check overhead wires and connections. | Incandescent | 38.97836084000 | -77.02287141000
3/29/11 | 1052477 | 900 | 4TH ST | SE | 1/26/12 | 67537 | 6A431 | (Light out) | 3-31-11 H Lancaster/Jason- contractors are installing new MH's and poles in area - feed to this pole is cut off and abandon (Eye Construction Co) no contact info (VW) DA 3-30-11 @ 324am T. Richards pole 367537 N/C Underground - (3rd party ? EYA) | High Pressure Sodium | 38.87890661000 | -77.00065113000
| 1052447 | 600 | 1ST ST | NE | 3/30/11 | 60930 | 6U604 | (Light out) | DA 3-30-11 @ 104am T. Richards repaired pole #60930 using 400 hps fixture refer to wo #1052262 11-00087035- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89760383000 | -77.00770399000
3/28/11 | 1052421 | 3600 | P ST | NW | 3/30/11 | 21002 | 2G125 | (Light out) | DA 3-30-11 @ 210am C. Ashton pole #21002 light is on and working DA 3-29-11 @ 115am C> Ashton pole #21002 light found on and working bulb dated 3-18-11 | High Pressure Sodium | 38.90864453000 | -77.07059706000
3/28/11 | 1052407 | 1748 | EAST CAPITOL ST | NE | 3/30/11 | 63712 | 6A501 | (Light dim) | DA 3-30-11 @ 1024pm T. Richards pole #63712 light is off DA 3-29-11 @ 1044pm T .Richards repaired pole #63712 | High Pressure Sodium | 38.88973040000 | -76.97991030000
3/28/11 | 1052402 | 18 | 3RD ST | SE | 3/29/11 | 6A003 | 6A003 | (Light out) | 3-29-11AL Young - installed 295 inc lamp (VW) | Incandescent | 38.87723028000 | -77.00452085000
3/27/11 | 1052330 | 4202 | 13TH ST | NW | 3/28/11 | 4K433 | 4U149 | (Light out) | DA 3-28-11 @ 231am R. Warren repaired pole #4k433 | High Pressure Sodium | 38.94238501000 | -77.02962392000
3/27/11 | 1052307 | 109 | 34TH ST | SE | 3/28/11 | 76504 | 76504DC | (Light out) | DA 3-28-11 @ 156am T. Richards repaired pole #76504 | High Pressure Sodium | 38.88863859000 | -76.95745535000
3/27/11 | 1052262 | 600 | 1ST ST | NE | 3/30/11 | 60930 | 6U604 | (Light out) | DA 3-30-11 @ 104am T. Richards repaired pole #60930 | High Pressure Sodium | 38.89760383000 | -77.00770399000
3/24/11 | 1052191 | 1000 | M ST | SE | 2/9/12 | 67367 | 6L939 | (Light out) | 4-5-11 Hudson/Jason - chk MH at p-base - was not able to find feed tried to rod duct - rod only went in 3' - traffic combo pole REFER to DDOT (VW) DA 3-30-11 @ 359am T. Richards pole #67367 N/C Underground 0 volts | High Pressure Sodium | 38.87641377000 | -76.99123690000
3/24/11 | 1052182 | 2300 | WASHINGTON CIR | NW | 3/25/11 | 28508 | 2G685 | (Light out) | DA 3-25-11 @ 130am C> aShton repaired pole #28508 | High Pressure Sodium | 38.90230813000 | -77.05085260000
3/24/11 | 1052142 | 1100 | 11TH ST | SE | 3/29/11 | 67613 | 6L941 | (Light out) | 3-29-11AL Young - installed 400hps lamp (VW) | High Pressure Sodium | 38.87665520000 | -76.99137008000
3/24/11 | 1052126 | 1909 | 14TH ST | SE | 3/24/11 | 80532 | 8M018 | (Light out) | DA 3-24-11 @ 1037pm K. Simmons repaired pole #80532 | High Pressure Sodium | 38.86632780000 | -76.98519170000
3/24/11 | 1052125 | 1909 | 14TH ST | SE | 3/25/11 | 80533 | 8M017 | (Light out) | DA 3-24-11 @ 1044pm K Simmons repaired pole #80533 | High Pressure Sodium | 38.86657133000 | -76.98511960000
3/22/11 | 1051987 | 0 | 13TH ST | NW | 3/24/11 | 4K430 | 4U144 | (Light out) | DA 3-24-11 @ 1259am R. Warren repaired pole #4k430 | High Pressure Sodium | 38.94357657000 | -77.02978724000
3/22/11 | 1051986 | 4400 | GEORGIA AVE | NW | 2/22/13 | 4K024 | 4G309 | (Light out) | 4-1-11 K Greenfield/S Manning - work zone - new poles being installed REFER to DDOT (VW) DA 3-24-11 2 1216am R. Warren pole #4k024 Bare Neturial inside pole - could not pull wire because of T base being half burried. | High Pressure Sodium | 38.94410262000 | -77.02599601000
3/22/11 | 1051957 | 1000 | NEW YORK AVE | NW | 3/28/11 | 22948 | 2L032 | (Light out) | DA 3-28-11 @ 1045pm C >Ashton repaired pole #22948 - respliced all wires in base now has 120volts @ base voth lights are on DA 3-24-11 @ 455am C .Ashton is going to recheck and repair pole #22948 this evening DA 3-23-11 @ 235am C. Ashton pole #22948 - 9 | High Pressure Sodium | 38.90132896000 | -77.02684244000
3/21/11 | 1051718 | 3458 | PENNSYLVANIA AVE | SE | 3/25/11 | 78532DC | 7E127DC | (Light out) | DA 3-25-11 @ 327am R. WArren repaired pole #78532dc | High Pressure Sodium | 38.86670538000 | -76.95424005000
3/21/11 | 1051717 | 3356 | PENNSYLVANIA AVE | SE | 3/25/11 | 78538DC | 7E121DC | (Light out) | DA 3-25-11 @ 318am R> Warren repaired pole #78538dc | High Pressure Sodium | 38.86749330000 | -76.95617036000
3/21/11 | 1051716 | 3230 | PENNSYLVANIA AVE | SE | 3/25/11 | 78549DC | 7E106 | (Light out) | DA 3-25-11 @ 305am R. Warren pole #78549dc N/C to overhead they are in the process of switching out pole | High Pressure Sodium | 38.86896025000 | -76.95979555000
3/21/11 | 1051715 | 3300 | PENNSYLVANIA AVE | SE | 2/7/12 | 78544DC | 7E115DC | (Light out) | 3-30-11 REFER to DDOT - Fort Myers Construction working on new lights - not Severn responsibility DA 3-25-11 @ 312am R> Warren pole #78544dc light has voltage of 186volts on 120circuit . light is off | High Pressure Sodium | 38.86824545000 | -76.95800685000
3/20/11 | 1051659 | 2407 | 18TH ST | NW | 3/24/11 | 11533 | 1G491 | (Light out) | DA 3-24-11 @ 325am C .AShton repaired pole #11533 3-23-11Al Young no access - Beef Frank Joy have the street blocked off (VW) | High Pressure Sodium | 38.92063969000 | -77.04213470000
3/20/11 | 1051641 | 0 | WISCONSIN AVE | NW | 3/22/11 | 30157 | 3G104 | (Light out) | DA 3-21-11 @ 1105pm K. Dunton repaired pole #30157 | High Pressure Sodium | 38.91800125000 | -77.06948371000
3/20/11 | 1051632 | 3222 | 14TH ST | NE | 3/21/11 | 51220DC | 5A114DC | (Light out) | 3-21-11 AL Young - 150 hps lamp (VW) | High Pressure Sodium | 38.93068379000 | -76.98625793000
3/20/11 | 1051595 | 0 | 7TH ST | NW | 3/21/11 | 13409 | 1M002 | (Light out) | DA 3-21-11 @ 1215am C. AShton repaired pole #13409 | High Pressure Sodium | 38.91546455000 | -77.02201750000
3/17/11 | 1051490 | 5800 | NANNIE HELEN BURROUGHS AVE | NE | 3/20/11 | 79661 | 72656 | (Light out) | DA 3-20-11 @ 1037pm T> Richards repaired pole #79661 | High Pressure Sodium | 38.89830700000 | -76.91763472000
3/17/11 | 1051461 | 3600 | P ST | NW | 3/18/11 | 21002 | 2G125 | (Light out) | DA 3-18-11 @ 225am C. Ashton repaired pole #21002 | High Pressure Sodium | 38.90864453000 | -77.07059706000
3/16/11 | 1051331 | 200 | W ST | NW | 3/22/11 | 13760 | 1U188 | (Light out) | 3-22-11 K Greenfield/Purnell - SAME as REFER to W/O #1051326 - installed 1 low voltage starter & made splices ist the main feed pole (VW) DA 3-20-11 @ 1040pm C .Ashton pole #13760 N/C Underground | High Pressure Sodium | 38.91949574000 | -77.01713787000
3/15/11 | 1051214 | 4200 | KANSAS AVE | NW | 3/17/11 | 4K570 | 4G318 | (Light out) | DA 3-16-11 @ 1152pm R. Warren repaired pole #4k570 | High Pressure Sodium | 38.94270247000 | -77.02543354000
3/15/11 | 1051194 | 900 | UPSHUR ST | NW | 3/17/11 | 4J744 | 4G330 | (Light out) | DA 3-16-11 @ 1128pm R. Warren repaired pole #4j744 | High Pressure Sodium | 38.94182164000 | -77.02494834000
3/15/11 | 1051193 | 4235 | 9TH ST | NW | 3/18/11 | 4K017 | 4G319 | (Light out) | 3-18-11 K Greenfielg/Purnell - new poles being installed by outside contractors (VW) DA 3-16-11 @ 1137pm R. Warren pole #4K017 N/C Underground | High Pressure Sodium | 38.94272297000 | -77.02520204000
3/14/11 | 1051064 | 0 | 4TH ST | SW | 3/14/11 | 21583 | 6L621 | (Light out) | DA 3-14-11 @ 335am C .AShton reattached globe and repaired pole #21583 | High Pressure Sodium | 38.88614980000 | -77.01743765000
3/9/11 | 1050814 | 3225 | PENNSYLVANIA AVE | SE | 2/7/12 | 78589 | 7E044 | (Light out) | DA 3-14-11 @ 333am T. Richards temp pole refer to Ddot | High Pressure Sodium | 38.86945735000 | -76.96055314000
3/9/11 | 1050807 | 5573 | SOUTHERN AVE | SE | 3/14/11 | 75511 | 75511DC | (Light out) | DA 3-14-11 @ 231am T. Richards repaired pole #75511 | High Pressure Sodium | 38.88389291000 | -76.92103667000
3/8/11 | 1050712 | 3500 | P ST | NW | 3/9/11 | 21005 | 2G130 | (Light out) | DA 3-9-11 @ 120am C. Ashton repaired pole #21005 | High Pressure Sodium | 38.90876207000 | -77.06960266000
3/8/11 | 1050663 | 900 | UPSHUR ST | NW | 2/9/12 | 4J743 | 4G313 | (Light out) | 3-9-11 Al Young - REFER to DDOT Tempory pole Traffic combo pole set up by MC Dean tempory foundation (VW) DA 3-8-11 @ 1156pm R. Warren pole #4j743 N/C Underground - Temp pole | High Pressure Sodium | 38.94182528000 | -77.02576756000
3/8/11 | 1050662 | 900 | UPSHUR ST | NW | 3/9/11 | 4J744 | 4G330 | (Light out) | DA 3-8-11 @ 1150pm R. Warren pole #4J744 light found on nad working | High Pressure Sodium | 38.94182164000 | -77.02494834000
3/8/11 | 1050635 | 0 | 11TH ST | NW | 3/10/11 | 23377 | 2L023 | (Light out) | DA 3-10-11 @ 1020pm C .Ashton pole #23377 light is on and working DA 3-9-11 @ 345am C> Ashton pole #23377 N/C @ base North Side 11-00064098-Please repair a streetlight where both lights are dark. The streetlight is in the 800 block of 11th Street, N | High Pressure Sodium | 38.90046875000 | -77.02690544000
3/8/11 | 1050630 | 1301 | U ST | NW | 3/8/11 | 11721 | 1G521 | (Light off/on) | DA 3-8-11 @ 415am K. Dunton repaired pole #11721 | High Pressure Sodium | 38.91709342000 | -77.03069626000
3/6/11 | 1050503 | 600 | 1ST ST | NE | 3/8/11 | 60930 | 6U604 | (Light out) | DA 3-8-11 @ 1114pm T. Richards repaired pole #60930 | High Pressure Sodium | 38.89760383000 | -77.00770399000
3/6/11 | 1050498 | 422 | K ST | NW | 9/12/11 | 60465 | 6A123 | (Light out) | 9-12-11 Marvin - completed restoration (VW) 3-9-11 D Dixon - BREAKDOWN - unable to rod REFER to construction (VW) 2-23-same as W/O 1048342 (VW) DA 3-7-11 @ 1145pm C .AShton pole #60465 N/C @ Base - no feed wire @ base | High Pressure Sodium | 38.90260315000 | -77.01690044000
3/6/11 | 1050494 | 126 | 3RD ST | SE | 3/7/11 | 6A001 | 6A001 | (Light out) | DA 3-7-11 @ 351am T. Richards repaired pole #6A001 | Incandescent | 38.87684494000 | -77.00438348000
3/4/11 | 1050420 | 5600 | 3RD ST | NE | 3/4/11 | 4P471DC | 4U158 | (Light out) | DA 3-4-11 @ 304am R> Warren repaired pole #4p471dc | High Pressure Sodium | 38.95858464000 | -77.00292664000
3/3/11 | 1050353 | 2800 | LINCOLN RD | NE |  | 50065 | 5A056 | (Light out) | DA 3-18-11 @ 134am K> Simmons pole #50065 light is on and working 3-17-11 D Smith -light working properly light is left on 24 hr b- (VW) DA 3-10-11 @ 944pm K .Simmons pole #50065 N/C underground DA 3-9-11 work canncelled due to inclement weather. | High Pressure Sodium | 38.92549974000 | -77.00275988000
3/3/11 | 1050343 | 3425 | 14TH ST | NE | 3/7/11 | 51210DC | 5A099DC | (Light out) | DA 3-7-11 @ 320am K. Simmons repaired pole #51210dc | High Pressure Sodium | 38.93246169000 | -76.98640494000
3/2/11 | 1050255 | 1000 | POTOMAC AVE | SE | 3/8/11 | 67616 | 6L992 | (Light out) | DA 3-7-11 @ 1136pm T. Richards repaired pole #67616 DA 3-7-11 @ 255am K. Dunton request for map | High Pressure Sodium | 38.87728655000 | -76.99171966000
3/2/11 | 1050247 | 1000 | HALF ST | SE | 3/7/11 | 67437 | 6B103 | (Light out) | DA 3-7-11 @ 1102pm T. Richards pole #67437 - This pole has been removed | High Pressure Sodium | 38.87769232000 | -77.00752782000
3/2/11 | 1050238 | 2512 | SHERIDAN RD | SE | 3/3/11 | 81366DC | 8M051 | (Light out) | DA 3-3-11 @ 1016pm K. Simmons repaired pole #81366dc | High Pressure Sodium | 38.85995179000 | -76.99345916000
3/1/11 | 1050101 | 2001 | 37TH ST | SE | 3/4/11 | 74793DC | 7A082DC | (Light out) | DA 3-4-11 @ 1247am T. Richards repaired pole #74793dc | High Pressure Sodium | 38.86459154000 | -76.95373421000
3/1/11 | 1050090 | 3935 | PENNSYLVANIA AVE | SE | 2/7/12 | 78519DC | 7E147DC | (Light out) | DA 3-4-11 @ 110am T. Richards pole #78519dc New teardrop fixture on an old wooden pole / not on list refer to Ddot | High Pressure Sodium | 38.86423333000 | -76.94818049000
2/27/11 | 1049861 | 0000 | TOBIAS DR | SE | 3/1/11 | 81782 | 88059 | (Light out) | DA 3-1-11 @ 1224am K. Simmons repaired pole 381782 | High Pressure Sodium | 38.85002391000 | -76.98250326000
2/27/11 | 1049859 | 4612 | 12TH ST | NE | 3/2/11 | 51256DC | 5A150DC | (Light out) | DA 3-2-11 @ 1215am K. Simmons repaired pole #51256dc | High Pressure Sodium | 38.94542966000 | -76.99072288000
2/27/11 | 1049832 | 2201 | WISCONSIN AVE | NW | 2/28/11 | 30160 | 3G090 | (Light out) | DA 2-28-11 @ 1045pm K. Dunton repaired pole #30160 | High Pressure Sodium | 38.91927198000 | -77.07055935000
2/24/11 | 1049722 | 4205 | KANSAS AVE | NW | 4/16/12 | 4K571 | 4G317 | (Light out) | 3-1-11 D Dixon - Tempory Combo Traffic & SLight under construction by Capitol Paving Inc. (202) 529-7225 - haven't been turned over (VW) DA 2-24-11 @ 1114pm R Warren pole #4K571 N/C underground | High Pressure Sodium | 38.94236617000 | -77.02546807000
2/24/11 | 1049689 | 3249 | O ST | NW | 2/28/11 | 21109 | 2G171 | (Light off/on) | DA 2-28-11 @ 150am C. Ashton pole #21109 light is on and working DA 2-25-11 @ 140am C .AShton repaired pole #21109 | High Pressure Sodium | 38.90787180000 | -77.06535629000
2/23/11 | 1049611 | 1527 | 18TH ST | NW | 3/7/11 | 26758 | 2M157 | (Light out) | DA 3-7-11 @ 1246am C .Ashton found pole has been removed 3-4-11 H Lancaster/Jason - Found pole removed earlier this week - took pictures of area - sidewalk is covered by Red brick - new poles has been installed in area (VW) DA 2-24-11 @ 125am C. ASh | High Pressure Sodium | 38.91061514000 | -77.04160716000
2/23/11 | 1049605 | 3100 | SHERMAN AVE | NW | 3/3/11 | 12820 | 1L255 | (Light out) | DA 3-3-11 @ 314am C. Ashton pole #12820 light is on and working D. Dixon completed on 2-2-11. Made splices inside manhole. DA 2-24-11 @ 300am C> Ashton pole #12820 N/C underground | High Pressure Sodium | 38.92892725000 | -77.02615558000
2/22/11 | 1049530 | 0 | 7TH ST | NW | 1/24/12 | 22455 | 6M667 | (Light out) | DA 2-24-11 @ 1145pm C .Ashton pole #22455 teardrop fixture not on list refer to Ddot 11-00049093-street ligthts in front of location are out concerned citzen would like to have the repaired asap creating a safety hazard for customers and employees cw | High Pressure Sodium | 38.90101301000 | -77.02181903000
2/21/11 | 1049466 | 0 | EAST CAPITOL ST | NE | 4/16/12 | 74205DC | 7A063DC | (Light out) | DA 2-25-11 @ 244am T. Richards pole #74205dc already been reffered to Ddot and on list refer to wo #775183 | High Pressure Sodium | 38.89216210000 | -76.94254713000
2/21/11 | 1049440 | 0 | WISCONSIN AVE | NW | 2/23/11 | 38777 | 3U421 | (Light out) | DA 2-23-11 @ 1205am K. Dunton repaired pole #38777 | High Pressure Sodium | 38.93458612000 | -77.07231604000
2/21/11 | 1049417 | 300 | C ST | SW | 2/23/11 | 21655 | 6L624 | (Light out) | DA 2-23-11 @ 1035pm C. AShton repaired pole #21655 | High Pressure Sodium | 38.88610744000 | -77.01642413000
2/17/11 | 1049160 | 1333 | NEW HAMPSHIRE AVE | NW | 2/18/11 | 24473 | 2G775 | (Light out) | DA 2-18-11 @ 1200am C. AShton repaired pole #24473- Adjusted photocell | High Pressure Sodium | 38.90894364000 | -77.04422669000
2/16/11 | 1049042 | 4400 | GEORGIA AVE | NW | 2/21/11 | 4K024 | 4G309 | (Light out) | DA 2-21-11 @ 1238am R. Warren repaired pole #4K024 adjusted TLPC | High Pressure Sodium | 38.94410262000 | -77.02599601000
2/16/11 | 1049041 | 4324 | GEORGIA AVE | NW | 2/21/11 | 4K023 | 4G307 | (Light out) | DA 2-21-11 @ 1225am R. Warren repaired pole #4K023 | High Pressure Sodium | 38.94366890000 | -77.02586118000
2/16/11 | 1049033 | 3636 | GEORGIA AVE | NW | 2/18/11 | 12965 | 1G222 | (Light out) | DA 2-18-11 @ 345am C .Ashton repaired pole #12965 | High Pressure Sodium | 38.93515126000 | -77.02421018000
2/16/11 | 1049011 | 1370 | H ST | NE | 2/16/11 | 62353 | 6S133 | (Bridge light out) | DA 2-15-11 @ 902pm T. Richards repaired pole #62353 - Bridge light | High Pressure Sodium | 38.90011788000 | -76.98594986000
2/15/11 | 1048998 | 0 | OVERLOOK AVE | SW | 2/15/11 | 81840 | 88101 | (Light out) | DA 2-15-11 @ 740pm T .Richards pole #81840 light found okay - burn test | High Pressure Sodium | 38.83216740000 | -77.01463184000
2/14/11 | 1048781 | 1530 | 11TH ST | NW | 2/14/11 | 25286 | 2U045 | (Light out) | DA 2-14-11 @ 1230am C. Ashton repaired pole #25686 T20 right side | High Pressure Sodium | 38.91105847000 | -77.02715860000
2/10/11 | 1048451 | 0 | NEW YORK AVE | NE | 2/10/11 | 50008 | 5A042 | (Light out) | DA 2-10-11 @ 805pm T. Richards repaired pole #50008 | High Pressure Sodium | 38.91724347000 | -76.96648514000
2/10/11 | 1048442 | 0 | KENILWORTH AVE | SE | 2/10/11 | 79495 | 7A148 | (Light out) | DA 2-10-11 @ 909pm T. Richards repaired pole #79495 | High Pressure Sodium | 38.88589091000 | -76.96283495000
2/9/11 | 1048376 | 1100 | 3RD ST | SE | 2/11/11 | 68140 | 6A471 | (Light off/on) | DA 2-11-11 @ 315am C .Ashton repaired pole #68140 | High Pressure Sodium | 38.87742931000 | -77.00197636000
2/9/11 | 1048365 | 0 | C ST | SW | 2/28/11 | 21748 | 6A386 | (Light out) | DA 2-28-11 @ 1215am C> AShton pole #21748 light is on and working 2-18-11 D Dixon - Nuetral improperly connected, made corrections installed 20 #10 cable, 2-#8copper butt splices & tape (VW) DA 2-9-11 @ 1050pm C .Ashton pole #21748 T20 - 1 side out - | High Pressure Sodium | 38.88607059000 | -77.01250580000
2/9/11 | 1048363 | 0 | WASHINGTON AVE | SW | 2/10/11 | 21664 | 6A383 | (Light dim) | DA 2-9-11 @ 1150pm C. Ashton epaired pole #21664 T20 Left Side | High Pressure Sodium | 38.88653687000 | -77.01302412000
2/9/11 | 1048354 | 1370 | H ST | NE |  | 62353 | 6S133 | (Light out) | DA 2-15-11 @ 902pm T. Richards repaired pole #62353 Unit Block H street / North Capitol Street | High Pressure Sodium | 38.90011788000 | -76.98594986000
2/9/11 | 1048353 | 1351 | H ST | NE | 2/15/11 | 62352 | 6S129 | (Light out) | DA 2-15-11 @ 413am T. Richards repaired pole #62352 | High Pressure Sodium | 38.90011783000 | -76.98674046000
| 1048342 | 422 | K ST | NW | 3/23/11 | 60465 | 6A123 | (Light out) | DA 3-23-11 @ 229am T. Richards pole #60465 light is on and working J. Lancaster completed on 3-22-11. Installed 8 FT of conduit 400FT of cable and made splices inside manhole. DA 2-14-11 @ 348am T. Richards pole #60465 N/C underground ) volts - no feed | High Pressure Sodium | 38.90260315000 | -77.01690044000
2/8/11 | 1048222 | 1332 | 35TH ST | NW | 2/10/11 | 20903 | 2G192 | (Light out) | DA 2-10-11 @ 250am C .AShton repaired pole #20903 | High Pressure Sodium | 38.90762144000 | -77.06910533000
2/8/11 | 1048185 | 3700 | MILITARY RD | NW | 2/14/11 | 32716DC | 3E023 | (Light out) | DA 2-13-11 @ 1110pm K> Dunton pole #32716dc light is on and working 2-11-11 Greenfielf/Purnell installed 150' #6 triplex, made splices at the secondary (VW) DA 2-9-11 @ 140am K .Dunton pole #32716dc N/C to Overhead | High Pressure Sodium | 38.96062593000 | -77.07197706000
2/8/11 | 1048140 | 4612 | 12TH ST | NE | 2/10/11 | 51256DC | 5A150DC | (Light out) | DA 2-10-11 @ 430am K. Simmons repaired pole #51256dc | High Pressure Sodium | 38.94542966000 | -76.99072288000
2/8/11 | 1048110 | 1400 | BRENTWOOD PKY | NE | 1/24/12 | 52559 | 5M037 | (Light out) | DA 2-8-11 @ 1231am K .Simmons pole #52559 N/C underground - no neturial underground | High Pressure Sodium | 38.91138782000 | -76.99222307000
2/7/11 | 1048089 | 2206 | 18TH ST | NW | 3/22/11 | 11411 | 1G502 | (Light out) | DA 3-22-11 @ 340am R. Warren pole #11411 light is on and working 2-18-11 H Lancaster - checked pole base and MH found break in duct (see map) REFER to construction (VW) 2-17-11 AL Young - breakdown at MH 8" in duct and 1/2' at base of pole REFER to c | High Pressure Sodium | 38.91905896000 | -77.04152631000
2/7/11 | 1048070 | 1000 | 4TH ST | SE | 2/9/11 | 67542 | 6A434 | (Light out) | DA 2-9-11 @ 132am T. Richards repaired pole #67542 | High Pressure Sodium | 38.87830526000 | -77.00064838000
2/7/11 | 1048065 | 0 | BRENTWOOD PKY | NE | 2/8/11 | 52558 | 5M038 | (Light out) | DA 2-8-11 @ 1221am K .Simmons repaired pole #52558 | Mercury Vapor | 38.91111323000 | -76.99244214000
2/7/11 | 1048046 | 4400 | GEORGIA AVE | NW | 2/8/11 | 4K024 | 4G309 | (Light out) | DA 2-7-11 @ 1145pm R. Warren repaired pole #4k024 adjusted TLPC | High Pressure Sodium | 38.94410262000 | -77.02599601000
2/7/11 | 1048007 | 3100 | SHERMAN AVE | NW | 3/4/11 | 12820 | 1L255 | (Light out) | DA 3-3-11 @ 1040pm K >Dunton pole #12820 light is on and working D. Dixon completed on 2-2-11. Made splices inside manhole. DA 2-9-11 @ 1210am C. Ashton pole #12820 N/C underground @ Base 11-00032999-STREET LIGHT IS OUT ---VERY DANGEROUSLY DARK //H | High Pressure Sodium | 38.92892725000 | -77.02615558000
2/6/11 | 1047990 | 4500 | EAST CAPITOL ST | SE | 2/9/11 | 70052 | 7A035 | (Light out) | DA 2-9-11 @ 603am pole #70052 refer to Ddot - Already on the Ddot refer list | High Pressure Sodium | 38.88960932000 | -76.93729068000
2/6/11 | 1047944 | 2114 | 18TH ST | NW | 2/8/11 | 11538 | 1G505 | (Light out) | DA2-8-11 @ 402am C. AShton repaired pole #11538 | High Pressure Sodium | 38.91851092000 | -77.04175253000
2/6/11 | 1047943 | 2206 | 18TH ST | NW | 3/22/11 | 11411 | 1G502 | (Light out) | DA 3-22-11 @ 340am C. aShton pole #11411 light is on and working 2-18-11 H Lancaster - checked poles base and MH found break in duct (see map) REFER to construction (VW) 2-17-11 AL Young - breakdown at MH 8" in duct and 1/2' at base of pole REFER to co | High Pressure Sodium | 38.91905896000 | -77.04152631000
2/6/11 | 1047941 | 2407 | 18TH ST | NW | 2/8/11 | 11533 | 1G491 | (Light out) | DA 2-8-11 @ 418am C .Adhton pole #11533 light found on and working | High Pressure Sodium | 38.92063969000 | -77.04213470000
2/3/11 | 1047758 | 422 | K ST | NW |  | 60465 | 6A123 | (Light out) | 2-23-11D Dixon Breakdown - unable to rod REFER to construction REFER to W/O#1048342(VW) DA 2-14-11 @ 348am T. Richards pole #60465 N?C underground ) volts - no feed wire, no fixture , no wire 2-11-11 Al Young light is abadoned (VW) DA 2-8-11 @ | High Pressure Sodium | 38.90260315000 | -77.01690044000
2/3/11 | 1047693 | 3226 | 15TH PL | SE | 2/4/11 | 81778 | 88055 | (Light out) | DA 2-4-11 @ 313am K. Simmons reattached globe pole #81778 11-00029727-Caller is reporting that there is a street light cover that is about to fell at this location. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.84869559000 | -76.98249181000
2/1/11 | 1047607 | 0 | 9TH ST | NW | 2/4/11 | 22988 | 2G982 | (Light out) | DA 2-4-11 @ 334am C> Ashton repaired pole #22988 | High Pressure Sodium | 38.90042206000 | -77.02407679000
1/30/11 | 1047476 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 2/7/12 | 71270 | 71270DC | (Light out) | DAd 2-3-11 @ 1202am T. Richards pole #71270 N/C underground 0 volts | High Pressure Sodium | 38.89827347000 | -76.92679095000
1/30/11 | 1047475 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 2/7/12 | 72645 | 7S073 | (Light out) | DA 2-3-11 @ 1212am T. Richards pole #72645 N/C underground 0 volts | High Pressure Sodium | 38.89826452000 | -76.92554310000
1/30/11 | 1047474 | 5214 | NANNIE HELEN BURROUGHS AVE | NE | 2/7/12 | 72646 | 7A198 | (Light out) | DA 2-3-11 @ 1221am T. Richards pole #72646 N/C underground 0 volts | High Pressure Sodium | 38.89827561000 | -76.92455911000
1/27/11 | 1047398 | 0 | H ST | NE | 1/31/11 | 61632 | 6S219 | (Light out) | DA 1-31-11 @ 125am T> Richards repaired pole #61632 11-00023651- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90029661000 | -76.99965221000
1/25/11 | 1047302 | 423 | NEW YORK AVE | NW | 1/26/11 | 25923 | 6M764 | (Light out) | DA 1-26-11 @ 315am C. Ashton repaired pole #25923 | High Pressure Sodium | 38.90450411000 | -77.01761089000
1/25/11 | 1047280 | 720 | RHODE ISLAND AVE | NE | 1/26/11 | 56389DC | 5M343 | (Light out) | DA 1-26-11 @ 243am K. Simmons repaired pole #56389dc | High Pressure Sodium | 38.92154000000 | -76.99495411000
1/25/11 | 1047279 | 806 | RHODE ISLAND AVE | NE |  | 56388DC | 5A274 | (Light out) | 1-29-11 D Smith/A Purnell - Circuit contains house service and is inside a construction site. DA 1-26-11 @ 250am K. Simmons pole #56388dc N/C to Overhead - no overhead neturial | High Pressure Sodium | 38.92176361000 | -76.99420034000
1/24/11 | 1047159 | 900 | UPSHUR ST | NW | 1/25/11 | 4R782 | 4R790 | (Light out) | DA 1-24-11 @ 1131pm R. Warren repaired pole #4R782 - adjusted photocell | High Pressure Sodium | 38.94192259000 | -77.02846969000
1/24/11 | 1047107 | 3100 | SHERMAN AVE | NW | 3/4/11 | 12820 | 1L255 | (Light out) | DA 3-3-11 @ 1040pm K >Dunton pole #12820 light is on and working D. Dixon completed on 2-2-11. Made splices inside manhole. DA 1-24-11 @ 1028pm C> Ashton pole #12820 N/C @ Base 11-00018833-metal pool streetlight is out ..very dark //high crime area | High Pressure Sodium | 38.92892725000 | -77.02615558000
1/23/11 | 1047045 | 5350 | CALL PL | SE | 1/25/11 | 75597 | 75597DC | (Light out) | DA 1-24-11 @ 1120pm T. Richards repaired pole #75597dc | Incandescent | 38.88403430000 | -76.92511243000
1/23/11 | 1047044 | 5350 | C ST | SE | 1/25/11 | 75596 | 75596DC | (Light out) | DA 1-24-11 @ 1109pm T .Richards repaired pole #75596dc | Incandescent | 38.88422223000 | -76.92507148000
1/23/11 | 1047020 | 1100 | HALF ST | SE | 1/26/12 | 67435 | 6B100 | (Light out) | DA 1-25-11 @ 231am T. Richards pole #67435 3rd party contractor instlled new 16ft metal poles teardrop fixtures - there is no current underground | High Pressure Sodium | 38.87824281000 | -77.00752674000
1/20/11 | 1046873 | 1332 | 35TH ST | NW | 1/21/11 | 20903 | 2G192 | (Light out) | DA 1-21-11 @ 152am C >AShton pole #20903 light found on and working | High Pressure Sodium | 38.90762144000 | -77.06910533000
1/20/11 | 1046864 | 2336 | WISCONSIN AVE | NW | 1/21/11 | 30149 | 3G073 | (Light off/on) | DA 1-21-11 @ 355am K .Dunton repaired pole #30149 | High Pressure Sodium | 38.92085423000 | -77.07199482000
1/20/11 | 1046824 | 3400 | 14TH ST | NW | 1/20/11 | 13680 | 1G081 | (Light out) | DA1-20-11 @ 245am K .Dunton repaired pole #13680 | High Pressure Sodium | 38.93204150000 | -77.03266569000
1/20/11 | 1046817 | 3100 | SHERMAN AVE | NW |  | 12820 | 1L255 | (Light out) | D. Dixon completed on 2-2-11. Made splices inside manhole. 1-25-11 Al Young - Traffic Combo Pole REFER to DDOT (VW) DA 1-20-11 @ 230am K. Dunton pole #12820 N/C underground - low voltage - 70 volts | High Pressure Sodium | 38.92892725000 | -77.02615558000
1/20/11 | 1046807 | 107 | WASHINGTON CIR | NW | 1/24/11 | 24655 | 2G671 | (Light out) | DA 1-24-11 @ 228am C. AShton t base door on pole #24655 is okay Front 11-00015274-PEDESTAL DOOR IS BROKEN cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90310962000 | -77.05038859000
1/19/11 | 1046742 | 1308 | H ST | NE | 1/26/12 | 62330 | 6S154 | (Light out) | DA 1-24-11 @ 235am K. Dunton pole # 62330 light out due to construction - no company info (trolly work?) | High Pressure Sodium | 38.90029744000 | -76.98780787000
1/19/11 | 1046730 | 3100 | SHERMAN AVE | NW | 1/20/11 | 12820 | 1L255 | (Light out) | DA 1-20-11 @ 110am K .Dunton repaired pole #12820 | High Pressure Sodium | 38.92892725000 | -77.02615558000
1/19/11 | 1046727 | 900 | 22ND ST | NW | 1/23/11 | 28305 | 2M291 | (Light out) | DA 1-23-11 @ 1032pm C .Ashton repaired pole #28305 | High Pressure Sodium | 38.90179684000 | -77.04875673000
1/19/11 | 1046696 | 2800 | BLADENSBURG RD | NE | 1/19/11 | 50093 | 5A079 | (Light out) | DA 1-18-11 @ 1133pm K. Simmons repaire pole #50093 | High Pressure Sodium | 38.92578158000 | -76.96424536000
1/15/11 | 1046609 | 0 | CHILLUM PL | NE | 1/19/11 | 4P515DC | 4U173 | (Light out) | DA 1-18-11 @ 1045pm R. Warren repaired pole #4p515dc 11-00012120- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.95902228000 | -77.00179861000
1/14/11 | 1046441 | 0 | MAPLE ST | NW | 1/14/11 | 4H589DC | 4L603 | (Light out) | DA 1-14-11 @ 340am R. WArren repaired pole #4h589dc | High Pressure Sodium | 38.97428343000 | -77.01522309000
1/14/11 | 1046419 | 1306 | L ST | SE | 1/14/11 | 66199 | 6U007 | (Light out) | DA 1-13-11 @ 1009pm T. Richards repaired pole #66199 | High Pressure Sodium | 38.87748181000 | -76.98785343000
1/13/11 | 1046345 | 3400 | SHERMAN AVE | NW | 1/14/11 | 13070 | 1L297 | (Light out) | DA 1-14-11 @ 115am C .Ashton repaired pole #13070 | High Pressure Sodium | 38.93240466000 | -77.02663265000
1/13/11 | 1046127 | 0 | ANACOSTIA FWY | SE | 2/2/11 | 79478 | 7A142 | (Light out) | 2-2-11 I Paraway/Rip replaced 40' #10 wire 100% complete (VW) DA 1-19-11 @ 1135pm T .Richards pole #79478 N/C undeground - 0 Volts | High Pressure Sodium | 38.88446501000 | -76.96303530000
1/11/11 | 1046060 | 2000 | FORT DAVIS ST | SE | 1/14/11 | 78523DC | 7E142 | (Light out) | DA 1-14-11 @ 140am K .Dunton pole #78523dc light was found on and working | High Pressure Sodium | 38.86502980000 | -76.95013502000
1/11/11 | 1046057 | 1735 | PENNSYLVANIA AVE | SE | 2/7/12 | 78542DC | 7E117DC | (Light off/on) | DA 1-13-11 @ 344am T. Richards - not our light 3rd party contractor refer to Ddot | High Pressure Sodium | 38.86796881000 | -76.95734397000
1/11/11 | 1046011 | 1000 | NEW YORK AVE | NW | 1/13/11 | 22912 | 2L064 | (Light out) | DA 1-13-11 @ 1029pm C .Ashton repaired pole #22912 Intersection 11-00008203- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90130097000 | -77.02614564000
1/10/11 | 1045947 | 1332 | 35TH ST | NW | 1/11/11 | 20903 | 2G192 | (Light out) | DA 1-11-11 @ 140am C .Ashton repaired pole #20903 | High Pressure Sodium | 38.90762144000 | -77.06910533000
1/10/11 | 1045946 | 3623 | O ST | NW | 1/11/11 | 21090 | 2G153 | (Light out) | DA 1-11-11 @ 148am C> aston repaired pole #21090 - tightened loose wire | High Pressure Sodium | 38.90774375000 | -77.07124202000
1/10/11 | 1045929 | 1400 | S ST | NW | 1/12/11 | 26184 | 2A080 | (Light off/on) | DA 1-12-11 @ 1000pm K. Simmons pole #26184 light was on upon arrival - new fixture, bulb dated - adjusted photocell | High Pressure Sodium | 38.91415171000 | -77.03212341000
1/10/11 | 1045923 | 6 | BARNEY CIR | SE | 1/13/11 | 65366 | 6U670 | (Light out) | DA 1-13-11 @ 132am T. Richards repaired pole #65366 | High Pressure Sodium | 38.87904725000 | -76.98154423000
1/9/11 | 1045856 | 0 | 23RD ST | NW | 1/10/11 | 28341 | 2A231 | (Light out) | DA 1-10-11 @ 107am C> Ashton repaired pole #28241 | High Pressure Sodium | 38.90047387000 | -77.05001383000
1/9/11 | 1045832 | 901 | 9TH ST | NW | 1/10/11 | 22987 | 2G988 | (Light out) | DA 1-10-11 @ 1057pm C. Ashton pole #22987 light is on and working previously repaired | High Pressure Sodium | 38.90092176000 | -77.02415354000
1/9/11 | 1045830 | 423 | NEW YORK AVE | NW | 1/14/11 | 25923 | 6M764 | (Light out) | DA 1-14-11 @ 324am C .AShton repaired pole #25923 | High Pressure Sodium | 38.90450411000 | -77.01761089000
1/5/11 | 1045607 | 901 | HALF ST | SE | 1/10/11 | 67433 | 6U342 | (Light out) | DA 1-6-11 @ 1028pm C. Ashton pole #67433 N/C Underground - No Voltage | High Pressure Sodium | 38.87894793000 | -77.00752512000
1/5/11 | 1045606 | 900 | HALF ST | SE | 1/10/11 | 67434 | 6U343 | (Light out) | DA 1-6-11 @ 1028pm C. Ashton pole #67434 N/C Underground - No Voltage | High Pressure Sodium | 38.87873279000 | -77.00752418000
1/5/11 | 1045605 | 1100 | HALF ST | SE | 1/26/12 | 67435 | 6B100 | (Light out) | 1-14-11 New poles are being installed by outside construction co. (VW) REFER to DDOT DA 1-6-11 @ 1028pm C. Ashton pole #67435 N/C Underground - No Voltage | High Pressure Sodium | 38.87824281000 | -77.00752674000
1/5/11 | 1045604 | 900 | K ST | SE | 1/10/11 | 67675 | 6U345 | (Light out) | DA 1-6-11 @ 1028pm T. Richards pole #67675 N/C Underground - No Voltage | High Pressure Sodium | 38.87846883000 | -77.00757395000
1/5/11 | 1045603 | 31 | K ST | SE | 1/26/12 | 67676 | 6B098 | (Light out) | 1-14-11 New poles are being installed by outside construction co. (VW) REFER to DDOT DA 1-6-11 @ 1028pm T. Richards pole #67676 N/C Underground - No Voltage | High Pressure Sodium | 38.87836069000 | -77.00783290000
1/4/11 | 1045526 | 1147 | CONNECTICUT AVE | NW | 1/5/11 | 27220 | 2U544 | (Light out) | DA 1-5-11 @ 232am C. Ashton repaire pole #27220 SE Corner 11-00002533-street light is blinking on and off. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90537241000 | -77.04079316000
1/4/11 | 1045442 | 0 | I ST | NW | 7/12/11 | 22487 | 2G985 | (Light out) | D 7-12-11 C .Ashton light is on DA 1-4-11 @ 220am C> Ashton new teardrop fixture / not on list | High Pressure Sodium | 38.90081220000 | -77.02379981000
1/2/11 | 1045286 | 901 | 9TH ST | NW | 1/3/11 | 22987 | 2G988 | (Light out) | DA 1-3-11 @ 1015pm C. Ashton repaired pole #22987 | High Pressure Sodium | 38.90092176000 | -77.02415354000
1/2/11 | 1045285 | 0 | NEW YORK AVE | NW | 1/4/11 | 22914 | 2L029 | (Light out) | DA 1-4-11 @ 1040pm C. Ashton repaired pole #22914 | High Pressure Sodium | 38.90105629000 | -77.02684066000
12/30/10 | 1045244 | 600 | MICHIGAN AVE | NE | 1/3/11 | 53649DC | 5U721 | (Light out) | DA 1-3-11 @ 234am K. Simmons repaired pole #53649dc 10-00431471- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93248081000 | -76.99750323000
12/29/10 | 1045154 | 1300 | UPSHUR ST | NW | 12/30/10 | 4J795 | 4U152 | (Light out) | DA 12-30-10 @ 350am R> Warren relocated TLPC pole #4J795 | High Pressure Sodium | 38.94192828000 | -77.02984643000
12/29/10 | 1045111 | 0 | SHERMAN AVE | NW | 12/29/10 | 12584 | 1G473 | (Light out) | DA 12-29-10 @ 120am C. Ashton repaired pole #12584 | High Pressure Sodium | 38.92101625000 | -77.02534481000
12/27/10 | 1044927 | 1403 | KEARNEY ST | NW | 12/27/10 | 59990 | 5A182 | (Light out) | DA 12-27-10 @ 1036pm K. Simmons repaired pole #59990 | High Pressure Sodium | 38.91424947000 | -77.01606264000
12/22/10 | 1044803 | 1330 | NEW HAMPSHIRE AVE | NW | 1/11/11 | 24477 | 2G768 | (Light out) | DA 1-11-11 @ 337am C> AShton pole #24477 light is on and working DA 12-23-10 @ 1245am C .Ashton pole #24477 N/C @ Base | High Pressure Sodium | 38.90790996000 | -77.04519509000
12/22/10 | 1044784 | 1700 | R ST | NW | 12/23/10 | 26234 | 2M134 | (Light out) | DA 12-23-10 @ 310am K. Dunton repaied pole #26234 | High Pressure Sodium | 38.91256978000 | -77.04156816000
12/21/10 | 1044735 | 3623 | O ST | NW | 12/27/10 | 21090 | 2G153 | (Light out) |  | High Pressure Sodium | 38.90774375000 | -77.07124202000
12/21/10 | 1044673 | 0 | INTERSTATE 295 | SE | 12/22/10 | 86510 | 8L768 | (Light out) | DA 12-20-10 @ 1041pm T. Richards pole #86510 N/C underground - no voltage | High Pressure Sodium | 38.86566546000 | -76.99168893000
12/21/10 | 1044669 | 0 | KENILWORTH AVE | SE | 2/7/12 | 79497 | 7A150 | (No current) | DA 12-20-10 @ 852pm T. Richards pole #79497 N/C underground - No Voltage | High Pressure Sodium | 38.88456308000 | -76.96344581000
12/20/10 | 1044614 | 1401 | V ST | SE | 12/20/10 | 80878 | 8M028DC | (Light out) | DA 12-20-10 @ 1038pm K >Simmons repaired pole #80878 | High Pressure Sodium | 38.86497272000 | -76.98559684000
12/20/10 | 1044610 | 457 | MASSACHUSETTS AVE | NW | 2/7/12 | 60481 | 6A195 | (Light out) | DA 12-22-10 @ 245am K. Dunton pole #60481 N/C underground no voltage | High Pressure Sodium | 38.90073307000 | -77.01753805000
12/16/10 | 1044489 | 1300 | 1ST ST | NE | 12/21/10 | 61247 | 6A279 | (Light out) | DA 12-21-10 @ 310am C> AShton repaired pole #61247 10-00420364- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90758804000 | -77.00596758000
12/16/10 | 1044463 | 4000 | GEORGIA AVE | NW | 2/7/12 | 4J352 | 4G276 | (Light out) | 2-8-11 J Lancaster REFER to DDOT capitol paving installing new poles (VW) DA 12-20-10 @ 1045pm R> WArren pole #4J352 N/C underground | High Pressure Sodium | 38.94007092000 | -77.02516512000
12/15/10 | 1044405 | 0 | ANACOSTIA FWY | SE | 12/21/10 | 79469 | 7A133 | (Light out) | DA 12-20-10 @ 829pm T .Richards repaired pole #79469 | High Pressure Sodium | 38.88182711000 | -76.96446211000
12/15/10 | 1044387 | 7051 | SPRING PL | NW | 12/16/10 | 4H523DC | 4H523 | (Light out) | DA 12-16-10 @ 219am R. Warren repaired pole #4h523dc | Incandescent | 38.97594098000 | -77.01865986000
12/15/10 | 1044353 | 3230 | PENNSYLVANIA AVE | SE | 12/20/10 | 78549DC | 7E106 | (Light out) | DA 12-20-10 @ 1050pm C .AShton pole #78549dc - could not acces light due to road construction but light was on | High Pressure Sodium | 38.86896025000 | -76.95979555000
12/14/10 | 1044241 | 741 | 51ST ST | SE | 12/15/10 | 75475 | 75475DC | (Light out) | DA 12-14-10 @ 1123pm T. Richards repaired pole #75475 10-00417885- cwDesc: ALLEYLIGHT REPAIR | Incandescent | 38.87911825000 | -76.93033276000
12/14/10 | 1044202 | 1400 | S ST | NW | 12/14/10 | 26184 | 2A080 | (Light off/on) | DA 12-14-10 @ 1020pm C .Ashton repaired pole #26184 | High Pressure Sodium | 38.91415171000 | -77.03212341000
12/13/10 | 1044085 | 0 | U ST | NW | 12/15/10 | 13288 | 1G548 | (Light out) | DA 12-15-10 @ 234am R. WArren repaired pole #13288 | High Pressure Sodium | 38.91691836000 | -77.02612231000
12/12/10 | 1043995 | 2448 | 18TH ST | NW | 12/15/10 | 11530 | 1G481 | (Light out) | K. Greenfield completed on 12-15-10. Made splices inside manhole. DA 12-13-10 @ 240am C .AShton pole #11530 N/C @ base | High Pressure Sodium | 38.92184690000 | -77.04249788000
12/12/10 | 1043989 | 3532 | GEORGIA AVE | NW | 12/15/10 | 12969 | 1G210 | (Light out) | DA 12-15-10 @ 117am R, Warren pole #12969 light is on and working but is only reading 112volts @ Base DA 12-12-10 @ 1046pm C. Ashton pole #12969 light found on and working | High Pressure Sodium | 38.93411676000 | -77.02407525000
12/12/10 | 1043956 | 900 | UPSHUR ST | NW | 12/14/10 | 4J744 | 4G330 | (Light out) | DA 12-12-10 @ 1125pm R. Warren pole #4j744 N/C underground | High Pressure Sodium | 38.94182164000 | -77.02494834000
12/12/10 | 1043954 | 901 | VARNUM ST | NW | 12/13/10 | 4K190 | 4G320 | (Light out) | DA 12-12-10 @ 1139pm R. Warren pole #4k190 temp pole but is on and working | High Pressure Sodium | 38.94289398000 | -77.02535229000
12/10/10 | 1043919 | 1431 | MONROE ST | NE | 12/13/10 | 51217DC | 5A107DC | (Light out) | DA 12-13-10 @ 209am K, Simmons repaired pole #51217dc 10-00415101-streetlight has been out for 2 weeks. please repair ASAP. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93279592000 | -76.98507761000
12/10/10 | 1043901 | 0 | OVERLOOK AVE | SE | 12/22/10 | 81813 | 88087 | (Light out) | DA 12-10-10 @ 417am T. Richards pole #81813 N/C underground - no voltage | High Pressure Sodium | 38.83101830000 | -77.01553587000
12/10/10 | 1043886 | 0400 | TAYLOR ST | NE | 12/10/10 | 50087 | 5A068 | (Light out) | DA 12-10-10 @ 139am K .Simmons repaired pole #50087 | High Pressure Sodium | 38.94068700000 | -77.00116728000
12/10/10 | 1043885 | 0400 | TAYLOR ST | NE | 12/10/10 | 50089 | 5A070 | (Light out) | DA 12-10-10 @ 120am K. Simmons repaired pole #50089 | High Pressure Sodium | 38.94080995000 | -77.00072598000
12/9/10 | 1043786 | 0 | 23RD ST | NW | 4/21/11 | 28318 | 2M274 | (Light out) | DA 4-21-11 @ 1230am C .AShton pole #28318 light found okay 2-15-11 H Lancaster -Job is under contract, light will work when feeders become energized (VW) 2-07-11 @ 1228am C. Ashton pole #28318 light is still off 2-3-11 J Lancater - installed 375' #10 | High Pressure Sodium | 38.89313901000 | -77.05025238000
12/9/10 | 1043775 | 0 | 23RD ST | NW | 4/16/12 | 28556 | 2M278 | (Light out) | BCM - 4/16/2012 - LIGHT ON - 12-9-10 M Craig install 1-118 globe VW DA 12-09-10 @ 215am C. Ashton pole #28556 pole has been hit needs new T Base, and Globe has N/C underground @ Base | High Pressure Sodium | 38.89224008000 | -77.05038174000
12/9/10 | 1043770 | 0 | BRANDYWINE ST | NW | 1/19/11 | 3A230DC | 3A230 | (Light out) | DA 12-09-10 @ 1220am K Dunton poe #3a230dc defective 250 mv fixture | High Pressure Sodium | 38.94974018000 | -77.08081828000
12/8/10 | 1043748 | 2912 | BLADENSBURG RD | NE | 12/9/10 | 51235DC | 5A131DC | (Light out) | DA 12-09-10 @ 1026pm K. Simmons repaired pole #51235dc | High Pressure Sodium | 38.92770962000 | -76.96225165000
12/8/10 | 1043724 | 0 | 23RD ST | NW |  | 28320 | 2M268 | (Light out) | 12-9-10 M Craig -need **special** base door - none in the shop VW DA 12-09-10 @ 240am Twin pole #28320 needs 2 crowns to hold fixture and need T Base Door ALL OUT BETWEEN C ST AND CONSTITUTION AVE | High Pressure Sodium | 38.89242239000 | -77.05003950000
12/8/10 | 1043614 | 2348 | WISCONSIN AVE | NW | 12/9/10 | 30165 | 3G072 | (Light out) | DA 12-09-10 @ 415am K. Dunton repaired pole #30165 | High Pressure Sodium | 38.92100387000 | -77.07184696000
12/8/10 | 1043537 | 0 | OVERLOOK AVE | SE | 12/22/10 | 81813 | 88087 | (Light out) | DA 12-07-10 @ 1112pm T Richards pole #81813 N/C Underground 0 volts | High Pressure Sodium | 38.83101830000 | -77.01553587000
12/7/10 | 1043477 | 1431 | MONROE ST | NE | 12/8/10 | 51217DC | 5A107DC | (Light out) | DA 12-08-10 @ 246am K> Simmons repaired pole #51217dc | High Pressure Sodium | 38.93279592000 | -76.98507761000
12/7/10 | 1043476 | 1000 | 1ST ST | NW | 12/10/10 | 61105 | 6A232 | (Light out) | DA 12-10-10 @ 230am K. Dunton repaired pole #61105 | High Pressure Sodium | 38.90337658000 | -77.01210139000
12/6/10 | 1043403 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 2/7/12 | 72649 | 7A189 | (Light out) | DA 12-09-10 @ 1211am T. Richards pole #72649 has improper voltage - voltage reading 174 power door is wired for 240 - traffic combo pole - t base rusted. | High Pressure Sodium | 38.89825683000 | -76.92196339000
12/5/10 | 1043267 | 1765 | NEW YORK AVE | NE | 12/7/10 | 50059 | 5A050 | (Light out) | DA 12-07-10 @ 301am K. Simmons repaired pole #50059 | High Pressure Sodium | 38.91711725000 | -76.97869992000
12/2/10 | 1043165 | 1936 | EAST CAPITOL ST | NE |  | 63721 | 6M804 | (Light out) | DA 12-02-10 @ 1050pm C .Ashton pole #63721 out due to new construction (no construction info avalible) | High Pressure Sodium | 38.88960987000 | -76.97672435000
12/2/10 | 1043084 | 3232 | P ST | NW | 12/2/10 | 21020 | 2G149 | (Light out) | DA 12-02-10 @ 145am C. Ashton repaired pole #21020 | High Pressure Sodium | 38.90878828000 | -77.06441557000
12/1/10 | 1043044 | 3327 | O ST | NW | 12/2/10 | 21103 | 2G165 | (Light out) | DA 12-02-10 @ 125am C. ashton repaired pole #21103 Center 10-00405233- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90782993000 | -77.06720414000
11/30/10 | 1043030 | 3253 | P ST | NW | 12/3/10 | 21018 | 2G147 | (Light out) | DA 12-03-10 @ 200am C. Ashtonrepaired pole #21018 DA 12-02-10 @ 138am C. AShton pole #21018 needs 150 conversion kit on P Street, NW 10-00404524- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90877550000 | -77.06502369000
11/30/10 | 1042993 | 1500 | KEARNEY ST | NE | 11/30/10 | 59986 | 5A177 | (Light out) | DA 11-30-10 @ 330am C. ashton repaired pole #59986 | High Pressure Sodium | 38.91401980000 | -77.01759054000
11/28/10 | 1042813 | 3311 | P ST | NW | 11/28/10 | 21013 | 2G138 | (Light out) | DA 11-28-10 @ 1035pm C. Ashton repaired pole #21013 10-00402676- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90883614000 | -77.06643273000
11/23/10 | 1042705 | 3043 | BLADENSBURG RD | NE | 11/23/10 | 51245DC | 5A141DC | (Light out) | DA 11-23-10 @ 1134pm K .Simmons repaired pole #51245dc | High Pressure Sodium | 38.93032628000 | -76.95815755000
11/21/10 | 1042454 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 11/22/10 | 71269 | 7A201 | (Light out) | DA 11-22-10 @ 322am T. Richards pole #71269 N/C underground - already in system refer to wo #1042382 | High Pressure Sodium | 38.89826963000 | -76.92624974000
11/21/10 | 1042453 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 11/22/10 | 71270 | 71270DC | (Light out) | DA 11-22-10 @ 332am T. Richards pole #71270 N/C underground - already in system refer to wo #1042337 | High Pressure Sodium | 38.89827347000 | -76.92679095000
11/21/10 | 1042451 | 3232 | P ST | NW | 11/22/10 | 21020 | 2G149 | (Light out) | DA 11-22-10 @ 140am C. Ashton pole #21020 light found on and working | High Pressure Sodium | 38.90878828000 | -77.06441557000
11/21/10 | 1042440 | 0 | H ST | NE | 2/7/12 | 62350 | 6S120 | (Light out) | DA 11-21-10 @ 1009pm T. Richards pole #62350 construction area - Temp pole | High Pressure Sodium | 38.90011633000 | -76.98846372000
11/19/10 | 1042382 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 2/7/12 | 71269 | 7A201 | (Light out) | DA 11-19-10 @ 246am T> Richards pole #71269 N/C Underground - no voltage | High Pressure Sodium | 38.89826963000 | -76.92624974000
11/18/10 | 1042347 | 2000 | M ST | NW | 11/22/10 | 23722 | 2A077 | (Light out) | DA 11-22-10 @ 100am C .ashton repaired pole #23722 SWC 20th and M St on 20th 10-00394830- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90574768000 | -77.04540447000
11/18/10 | 1042337 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 2/7/12 | 71270 | 71270DC | (Light out) | DA 11-19-10 @ 255am T Richards pole #71270 N/C underground - no voltage | High Pressure Sodium | 38.89827347000 | -76.92679095000
11/17/10 | 1042241 | 3043 | BLADENSBURG RD | NE | 11/19/10 | 51245DC | 5A141DC | (Light out) | DA 11-19-10 @ 241am K. Simmons repaired pole #51245dc reconnected hot overhead 10-00393841- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.93032628000 | -76.95815755000
11/17/10 | 1042182 | 900 | 4TH ST | SE | 11/18/10 | 67536 | 6A429 | (Light out) | DA 11-18-10 @ 108am T. Richards repaired pole #67536 | High Pressure Sodium | 38.87918965000 | -77.00064880000
11/16/10 | 1042104 | 0 | P ST | NW | 11/17/10 | 25805 | 6A807 | (Light out) | DA 11-16-10 @ 1150pm C .Ashton repaired pole #25805 | High Pressure Sodium | 38.90960205000 | -77.02177585000
11/15/10 | 1042019 | 900 | UPSHUR ST | NW | 11/16/10 | 4J744 | 4G330 | (Light out) | DA 11-16-10 @ 1201am R. Warren pole #4j744 has been repaired by 3rd party contractor | High Pressure Sodium | 38.94182164000 | -77.02494834000
11/11/10 | 1041806 | 2 | L ST | NE | 11/15/10 | 61201 | 6A240 | (Light out) | DA 11-15-10 @ 221am T> Richards repaired pole #61201 | High Pressure Sodium | 38.90378899000 | -77.00858856000
11/14/10 | 1041929 | 5412 | E ST | SE | 11/16/10 | 75501 | 75501DC | (Light out) | DA 11-15-10 @ 1153pm T. Richards repaired pole #75501 | High Pressure Sodium | 38.88126024000 | -76.92504376000
11/14/10 | 1041924 | 3230 | PENNSYLVANIA AVE | SE | 3/10/11 | 78549DC | 7E106 | (Light out) | DA 11-16-10 @ 1241am T. Richards pole #78549dc N/C to overhead - pepco installed new poles and did not energize them yet | High Pressure Sodium | 38.86896025000 | -76.95979555000
11/10/10 | 1041388 | 777 | NORTH CAPITOL ST | NE | 11/12/10 | 68241DC | 68241 | (Light out) | DA 11-11-10 @ 123am T. Richards pole #68241dc N/C underground - Needs MOT | High Pressure Sodium | 38.90010486000 | -77.00885876000
11/9/10 | 1041219 | 3170 | BLADENSBURG RD | NE | 11/10/10 | 51230DC | 5A126DC | (Light out) | DA 11-09-10 @ 1107pm K. Simmons repaired pole #51230dc | High Pressure Sodium | 38.92882531000 | -76.96080667000
11/8/10 | 1041035 | 1801 | P ST | NW | 11/16/10 | 26339 | 2M169 | (Light dim) | DA 11-08-10 @ 1135pm C. Ashton pole #26339 installed 400hps lamp - checked wires @ base reading 120volts hot to Ground - 5 volts hot to neturial suggest that needs stronger ground on neturial | High Pressure Sodium | 38.90971066000 | -77.04178765000
11/8/10 | 1041031 | 1904 | 18TH ST | NW | 11/11/10 | 26782 | 2M096 | (Light out) | DA 11-08-10 @ 1045pm C .Ashton pole #26782 N/C @ Base no voltage | High Pressure Sodium | 38.91581064000 | -77.04174130000
11/8/10 | 1041030 | 1829 | 18TH ST | NW | 11/11/10 | 26749 | 2M103 | (Light out) | 11-10-10 M Craig TBase door DA 11-09-10 @ 1250am C >AShton pole #26749 N/C @ Base = Needs screws for T Base Door | High Pressure Sodium | 38.91509042000 | -77.04157398000
11/8/10 | 1041027 | 3232 | P ST | NW | 11/9/10 | 21020 | 2G149 | (Light out) | DA 11-09-10 @ 130am C .Ashton pole #21020 light found on and working | High Pressure Sodium | 38.90878828000 | -77.06441557000
11/5/10 | 1040889 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 11/5/10 | 72649 | 7A189 | (Light out) | DA 11-05-10 @ 158am T> Richards repaired pole #72649 | High Pressure Sodium | 38.89825683000 | -76.92196339000
11/5/10 | 1040887 | 4600 | NANNIE HELEN BURROUGHS AVE | NE | 11/5/10 | 71301DC | 7A236 | (Light out) | DA 11-05-10 @ 109am T. Richards repaired pole #71301dc | High Pressure Sodium | 38.89952817000 | -76.93621663000
11/5/10 | 1040868 | 2122 | 14TH ST | SE | 11/5/10 | 80522 | 8M024 | (Light out) | DA 11-05-10 @ 140am K .Simmons repaired pole #80522 resplice wires in powerdoor | High Pressure Sodium | 38.86436582000 | -76.98590224000
11/4/10 | 1040857 | 0 | 9TH ST | NW | 11/4/10 | 22988 | 2G982 | (Light out) | DA 11-04-10 @ 1100pm C .Ashton repaired pole #22988 | High Pressure Sodium | 38.90042206000 | -77.02407679000
11/4/10 | 1040852 | 2427 | MINNESOTA AVE | SE | 11/5/10 | 70076 | 80098 | (Light out) | DA 11-05-10 @ 318am T. Richards repaired pole #70076 10-00380658- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.87320803000 | -76.97100322000
| 1040751 | 1005 | 1ST ST | NE | 2/2/12 | 61231 | 6S439 | (Light out) | DA 11-03-10 @ 1125pm C .Ashton pole #61231 Teardrop fixture not on list refer to Ddot 10-00379888- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90311217000 | -77.00596908000
11/3/10 | 1040690 | 2902 | BLADENSBURG RD | NE | 11/10/10 | 50099 | 5A085 | (Light out) | DA 11-09-10 @ 1101pm K. Simmons pole #50099 light is on and working DA 11-3-10 @ 225am K .Dunton pole #50099 N/C underground - low voltage - 7 volts | High Pressure Sodium | 38.92725738000 | -76.96243723000
11/1/10 | 1040458 | 0 | O ST | NW | 11/1/10 | 25844 | 6U450 | (Light out) |  | High Pressure Sodium | 38.90864165000 | -77.02306302000
11/1/10 | 1040439 | 2200 | H ST | NW | 11/1/10 | 27995 | 2A219 | (Light out) |  | High Pressure Sodium | 38.89963616000 | -77.04899852000
10/26/10 | 1036177 | 5403 | NANNIE HELEN BURROUGHS AVE | NE | 11/1/10 | 72648 | 7A191 | (Light out) | DA 10-29-10 @ 355am T Richards pole #72648 N/C underground - no voltage missing underground neturial | High Pressure Sodium | 38.89829839000 | -76.92250388000
10/26/10 | 1035841 | 2407 | 18TH ST | NW | 10/26/10 | 11533 | 1G491 | (Light out) | DA 10-26-10 @ 255am K. Dunton repaired pole #11533 | High Pressure Sodium | 38.92063969000 | -77.04213470000
10/26/10 | 1035814 | 0 | MASSACHUSETTS AVE | NW | 10/28/10 | 25939 | 2L551 | (Light out) | DA 10-28-10 @ 1030pm C .Ashton pole #25969 light found on and working removed N/C tape DA 10-26-10 @ 150am C >aShton pole #25939 N/C @ Base | High Pressure Sodium | 38.90325148000 | -77.02477750000
10/25/10 | 1035794 | 0 | WASHINGTON AVE | SW | 10/25/10 | 21662 | 6A381 | (Light out) | DA 10-25-10 @ 1125pm C .Ashton repaired pole #21662 | High Pressure Sodium | 38.88686324000 | -77.01343008000
10/25/10 | 1035793 | 0 | WASHINGTON AVE | SW | 10/25/10 | 21664 | 6A383 | (Light out) | DA 10-25-10 @ 1105pm C .Ashton repaired pole #21664 | High Pressure Sodium | 38.88653687000 | -77.01302412000
10/22/10 | 1033472 | 907 | T ST | NW | 10/22/10 | 13453 | 1L372 | (Light off/on) | DA 10-22-10 @ 420am K. Dunton repaired pole #13453 | High Pressure Sodium | 38.91563204000 | -77.02439690000
10/21/10 | 1033431 | 2022 | 14TH ST | SE | 10/25/10 | 80525 | 80525DC | (Light out) | DA 10-21-10 @ 1101pm K. Simmons pole #80525 - N/C underground - no voltage | High Pressure Sodium | 38.86531307000 | -76.98537942000
10/21/10 | 1032943 | 1200 | CONNECTICUT AVE | NW | 10/22/10 | 27221 | 2U530 | (Light out) | DA 10-22-10 @ 1205am C. Ashton repaired pole #27221 | High Pressure Sodium | 38.90584530000 | -77.04105305000
10/20/10 | 1032507 | 2010 | 14TH ST | SE | 10/25/10 | 80528 | 80528DC | (Light out) | DA 10-21-10 @ 1109pm K. Simmons pole #80528 N/C underground - no voltage 10-00364139- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86553911000 | -76.98531326000
10/20/10 | 1031589 | 1300 | 7TH ST | NW | 10/20/10 | 25660 | 6A794 | (Light out) | DA 10-20-10 @ 240am c. Ashton repaired pole #25660 | High Pressure Sodium | 38.90748515000 | -77.02201647000
10/19/10 | 1031132 | 806 | RHODE ISLAND AVE | NE | 10/20/10 | 56388DC | 5A274 | (Light out) | DA 10-20-10 @ 1259am K Simmons repaired pole #56388 | High Pressure Sodium | 38.92176361000 | -76.99420034000
10/18/10 | 1030848 | 0 | H ST | NE | 2/9/12 | 62350 | 6S120 | (Light out) | DA 10-20-10 @ 339am T> Richards pole #62350 N/C underground - no voltage SW Corner 10-00361292-This one has been out for some time. Frequent vagrants on the corner could be to blame... cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90011633000 | -76.98846372000
10/18/10 | 1029752 | 717 | BARNES ST | NE | 10/19/10 | 72462DC | 7A473 | (Light out) | DA 10-18-10 @ 1142pm T. Richards pole #72462dc light found on and working previously repaired Front 10-00360046-STREETLIGHT BURNT OUT cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90163933000 | -76.95010523000
10/18/10 | 1029745 | 2010 | 14TH ST | SE | 10/18/10 | 80528 | 80528DC | (Light out) | DA 10-18-10 @ 1039pm K .Simmons installed 90ft wire, 250hps lamp, fixture and TLPC pole #80528 ( referrred for low voltage refer to wo #1026076) Front 10-00359508- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86553911000 | -76.98531326000
10/18/10 | 1029128 | 3513 | O ST | NW | 10/19/10 | 21096 | 2G159 | (Light off/on) | DA 10-19-10 @ 410am K. Dunton repaired pole #21096 | High Pressure Sodium | 38.90777166000 | -77.06970579000
10/18/10 | 1029111 | 200 | I ST | SE | 10/20/10 | 67648 | 6A422 | (Light out) | DA 10-20-10 @ 224am T. Richards repaired pole #67648 | High Pressure Sodium | 38.87934724000 | -77.00236217000
10/17/10 | 1029057 | 2200 | H ST | NW | 10/19/10 | 27996 | 2A218 | (Light off/on) | DA 10-19-10 @ 115am C, Ashon repaired pole #27996 | High Pressure Sodium | 38.89963734000 | -77.04920747000
10/17/10 | 1029040 | 5403 | NANNIE HELEN BURROUGHS AVE | NE | 10/19/10 | 72648 | 7A191 | (Light out) | DA 10-19-10 @ 1158pm T. Richards repaired pole #72648 ( bird flap) | High Pressure Sodium | 38.89829839000 | -76.92250388000
10/17/10 | 1029039 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 10/19/10 | 71270 | 71270DC | (Light off/on) | DA 10-19-10 @ 1259am T, Richards repaired pole #71270 | High Pressure Sodium | 38.89827347000 | -76.92679095000
10/15/10 | 1028947 | 717 | BARNES ST | NE | 10/18/10 | 72462DC | 7A473 | (Light out) | DA 10-18-10 @ 411am T> Richards repaired pole #72462dc 10-00357360- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90163933000 | -76.95010523000
10/14/10 | 1028400 | 610 | I ST | NW | 10/15/10 | 22502 | 6S553 | (Light out) | DA 10-15-10 @ 300AM C. Ashton repaired pole #22502 Front 10-00356851-front cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90080788000 | -77.02049021000
10/14/10 | 1026710 | 5220 | WISCONSIN AVE | NW | 10/15/10 | 3A084DC | 3A084 | (Light out) | DA 10-15-10 @ 1210am K. Dunton repaired pole #3a084dc | High Pressure Sodium | 38.95810245000 | -77.08423960000
10/13/10 | 1026076 | 2010 | 14TH ST | SE | 10/26/10 | 80528 | 80528DC | (Light out) | DA 10-26-10 @ 145am K. Simmons pole #80528 light found on and working DA 10-18-10 @ 1039pm K. Simmons installed 250hps lamp, fixture, TLPC and 90 ft wire.(wo#1029745) pole #80528 still has low current 118 volts no underground Neturial DA 10-13-10 @ 103 | High Pressure Sodium | 38.86553911000 | -76.98531326000
10/13/10 | 1026072 | 4017 | GEORGIA AVE | NW | 10/19/10 | 4J345 | 4G277 | (Light out) | DA 10-13-10 @ 1050pm R. Warren pole #4j345 N/C underground | High Pressure Sodium | 38.94036991000 | -77.02500450000
10/12/10 | 1026025 | 0 | SHERMAN AVE | NW | 10/12/10 | 12587 | 1G451 | (Light out) | DA 10-12-10 @ 1108pm C. Ashton repaired pole #12587 | High Pressure Sodium | 38.92300485000 | -77.02549655000
10/12/10 | 1026004 | 832 | UPSHUR ST | NW | 10/13/10 | 4J745 | 4G332 | (Light out) | DA 10-12-10 @ 1146pm R. Warren repaired pole #4j745 | High Pressure Sodium | 38.94182944000 | -77.02466826000
10/12/10 | 1026002 | 4400 | GEORGIA AVE | NW | 10/13/10 | 4K024 | 4G309 | (Light out) | DA 10-13-10 @ 1238am R. Warren repaired pole #4k024 | High Pressure Sodium | 38.94410262000 | -77.02599601000
10/11/10 | 1025916 | 0 | NEW YORK AVE | NE | 10/11/10 | 50003 | 5A037 | (Light out) | DA 10-11-10 @ 816pm T .Richards repaired pole #50003 - redirected photocell | High Pressure Sodium | 38.91737165000 | -76.96995714000
10/11/10 | 1025886 | 4017 | GEORGIA AVE | NW | 2/7/12 | 4J346 | 4G281 | (Light out) | DA 10-11-10 @ 1047pm R .Warren pole #4j346 N/C underground | High Pressure Sodium | 38.94075824000 | -77.02507073000
10/11/10 | 1025885 | 4021 | 9TH ST | NW | 2/7/12 | 4J794 | 4G279 | (Light out) | DA 10-11-10 @ 1047pm R .Warren pole #4j794 N/C underground | High Pressure Sodium | 38.94051550000 | -77.02504396000
10/11/10 | 1025850 | 1800 | R ST | NW | 10/12/10 | 26233 | 2M133 | (Light out) | DA 10-11-10 @ 1106pm C .Ashton repaired pole #26233 | High Pressure Sodium | 38.91267387000 | -77.04178884000
10/10/10 | 1025755 | 3102 | CLEVELAND AVE | NW | 10/11/10 | 37361 | 37561 | (Light out) | front 10-00352623- cwDesc: STREETLIGHT REPAIR 10-11-10 A.Young---repaired (sc) | High Pressure Sodium | 38.92574190000 | -77.06111143000
10/7/10 | 1024054 | 515 | H ST | NE | 10/14/10 | 61722 | 6S062 | (Light out) | DA 10-08-10 @ 1205am C. Ashton could not access light due to construction in area 10-00350052-streetlight is out. please repair asap. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90011936000 | -76.99890875000
10/7/10 | 1023674 | 0 | 54TH ST | SE | 10/8/10 | 75595 | 75595DC | (Light out) | DA 10-08-10 @ 1231am K. Simmons repaired pole #75595 - reconnected overhead neturial | High Pressure Sodium | 38.88381578000 | -76.92397025000
10/7/10 | 1023320 | 0 | NEW YORK AVE | NE | 10/11/10 | 50008 | 5A042 | (Light out) | DA 10-11-10 @ 757pm T. Richards repaired pole #50008 | High Pressure Sodium | 38.91724347000 | -76.96648514000
10/7/10 | 1023319 | 0 | NEW YORK AVE | NE | 10/11/10 | 50006 | 5A040 | (Light out) | DA 10-11-10 @ 728pm T. Richards repaired pole #50006 | High Pressure Sodium | 38.91731218000 | -76.96789154000
10/7/10 | 1023300 | 2400 | SHERMAN AVE | NW | 10/7/10 | 12585 | 1G465 | (Light out) | DA 10-07-10 @ 337am C. Ashton repaired pole #12585 | High Pressure Sodium | 38.92169397000 | -77.02539372000
10/6/10 | 1023054 | 1423 | 35TH ST | NW | 10/7/10 | 20901 | 2G196 | (Light out) | DA 10-07-10 @ 118am C. Ashton repaired pole #20901 In front of 1423 10-00348568- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90838737000 | -77.06913765000
10/6/10 | 1022711 | 100 | 1ST ST | NE |  | 56986 | 5M095 | (Light out) | DA 10-06-10 @ 1033pm K. Simmons pole #56986 has been removed and 3rd party contractor has installed new teardrop poles and they are not yet connected | High Pressure Sodium | 38.90945362000 | -77.00612005000
10/6/10 | 1022297 | 0 | 7TH ST | NW | 10/6/10 | 22452 | 6M651 | (Light out) | DA 10-06-10 @ 225am C. Ashton repaired pole #22452 | High Pressure Sodium | 38.89955549000 | -77.02182020000
10/6/10 | 1022262 | 3600 | P ST | NW | 10/6/10 | 21003 | 2G126 | (Light out) | DA 10-06-10 @ 100am C .Ashton repaired pole #21003 | High Pressure Sodium | 38.90874440000 | -77.07034165000
10/5/10 | 1021332 | 1250 | CONNECTICUT AVE | NW | 10/5/10 | 24531 | 2U509 | (Light out) | DA 10-05-10 @ 1055pm C .Ashton repaired pole #24531 | High Pressure Sodium | 38.90701415000 | -77.04208547000
10/4/10 | 1020244 | 0 | 35TH ST | NW | 10/5/10 | 36941 | 3G109 | (Light out) | 10-5-10 A.Young---repaired (sc) | High Pressure Sodium | 38.91759465000 | -77.06949788000
10/4/10 | 1020235 | 3200 | WISCONSIN AVE | NW | 10/5/10 | 38774 | 3U388 | (Light out) | DA 10-05-10 @ 325am K. Dunton repaired pole #38774 | High Pressure Sodium | 38.93433690000 | -77.07255580000
9/30/10 | 1018054 | 1503 | TANNER ST | SE | 10/4/10 | 81775 | 88052 | (Light off/on) | DA 10-03-10 @ 1109pm K. Simmons repaired pole #81775 | High Pressure Sodium | 38.84731165000 | -76.98236222000
9/29/10 | 1017347 | 3232 | P ST | NW | 10/4/10 | 21020 | 2G149 | (Light out) | DA 10-04-10 @ 1235am C .ashton repaired pole #21020 | High Pressure Sodium | 38.90878828000 | -77.06441557000
9/29/10 | 1017346 | 3624 | P ST | NW | 10/6/10 | 21001 | 2G124 | (Light out) | DA 10-06-10 @ 1245am K .Simmons pole #21001 light found on and working DA 10-04-10 @ 153am C. Ashton pole #21001 N/C @ Base | High Pressure Sodium | 38.90872996000 | -77.07099893000
9/27/10 | 1015809 | 1000 | M ST | SE | 2/9/12 | 67367 | 6L939 | (Light out) | 4-5-11 Hudson/Jason - chk MH at p-base - was not able to find feed tried to rod duct - rod only went in 3' - traffic combo pole REFER to DDOT (VW) DA 9-28-10 @ 225am K .Dunton - temp pole refer to ddot | High Pressure Sodium | 38.87641377000 | -76.99123690000
9/26/10 | 1015404 | 1845 | 7TH ST | NW | 9/26/10 | 14314 | 1A058 | (Light out) | DA 9-26-10 @ 1005pm C. Ashton repaired pole #14314 | High Pressure Sodium | 38.91517340000 | -77.02182333000
9/26/10 | 1015391 | 0 | IOWA AVE | NW | 9/27/10 | 4K496 | 4U128 | (Light out) | DA 9-27-10 @ 1210am R Warren repaired pole #4k496 | High Pressure Sodium | 38.94605354000 | -77.02957834000
9/24/10 | 1014166 | 0 | BENNING RD | NE | 9/27/10 | 74691DC | 5M293 | (Light out) | DA 9-26-10 @ 1020pm T. Richards repaired pole #74691dc Front 10-00334055-need to be repair light out. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89758397000 | -76.96659668000
9/23/10 | 1013940 | 908 | EASTERN AVE | NE | 9/24/10 | 79483 | 7A152 | (Light out) | DA 9-24-10 @ 204am T. Richards repaired pole #79483 | High Pressure Sodium | 38.88978699000 | -76.95795735000
9/23/10 | 1013935 | 0 | KENILWORTH AVE | SE | 2/7/12 | 79497 | 7A150 | (Light out) | DA 9-23-10 @ 943pm T. Richards pole #79497 N/C underground no voltage | High Pressure Sodium | 38.88456308000 | -76.96344581000
9/23/10 | 1013184 | 600 | 1ST ST | NE | 9/23/10 | 60930 | 6U604 | (Light out) | DA 9-23-10 @ 219am T. Richards repaired pole #60930 | High Pressure Sodium | 38.89760383000 | -77.00770399000
9/22/10 | 1012983 | 600 | 1ST ST | NE | 9/23/10 | 60927 | 6U601 | (Light out) | DA 9-23-10 @ 152am T. Richards repaired pole #60927 10-00331989-odd side of street near loading dock of postal museum cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89824861000 | -77.00746947000
9/22/10 | 1012680 | 3848 | SOUTH CAPITOL ST | SE | 2/7/12 | 85647 | 8M006 | (Light off/on) | DA 9-23-10 @ 403am K. Simmons pole #85647 N/C underground | High Pressure Sodium | 38.83413920000 | -77.00815861000
9/22/10 | 1012632 | 601 | KENNEDY ST | NW | 9/26/10 | 4M067 | 4M067DC | (Light out) | DA 9-22-10 @ 1130pm R> Warren pole #4m067 N/C underground - ran 80ft wire and made 2 splices | High Pressure Sodium | 38.95648496000 | -77.02110063000
9/21/10 | 1011789 | 4200 | GEORGIA AVE | NW | 9/22/10 | 4K514 | 4G300 | (Light out) | DA 9-21-10 @ 1155pm R> Warren repaired pole #4k514 (short cap) | High Pressure Sodium | 38.94278654000 | -77.02583884000
9/21/10 | 1011727 | 1807 | MARTIN LUTHER KING JR AVE | SE | 9/21/10 | 81019 | 8L851 | (Light out) | DA 9-21-10 @ 1042pm K. Simmons repaired pole #81019 | High Pressure Sodium | 38.86789068000 | -76.98847973000
9/21/10 | 1011520 | 2201 | G ST | NW | 9/21/10 | 27947 | 2M443 | (Light out) | DA 9-21-10 @ 1206am C. Ashton repaired pole #27947 | High Pressure Sodium | 38.89827367000 | -77.04945470000
9/20/10 | 1010937 | 3233 | PENNSYLVANIA AVE | SE | 9/22/10 | 78547DC | 7E110 | (Light out) | DA 9-22-10 @ 1230am T. Richards repaired pole #78547dc | High Pressure Sodium | 38.86864144000 | -76.95900959000
9/19/10 | 1010571 | 1101 | NEW HAMPSHIRE AVE | NW | 9/20/10 | 23902 | 2G711 | (Light out) | DA 9-20-10 @ 1216am C .Ashton repaired pole #23902 | High Pressure Sodium | 38.90394590000 | -77.04867186000
9/19/10 | 1010565 | 0 | PENNSYLVANIA AVE | NW | 9/20/10 | 28039 | 2G694 | (Light out) | DA 9-20-10 @ 107am C. Ashton repaired pole #28039 | High Pressure Sodium | 38.90227133000 | -77.04894911000
9/16/10 | 1007986 | 0 | 14TH ST | NW | 9/17/10 | 12047 | 1A048 | (Light out) | DA 9-16-10 @ 1104pm C .Ashton repaired pole #12047 | High Pressure Sodium | 38.92125581000 | -77.03199899000
9/16/10 | 1007705 | 3532 | GEORGIA AVE | NW | 9/16/10 | 12969 | 1G210 | (Light out) | DA 9-16-10 @ 438am C. Ashton repaired pole #12969 | High Pressure Sodium | 38.93411676000 | -77.02407525000
9/16/10 | 1007673 | 600 | MICHIGAN AVE | NE | 9/16/10 | 53646DC | 5U708 | (Light out) | DA 9-16-10 @ 150am K. Simmons repaired pole #53646dc | High Pressure Sodium | 38.93303755000 | -76.99623620000
9/15/10 | 1007202 | 3700 | GEORGIA AVE | NW | 9/16/10 | 4J338 | 4G239 | (Light off/on) | DA 9-16-10 @ 322am R. Warren repaired pole #4j338 | High Pressure Sodium | 38.93706218000 | -77.02429716000
9/15/10 | 1006813 | 0000 | OVERLOOK AVE | SW | 9/17/10 | 81837 | 88098 | (No current) | DeVon Smith on 9-17-10. Pepco close fuse on transformer. | High Pressure Sodium | 38.83304530000 | -77.01393197000
9/15/10 | 1006812 | 0000 | OVERLOOK AVE | SW | 9/17/10 | 81836 | 88097 | (No current) | DeVon Smith on 9-17-10. Pepco close fuse on transformer. | High Pressure Sodium | 38.83334467000 | -77.01372200000
9/15/10 | 1006811 | 0000 | OVERLOOK AVE | SW | 9/17/10 | 81835 | 88096 | (No current) | DeVon Smith on 9-17-10. Pepco close fuse on transformer. | High Pressure Sodium | 38.83364467000 | -77.01350898000
9/15/10 | 1006810 | 0000 | OVERLOOK AVE | SW | 9/17/10 | 81834 | 88095 | (No current) | DeVon Smith on 9-17-10. Pepco close fuse on transformer. | High Pressure Sodium | 38.83393831000 | -77.01328820000
9/15/10 | 1006809 | 0000 | OVERLOOK AVE | SW | 9/17/10 | 81833 | 88094 | (No current) | DeVon Smith on 9-17-10. Pepco close fuse on transformer. | High Pressure Sodium | 38.83423707000 | -77.01306892000
9/15/10 | 1006808 | 0000 | OVERLOOK AVE | SW | 9/17/10 | 81832 | 88093 | (No current) | DeVon Smith on 9-17-10. Pepco close fuse on transformer. | High Pressure Sodium | 38.83453118000 | -77.01284962000
9/15/10 | 1006807 | 0000 | OVERLOOK AVE | SW | 9/17/10 | 81831 | 88092 | (No current) | DeVon Smith on 9-17-10. Pepco close fuse on transformer. | High Pressure Sodium | 38.83482648000 | -77.01263154000
9/15/10 | 1006806 | 0000 | OVERLOOK AVE | SW | 9/17/10 | 81830 | 88091 | (No current) | DeVon Smith on 9-17-10. Pepco close fuse on transformer. | High Pressure Sodium | 38.83513004000 | -77.01240514000
9/15/10 | 1006777 | 3375 | WISCONSIN AVE | NW | 9/15/10 | 38775 | 3U386 | (Light out) | DA 9-15-10 @ 245am K. Dunton repaired pole #38775 | High Pressure Sodium | 38.93401705000 | -77.07253869000
9/15/10 | 1006774 | 0 | WISCONSIN AVE | NW | 9/15/10 | 30178 | 3G016 | (Light out) | DA 9-15-10 @ 210am K .Dunton repaired pole #30178 | High Pressure Sodium | 38.92652860000 | -77.07306865000
9/14/10 | 1005752 | 1218 | CONNECTICUT AVE | NW | 2/9/12 | 24532 | 2U519 | (Light out) | DA 9-15-10 @ 355am C .ashton pole #24532 N/C @ Base Front 10-00321198-street light is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90651643000 | -77.04185036000
9/14/10 | 1005561 | 3100 | BLADENSBURG RD | NE | 9/16/10 | 51244DC | 5A144DC | (Light out) | DA 9-16-10 @ 245am K .Dunton repaired pole #51244dc | High Pressure Sodium | 38.94258460000 | -76.99602786000
9/14/10 | 1005528 | 5300 | SOUTH DAKOTA AVE | NE | 2/7/12 | 4P563DC | 4P570 | (Light out) | DA 9-14-10 @ 1134pm R. Warren pole #4p563dc N/C to Overhead | High Pressure Sodium | 38.95614032000 | -77.00115198000
9/14/10 | 1005502 | 1700 | RHODE ISLAND AVE | NW | 9/14/10 | 26383 | 2U538 | (Light out) | DA 9-14-10 @ 215am C, Ashton repaired pole #26383 | High Pressure Sodium | 38.90590732000 | -77.04061898000
9/12/10 | 1004724 | 3945 | PENNSYLVANIA AVE | SE | 9/13/10 | 78518DC | 7E149DC | (Light out) | DA 9-13-10 @ 140am K .Dunton repaired pole #78518dc | High Pressure Sodium | 38.86392263000 | -76.94743025000
9/12/10 | 1004701 | 905 | N ST | NW | 9/13/10 | 25573 | 2A114 | (Light out) | DA 9-13-10 @ 326am C .aShton repaired pole #25573 | High Pressure Sodium | 38.90720051000 | -77.02440349000
9/10/10 | 1003122 | 1000 | 4TH ST | SE | 9/10/10 | 67544 | 6A436 | (Light out) | DA 9-10-10 @ 121am T .Richards repaired pole #67544 | High Pressure Sodium | 38.87791653000 | -77.00064890000
9/10/10 | 1003096 | 1201 | BRENTWOOD PKY | NE | 9/10/10 | 56830 | 5M058 | (Light out) | DA 9-10-10 @ 158am K .Simmons repaired pole #56830 | High Pressure Sodium | 38.91354293000 | -76.99082318000
9/9/10 | 1003080 | 0 | U ST | NW | 9/9/10 | 12574 | 1G539 | (Light out) | DA 9-9-10 @ 1005pm C, Ashton repaired pole #12574 | High Pressure Sodium | 38.91709775000 | -77.02763641000
9/9/10 | 1001782 | 3532 | GEORGIA AVE | NW | 9/9/10 | 12969 | 1G210 | (Light out) | DA 9-9-10 @ 336am C ,AShton repaired pole #12969 | High Pressure Sodium | 38.93411676000 | -77.02407525000
9/9/10 | 1001745 | 919 | L ST | NW | 9/9/10 | 29202 | 2L562 | (Light out) | DA 9-8-10 @ 1022pm C .ashton repaired pole #29202 | High Pressure Sodium | 38.90411036000 | -77.02503736000
9/7/10 | 1000201 | 815 | KENNEDY ST | NW | 9/9/10 | 4M078 | 4M078DC | (Light out) | DA 9-9-10 @ 1210am R. WArren repaired pole #4m078 | High Pressure Sodium | 38.95637067000 | -77.02492280000
9/7/10 | 1000174 | 1743 | 18TH ST | NW | 9/8/10 | 26752 | 2M124 | (Light out) | DA 9-7-10 @ 1118pm C .AShton repaired pole #26752 | High Pressure Sodium | 38.91344712000 | -77.04160072000
9/7/10 | 1000103 | 2400 | OBSERVATORY PL | NW | 9/9/10 | 36742 | 36742DC | (Light out) | DA 9-9-10 @ 1235am K .Dunton repaired pole #36742 | High Pressure Sodium | 38.92165320000 | -77.07512015000
9/6/10 | 999819 | 2828 | WISCONSIN AVE | NW | 9/7/10 | 30136 | 3G013 | (Light out) | DA 9-7-10 @ 300am K .Dunton repaired pole #30136 | High Pressure Sodium | 38.92695687000 | -77.07330485000
9/2/10 | 997812 | 1601 | 18TH ST | NW | 2/7/12 | 26773 | 2M145 | (Light out) | DA 9-3-10 @ 1210am C .Ashton pole #26773 N/C underground - construction in area | High Pressure Sodium | 38.91132223000 | -77.04173550000
9/1/10 | 996150 | 800 | 23RD ST | NW | 9/1/10 | 28340 | 2A234 | (Light out) | DA 9-1-10 @ 127am C. Ashton repaired pole #28340 | High Pressure Sodium | 38.89992932000 | -77.05001890000
8/30/10 | 994842 | 3900 | GEORGIA AVE | NW | 8/30/10 | 4J354 | 4G266 | (Light out) | DA 8-30-10 @ 1110pm R. Warren repaired pole #4j354 | High Pressure Sodium | 38.93907624000 | -77.02491081000
8/30/10 | 994840 | 2206 | 18TH ST | NW | 8/31/10 | 11411 | 1G502 | (Light out) | DA 8-31-10 @ 240am K .Dunton repaired pole #11411 | High Pressure Sodium | 38.91905896000 | -77.04152631000
8/30/10 | 994787 | 3458 | PENNSYLVANIA AVE | SE | 8/31/10 | 78530DC | 7E129DC | (Light out) | DA 8-30-10 @ 1125pm T. Richards repaired pole #78530dc (light on upon arrival) | High Pressure Sodium | 38.86643024000 | -76.95357155000
8/30/10 | 994761 | 1330 | NEW HAMPSHIRE AVE | NW | 8/31/10 | 24477 | 2G768 | (Light out) | DA 8-31-10 @ 445am C. Ashton repaired pole #24477 | High Pressure Sodium | 38.90790996000 | -77.04519509000
8/30/10 | 994736 | 800 | 23RD ST | NW | 9/1/10 | 28340 | 2A234 | (Light out) | DA 9-1-10 @ 127am C. Ashton repaired pole #28340 using 400hps lamp refer to wo #996150 | High Pressure Sodium | 38.89992932000 | -77.05001890000
8/26/10 | 992517 | 4612 | 12TH ST | NE | 8/31/10 | 51256DC | 5A150DC | (Light out) | DA 8-30-10 @ 1100pm K. Simmons reattached overhead hot and neturial pole #51256dc | High Pressure Sodium | 38.94542966000 | -76.99072288000
8/26/10 | 991608 | 501 | H ST | NW | 8/26/10 | 60495 | 6S546 | (Light out) | DA 8-26-10 @ 410am C.Ashton repaired pole #60495 | High Pressure Sodium | 38.89990452000 | -77.01906652000
8/26/10 | 991596 | 0 | 7TH ST | NW | 8/26/10 | 22452 | 6M651 | (Light out) | DA 8-26-10 @ 331am C. Ashton repaired pole #22452 | High Pressure Sodium | 38.89955549000 | -77.02182020000
8/26/10 | 991595 | 737 | 7TH ST | NW | 8/26/10 | 22450 | 6M647 | (Light out) | DA 8-26-10 @ 315am C. AShton repaired pole #22450 | High Pressure Sodium | 38.89929255000 | -77.02181765000
8/26/10 | 991593 | 1771 | N ST | NW | 8/26/10 | 27182 | 2U512 | (Light out) | DA 8-26-10 @ 245am C. Ashton repaired pole #27182 | High Pressure Sodium | 38.90719403000 | -77.04157485000
8/26/10 | 991592 | 1147 | CONNECTICUT AVE | NW | 8/26/10 | 27220 | 2U544 | (Light out) | DA 8-26-10 @ 225am C. Ashton repaired pole #27220 | High Pressure Sodium | 38.90537241000 | -77.04079316000
8/26/10 | 991577 | 0 | SHERMAN AVE | NW | 8/26/10 | 12584 | 1G473 | (Light out) | DA 8-26-10 @ 1205am C.ashton repaired pole #12584 | High Pressure Sodium | 38.92101625000 | -77.02534481000
8/25/10 | 991092 | 4100 | GEORGIA AVE | NW | 8/27/10 | 4J350 | 4J025 | (Light out) | DA 8-27-10 @ 255am K .Dunton repaired pole #4j350 | High Pressure Sodium | 38.94087801000 | -77.02540931000
8/24/10 | 990441 | 601 | KENNEDY ST | NW | 8/26/10 | 4M067 | 4M067DC | (Light out) | DA 8-26-10 @ 132am R. Warren repaired pole #4m067 | High Pressure Sodium | 38.95648496000 | -77.02110063000
8/24/10 | 990223 | 0 | NEW YORK AVE | NW | 8/25/10 | 22914 | 2L029 | (Light out) | DA 8-25-10 @ 405am C. Ashton repaired pole #22914 | High Pressure Sodium | 38.90105629000 | -77.02684066000
8/24/10 | 990138 | 5000 | NANNIE HELEN BURROUGHS AVE | NE | 8/25/10 | 71278DC | 7A212 | (Light out) | DA 8-25-10 @ 347am T. Richards redirected photocell pole #71278dc | High Pressure Sodium | 38.89843573000 | -76.92937719000
8/23/10 | 989371 | 0 | H ST | NE | 8/24/10 | 62350 | 6S120 | (Light out) | DA 8-24-10 @ 408am T. Richards repaired pole #62350 | High Pressure Sodium | 38.90011633000 | -76.98846372000
8/22/10 | 988650 | 16 | FLORIDA AVE | NE | 8/22/10 | 56993 | 5M148 | (Light out) | DA 8-22-10 @ 1000pm K/ Simmons repaired pole #56993 | High Pressure Sodium | 38.91067346000 | -77.00853665000
8/18/10 | 986125 | 0 | ANACOSTIA FWY | SE | 8/20/10 | 79481 | 7A145 | (Light out) | DA 8-20-10 @ 211am T. Richards repaired pole #79481 | High Pressure Sodium | 38.88647157000 | -76.96221690000
8/17/10 | 984464 | 0000 | H ST | NE | 8/20/10 | 68259DC | 68259 | (Light out) | DA 8-19-10 @ 904pm T. Richards repaired pole #68259dc ( bird flap) Needs Big Boom and MOT | High Pressure Sodium | 38.90033650000 | -77.00847314000
8/17/10 | 984461 | 425 | MASSACHUSETTS AVE | NW | 8/19/10 | 60482 | 6A192 | (Light out) | DA 8-19-10 @ 101am T. Richards repaired pole #60482 | Mercury Vapor | 38.90049835000 | -77.01683728000
8/16/10 | 983814 | 3356 | PENNSYLVANIA AVE | SE | 8/18/10 | 78539DC | 7E120DC | (Light off/on) | DA 8-17-10 @ 1154pm T. richards repaired pole #78539dc | High Pressure Sodium | 38.86758817000 | -76.95639801000
8/16/10 | 983788 | 3845 | PENNSYLVANIA AVE | SE | 8/18/10 | 77880DC | 7E012 | (Light out) | DA 8-18-10 @ 1208am T. Richards repaired pole #77880dc | High Pressure Sodium | 38.86541018000 | -76.95063108000
8/16/10 | 983686 | 4200 | GEORGIA AVE | NW | 8/20/10 | 4K514 | 4G300 | (Light out) | DA 8-20-10 @ 322am R. Warren pole #4k514 light is on and working needs TL pole cap | High Pressure Sodium | 38.94278654000 | -77.02583884000
8/15/10 | 983014 | 2512 | SHERIDAN RD | SE | 8/15/10 | 81366DC | 8M051 | (Light out) | DA 8-15-10 @ 1136pm K. Simmons repaired pole #81366dc | High Pressure Sodium | 38.85995179000 | -76.99345916000
8/15/10 | 982997 | 0 | NEW YORK AVE | NE | 8/20/10 | 50009 | 5A043 | (Light out) | DA 8-16-10 @ 150am K. Simmons pole #50009 needs Big Boom and MOT | High Pressure Sodium | 38.91719217000 | -76.96575011000
8/15/10 | 982959 | 1331 | CONNECTICUT AVE | NW | 8/16/10 | 24528 | 2U495 | (Light out) | DA 8-16-10 @ 1240am K. Dunton repaired pole #24528 | High Pressure Sodium | 38.90805642000 | -77.04271948000
8/15/10 | 982953 | 2209 | WASHINGTON CIR | NW | 8/18/10 | 24657 | 2G676 | (Light out) | DA 8-18-10 @ 300am C. Ahton repaired pole #24657 | High Pressure Sodium | 38.90276536000 | -77.04937893000
8/15/10 | 982952 | 2124 | I ST | NW | 8/17/10 | 28107 | 2A184 | (Light out) | DA 8-17-10 @ 130am K. Dunton repaired pole #28107 | High Pressure Sodium | 38.90064216000 | -77.04764401000
8/13/10 | 981464 | 3033 | BLADENSBURG RD | NE | 2/7/12 | 58720DC | 5A172DC | (Light out) | DA 8-17-10 @ 1103pm K. simmons could not access light due to dumpster blocking alley 10-00280644-wooden pole light out cwDesc: ALLEYLIGHT REPAIR | Incandescent | 38.92960546000 | -76.95868010000
8/12/10 | 980646 | 600 | 1ST ST | NE | 8/13/10 | 60927 | 6U601 | (Light out) | DA 8-13-10 @ 226am T. Richards pole #60927 light was on upon arrival installed 400 powerdoor | High Pressure Sodium | 38.89824861000 | -77.00746947000
8/11/10 | 979506 | 30 | FLORIDA AVE | NE | 8/12/10 | 56984 | 5M089 | (Light out) | DA 8-12-10 @ 351am K. Simmons repaired pole #56984 | High Pressure Sodium | 38.91031777000 | -77.00814524000
8/11/10 | 979472 | 1301 | U ST | NW | 8/12/10 | 11721 | 1G521 | (Light off/on) | DA -8-11-10 @ 1145pm C. Ashton repaired pole #11721 | High Pressure Sodium | 38.91709342000 | -77.03069626000
8/11/10 | 979190 | 1215 | CONNECTICUT AVE | NW | 8/11/10 | 24533 | 2U523 | (Light out) | DA 8-11-10 @ 130am C .ashton repaired pole #24533 | High Pressure Sodium | 38.90616068000 | -77.04157912000
8/10/10 | 978534 | 4121 | GEORGIA AVE | NW | 8/11/10 | 4J347 | 4G291 | (Light off/on) | DA 8-10-10 @ 1100pm R. Warren repaired pole #4j347 | High Pressure Sodium | 38.94149651000 | -77.02529646000
8/10/10 | 978408 | 0 | L ST | SE | 8/12/10 | 67701 | 6A438 | (Light out) | DA 8-11-10 @ 1138pm T. Richards repaired pole #67701 | High Pressure Sodium | 38.87758258000 | -77.00088038000
8/9/10 | 977578 | 2500 | SHERIDAN RD | SE | 8/10/10 | 81361DC | 88103 | (Light out) | DA 8-10-10 @ 121am K Simmons pole #81361dc - N/C to overehead | High Pressure Sodium | 38.85871022000 | -76.99326612000
8/9/10 | 977577 | 0 | STANTON RD | SE | 8/10/10 | 81360DC | 88104 | (Light out) | DA 8-10-10 @ 121am K Simmons pole #81360dc - N/C to overehead | High Pressure Sodium | 38.85852446000 | -76.99323709000
8/9/10 | 977576 | 4500 | SHERIDAN RD | SE | 8/10/10 | 81359DC | 8U644 | (Light out) | DA 8-10-10 @ 1010pm K. Simmons pole #81359dc light found on and working DA 8-10-10 @ 121am K Simmons pole #81359dc - N/C to overehead | High Pressure Sodium | 38.85817131000 | -76.99317521000
8/6/10 | 976480 | 457 | MASSACHUSETTS AVE | NW | 8/9/10 | 60481 | 6A195 | (Light out) | DA 8-9-10 K. Simmons -light is actually double kit pole #60481 10-00272448-An abandonded teardrop streetlight was left standing after streetscape improvements and needs to be removed. It is located mid-block on the north side of the street. cwDesc: STR | High Pressure Sodium | 38.90073307000 | -77.01753805000
8/6/10 | 975698 | 1007 | NEW HAMPSHIRE AVE | NW | 8/6/10 | 23863 | 2G706 | (Light out) | DA 8-6-10 @ 245am C. Ashton repaired pole #23863 | High Pressure Sodium | 38.90335191000 | -77.04923699000
8/3/10 | 972715 | 1801 | 18TH ST | NW | 8/3/10 | 26751 | 2M113 | (Light out) | DA 8-2-10 @ 1120pm C. Ashton repaired pole #26751 TL Adapter | High Pressure Sodium | 38.91419269000 | -77.04157712000
8/2/10 | 971979 | 0 | MICHIGAN AVE | NE | 8/2/10 | 53647DC | 5U715 | (Light out) | DA 8-2-10 @ 207am K .Simmons repaired pole #53647dc | Mercury Vapor | 38.93277908000 | -76.99689474000
8/1/10 | 971919 | 0 | BRANDYWINE ST | NW | 8/2/10 | 3A230DC | 3A230 | (Light out) | DA 8-2-10 @ 330am K .Dunton pole #3a230dc defective inc fixture - referred to ddot refer to wo #869647 | High Pressure Sodium | 38.94974018000 | -77.08081828000
7/30/10 | 971437 | 1215 | 18TH ST | NW | 8/3/10 | 26765 | 2U518 | (Light out) | DA 8-2-10 @ 1110pm C. Ashton pole #26765 light found on and working Alley 10-00263973- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.90652301000 | -77.04146586000
7/30/10 | 970425 | 2201 | G ST | NW | 7/30/10 | 27947 | 2M443 | (Light out) | DA 7-30-10 @ 145am C. Ashton repaired pole #27947 | High Pressure Sodium | 38.89827367000 | -77.04945470000
7/29/10 | 970390 | 0 | 9TH ST | NW | 8/4/10 | 25436 | 2L559 | (Light out) | DA 8-3-10 @ 1145pm C. Ashton pole #25436 light found on and working Al Young completed on 8-2-10 Found OK, 120V at the fixture. BCM 7/29/10 10:25p - C. Ashton low voltaqe No Current | High Pressure Sodium | 38.90407457000 | -77.02409965000
7/29/10 | 969694 | 1421 | 37TH ST | NW | 8/2/10 | 21143 | 2G207 | (Light out) | DA 8-2-10 @ 315am C. Ashton repaired pole #21143 | High Pressure Sodium | 38.90829140000 | -77.07156966000
7/28/10 | 968886 | 631 | BARNES ST | NE | 7/31/10 | 72468 | 7U751 | (Light out) | DA 7-29-10 @ 332am T .Richards pole #72468 N/C Underground | High Pressure Sodium | 38.90045955000 | -76.95160664000
7/28/10 | 968884 | 643 | BARNES ST | NE | 7/31/10 | 72469 | 7U750 | (Light out) | DA 7-29-10 @ 332am T .Richards pole #72469 N/C Underground | High Pressure Sodium | 38.90075954000 | -76.95122635000
7/28/10 | 968844 | 45 | L ST | NE | 8/1/10 | 61204 | 6A244 | (Light out) | DA 8-1-10 @ 1129pm T .Richards repaired pole #61204 (corroded contact with bulb) | High Pressure Sodium | 38.90379039000 | -77.00717091000
7/27/10 | 968375 | 2010 | 14TH ST | SE | 8/29/10 | 80528 | 80528DC | (Light out) | DA 8-29-10 @ 1008pm K Simmons pole #80528 light is on and working DA 7-28-10 @ 1215am K .Simmons pole #80528 Refer to underground fault crew - pole reads 113volts when photocell off and 82 volts when on | High Pressure Sodium | 38.86553911000 | -76.98531326000
7/27/10 | 967810 | 0 | WISCONSIN AVE | NW | 7/28/10 | 38770 | 3U406 | (Light out) | DA 7-27-10 @ 1130pm K .Dunton repaired pole #38770 | High Pressure Sodium | 38.93584295000 | -77.07318687000
| 967379 | 2007 | 18TH ST | NW | 7/29/10 | 11540 | 1G512 | (Light out) | DA 7-29-10 @ 345am K .Dunton repaired pole #11540 10-00257456- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91748766000 | -77.04154150000
7/26/10 | 966924 | 2500 | SHERIDAN RD | SE | 7/27/10 | 81367DC | 8M053 | (Light out) | DA 7-26-10 @ 1140pm K .Simmons repaired pole #81367dc - reconected hot wire | High Pressure Sodium | 38.86029651000 | -76.99351508000
7/23/10 | 964985 | 3600 | P ST | NW | 7/26/10 | 21003 | 2G126 | (Light out) | DA 7-26-10 2 220am C. Ashton repaired poel #21003 Front 10-00253299-blinks on and off for about a week and a half cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90874440000 | -77.07034165000
7/22/10 | 964743 | 1218 | CONNECTICUT AVE | NW | 2/9/12 | 24532 | 2U519 | (Light out) | DA 7-26-10 @ 305am C> AShton pole #24532 N/C Underground | High Pressure Sodium | 38.90651643000 | -77.04185036000
7/22/10 | 964159 | 0 | L ST | SE | 7/26/10 | 67701 | 6A438 | (Light out) | DA 7-22-10 @ 1137pm K. Simmons pole #67701 N/C underground | High Pressure Sodium | 38.87758258000 | -77.00088038000
7/22/10 | 964157 | 1000 | HALF ST | SE | 7/23/10 | 67437 | 6B103 | (Light out) | DA 7-22-10 @ 1131pm K .Simmons repaired pole #67437 | High Pressure Sodium | 38.87769232000 | -77.00752782000
7/22/10 | 964113 | 0 | 23RD ST | NW | 2/2/12 | 28342 | 2M279 | (Light out) | DA 7-22-10 @ 1050pm C. Ashton pole #28342 No Access due to construction - no info | High Pressure Sodium | 38.90081677000 | -77.05001410000
7/22/10 | 964112 | 200 | 23RD ST | NW | 2/2/12 | 28319 | 2M276 | (Light out) | DA 7-26-10 @ 220am C> Ashton could not access light due to construction - Clark Construction co. | High Pressure Sodium | 38.89259094000 | -77.05025420000
7/21/10 | 963768 | 2611 | POMEROY RD | SE | 7/21/10 | 81349DC | 8U662 | (Light out) | DA 7-21-10 @ 1000pm K. Simmons repaired pole #81349dc | High Pressure Sodium | 38.85564643000 | -76.99229526000
7/21/10 | 962898 | 0000 | MONROE ST | NE | 7/23/10 | 52504DC | 5A165DC | (Light out) | DA 7-23-10 @ 352am K. Simmons repaired pole #52504dc | High Pressure Sodium | 38.93229659000 | -76.99488754000
| 962413 | 1800 | Q ST | NW | 7/21/10 | 26293 | 2M148 | (Light out) | DA 7-21-10 @ 125am C .AShton repaired pole #26293 Front 10-00244646-caller states that streetlight out for about 4 days and before it burnt out it was on for 24 hours a day that's probably the cause for the burnout cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91118563000 | -77.04218793000
| 959338 | 3960 | PENNSYLVANIA AVE | SE | 7/21/10 | 78580DC | 7E006DC | (Light out) | DA 7-21-10 @ 241am T .Richards all lights and poles found okay - wire is loose telephone line Block 10-00248109- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86466564000 | -76.94882256000
7/20/10 | 959559 | 3200 | KENYON PL | NW | 2/7/12 | 14683 | 1G052 | (Light out) | DA 7-21-10 @ 310am K .Dunton pole #14683 N/C Underground | High Pressure Sodium | 38.93003166000 | -77.03236323000
7/20/10 | 959064 | 3960 | PENNSYLVANIA AVE | SE | 7/21/10 | 78580DC | 7E006DC | (Light out) | DA 7-21-10 @ 241am T .Richards all lights and poles found okay - wire is loose telephone line 10-00247741-WIRE IS HANGING FROM LAMP POST....PLEASE INSPECT AND ASSIST IMMEDIATELY....THANK YOU.....ALOT OF A.M TRAFFIC COMES THIS WAY...WIRE COULD BE HAZARD | High Pressure Sodium | 38.86466564000 | -76.94882256000
7/20/10 | 959142 | 711 | 4TH ST | NW | 2/7/12 | 60453 | 6S473 | (Light out) | DA 7-20-10 @ 1020pm C /Ashton pole #60453 N/C underground | High Pressure Sodium | 38.90264718000 | -77.01608462000
7/20/10 | 959040 | 0 | ANACOSTIA FWY | SE | 7/20/10 | 79491 | 7A160 | (Light out) | DA 7-19-10 @ 1047pm T. Richards repaired pole #79491 | High Pressure Sodium | 38.88928656000 | -76.95990942000
7/20/10 | 959038 | 0 | NEW YORK AVE | NE | 7/20/10 | 50008 | 5A042 | (Light out) | DA 7-19-10 @ 940pm T. Richards repaired pole #50008 | High Pressure Sodium | 38.91724347000 | -76.96648514000
7/19/10 | 958915 | 0 | D ST | SW | 7/20/10 | 21554 | 6A359 | (Light out) | DA 7-19-10 @ 1100pm C. Ashton repaired pole #21554 | High Pressure Sodium | 38.88513671000 | -77.01505083000
7/18/10 | 958563 | 4649 | 48TH ST | NE | 7/19/10 | 71297DC | 7A228 | (Light out) | DA 7-18-10 @ 1043pm K .Simmons repaired pole #71297dc | High Pressure Sodium | 38.89911096000 | -76.93384917000
7/16/10 | 958478 | 3850 | GEORGIA AVE | NW | 2/7/12 | 4J355 | 4G260 | (Light out) | DA 7-16-10 @ 330am C .Ashton pole #4j355 N/C underground | High Pressure Sodium | 38.93855929000 | -77.02474527000
7/15/10 | 958456 | 900 | 17TH ST | NE | 7/16/10 | 59373 | 5M004 | (Light out) | DA 7-16-10 @ 101am K. Simmons repaired pole #59373 | High Pressure Sodium | 38.90100292000 | -76.97890516000
7/15/10 | 957687 | 600 | 1ST ST | NE | 7/16/10 | 60927 | 6U601 | (Light out) | 7-16-10 H.Lancaster---unable to find pole (sc) | High Pressure Sodium | 38.89824861000 | -77.00746947000
7/15/10 | 957495 | 0 | INTERSTATE 295 | SE | 7/16/10 | 68025 | 6U010 | (Light out) | DA 7-16-10 @ 306am T. Richards repaired pole #68025 | High Pressure Sodium | 38.87708996000 | -76.98903583000
7/15/10 | 957485 | 0 | NEW YORK AVE | NE | 7/20/10 | 50004 | 5A038 | (Light out) | DA 719-10 @ 927pm T. Richards repaired pole #50004 DA 7-19-10 @ 314am K. Simmons pole #50004 needs big boom and MOT | High Pressure Sodium | 38.91736785000 | -76.96929432000
7/15/10 | 957481 | 1900 | 37TH ST | NW | 7/16/10 | 36891 | 30482 | (Light off/on) | DA 7-16-10 @ 330am K. Dunton repaired pole #36891 | High Pressure Sodium | 38.91672906000 | -77.07292654000
7/14/10 | 956258 | 0 | 22ND ST | NW | 7/15/10 | 23904 | 2G784 | (Light out) | DA 7-15-10 @ 115am C .ashton repaired pole #23904 | High Pressure Sodium | 38.90422508000 | -77.04874413000
7/13/10 | 954913 | 900 | UPSHUR ST | NW | 7/13/10 | 4J743 | 4G313 | (Light out) | DA 7-13-10 @ 355am R. Warren repaired pole #4j743 | High Pressure Sodium | 38.94182528000 | -77.02576756000
7/9/10 | 952194 | 6950 | MAPLE ST | NW | 7/9/10 | 4H590DC | 4L605 | (Light out) | DA 7-9-10 @ 421am R. Warren repaired pole #4h590dc | High Pressure Sodium | 38.97397272000 | -77.01544302000
7/8/10 | 952055 | 0000 | 15TH PL | SE | 7/9/10 | 81780 | 88057 | (Light out) | DA 7-9-10 @ 154am K .Simmons repaired pole #81780 | High Pressure Sodium | 38.84932860000 | -76.98242224000
7/8/10 | 952054 | 1418 | TOBIAS DR | SE | 7/9/10 | 81787 | 88064 | (Light out) | DA 7-9-10 @ 127am K. Simmns repaired pole #81787 | High Pressure Sodium | 38.85052622000 | -76.98343381000
7/8/10 | 952016 | 1224 | H ST | NE | 7/13/10 | 62348 | 6S114 | (Light out) | DA 7-13-10 @ 1201am T. Richards pole #62348 light is on and working 7-9-10 D.Dixon---no current (sc) | High Pressure Sodium | 38.90011721000 | -76.98943529000
7/8/10 | 951066 | 888 | 1ST ST | NE | 7/8/10 | 61224 | 6S501 | (No current) |  | High Pressure Sodium | 38.90219520000 | -77.00581473000
7/6/10 | 949572 | 900 | 4TH ST | SE | 7/7/10 | 67536 | 6A429 | (Light out) | DA 7-7-10 @ 124am T .Richards redirected photocell pole #67536 | High Pressure Sodium | 38.87918965000 | -77.00064880000
7/5/10 | 948676 | 0 | 13TH PL | NW | 7/23/10 | 4J740 | 4U153 | (Light out) | DA 7-23-10 @ 1205am R> Warren pole #4j740 light found on and working DA 7-6-10 @ 257am R. Warren pole #4j740 N/C underground | High Pressure Sodium | 38.94182450000 | -77.02958631000
7/2/10 | 947109 | 0400 | TAYLOR ST | NE | 7/2/10 | 50088 | 5A069 | (Light out) | DA 7-2-10 @ 225am K. Simmons repaired pole #50088 | High Pressure Sodium | 38.94068397000 | -77.00029052000
7/2/10 | 947100 | 0 | INTERSTATE 295 | SE | 2/2/12 | 86513 | 8L772 | (Light out) | DA 7-15-10 Refer to DDot - 11TH STREET BRIDGE PROJECT DA 7-12-10 @ 1033pm T. Richards pole #86513 light is still off - N/C DA 7-2-10 @ 1218am T .Richards pole #86513 N/C underground - (part of the 11th street bridge project) | High Pressure Sodium | 38.86640747000 | -76.99106026000
7/2/10 | 947098 | 0 | INTERSTATE 295 | SE | 4/16/12 | 86511 | 8L770 | (Light out) | DA 7-15-10 Refer to DDot - 11TH STREET BRIDGE PROJECT DA 7-12-10 @ 1033pm T. Richards pole #86511 light is still off - N/C DA 7-2-10 @ 1218am T .Richards pole #86511 N/C underground - (part of the 11th street bridge project) | High Pressure Sodium | 38.86604296000 | -76.99135445000
7/2/10 | 947097 | 0 | INTERSTATE 295 | SE | 2/2/12 | 86510 | 8L768 | (Light out) | DA 7-12-10 @ 1033pm T. Richards pole #86510 light is still off - N/C DA 7-2-10 @ 1218am T .Richards pole #86510 N/C underground - (part of the 11th street bridge project) | High Pressure Sodium | 38.86566546000 | -76.99168893000
7/2/10 | 947080 | 0 | NEW YORK AVE | NE | 7/6/10 | 50007 | 5A041 | (Light out) | DA 7-1-10 @ 1030pm T. Richards pole #50007 Refer to fault crew - A to B / 0 volts | High Pressure Sodium | 38.91727852000 | -76.96718437000
7/1/10 | 947079 | 0 | NEW YORK AVE | NE | 7/6/10 | 50010 | 5A044 | (Light out) | DA 7-1-10 @ 1030pm T. Richards pole #50010 Refer to Fault crew - AandB has current / A to B -0 Volts | High Pressure Sodium | 38.91713437000 | -76.96502016000
7/1/10 | 947078 | 0 | NEW YORK AVE | NE | 7/6/10 | 50011 | 5A045 | (Light out) | DA 7-1-10 @ 1030pm T. Richards pole #50011 Refer to fault crew - AandB has current / A to B -0 volts | High Pressure Sodium | 38.91707776000 | -76.96424700000
7/1/10 | 946395 | 4620 | EASY PL | SE | 7/6/10 | 75825 | 75825DC | (Light out) | DA 7-6-10 @ 133am T .Richards repaired pole #75825 | Incandescent | 38.87603739000 | -76.93290309000
7/1/10 | 946176 | 0 | H ST | NE | 2/7/12 | 68249DC | 68249 | (No current) | DA7-1-10 B. Black pole tag missing (metal pole) H st Bridge - N/C underground 7-14-10 S.Manning---install pole tag (sc) | High Pressure Sodium | 38.90004036000 | -77.00401332000
7/1/10 | 946174 | 0 | H ST | NE | 2/7/12 | 68250DC | 68520 | (No current) | DA7-1-10 B. Black pole #68250 (metal pole) H st Bridge - N/C underground | High Pressure Sodium | 38.87458286000 | -77.00571187000
7/1/10 | 946173 | 0000 | H ST | NE | 2/7/12 | 68248DC | 68248 | (No current) | DA7-1-10 B. Black pole #68248 (metal pole) H st Bridge - N/C underground | High Pressure Sodium | 38.90004513000 | -77.00446924000
7/1/10 | 946172 | 0000 | H ST | NE | 2/7/12 | 68247DC | 68247 | (No current) | DA7-1-10 B. Black pole #68247 (metal pole) H st Bridge - N/C underground | High Pressure Sodium | 38.90004666000 | -77.00500029000
6/30/10 | 945513 | 3600 | O ST | NW | 7/1/10 | 21091 | 2G152 | (Light out) | DA 7-1-10 @ 410am C. Ashton repaired pole #21091 | High Pressure Sodium | 38.90765383000 | -77.07088676000
6/30/10 | 945512 | 3624 | P ST | NW | 7/1/10 | 21001 | 2G124 | (Light out) | DA 7-1-10 @ 350am C. Ashton repaired pole #21001 | High Pressure Sodium | 38.90872996000 | -77.07099893000
6/30/10 | 945092 | 17 | V ST | NW | 6/30/10 | 53341DC | 53341 | (Light out) | DA 6-30-10 @ 255am K. Simmons repaired pole #53341dc | High Pressure Sodium | 38.91862284000 | -77.01031338000
6/29/10 | 944597 | 0 | EAST CAPITOL ST | SE | 6/30/10 | 73588 | 73588DC | (Light out) | DA 6-30-10 @ 241am T. Richards repaired pole #73588 | High Pressure Sodium | 38.88965078000 | -76.92405517000
6/28/10 | 943990 | 719 | T ST | NW | 6/28/10 | 13457 | 1L381 | (Light out) | DA 6-27-10 @ 10pm C. Ashton repaired pole #13457 | High Pressure Sodium | 38.91552891000 | -77.02223733000
6/28/10 | 943869 | 0 | MONROE ST | NE | 6/30/10 | 56171DC | 5U697 | (Light out) | DA 6-30-10 @ 240am K. Simmons pole #56171dc light is on and working | High Pressure Sodium | 38.93174197000 | -76.99624769000
6/25/10 | 942333 | 1300 | UPSHUR ST | NW | 6/25/10 | 4J795 | 4U152 | (Light out) | DA 6-25-10 @ 1223am R> Warren repaired pole #4j795 | High Pressure Sodium | 38.94192828000 | -77.02984643000
6/25/10 | 942332 | 0 | 13TH PL | NW | 6/25/10 | 4J740 | 4U153 | (Light out) | DA 6-25-10 @ 1210am R. Warren pole #4j740 N/C Underground | High Pressure Sodium | 38.94182450000 | -77.02958631000
6/23/10 | 941219 | 1240 | UPSHUR ST | NW | 6/29/10 | 4R784 | 4R792 | (Light out) | DA 6-23-10 @ 1059pm R. Warren repaired pole #4r784 - tightened loose connection in powerdoor REAR - ALLEY 10-00216123-SOMETIMES THE LIGHT IS ON, BUT NOT ALL THE TIME. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.94192309000 | -77.02764852000
6/23/10 | 940910 | 2307 | WASHINGTON CIR | NW | 6/24/10 | 24654 | 2G670 | (Light out) | DA 6-24-10 @ 245am . Ashton repaired pole #24654 | High Pressure Sodium | 38.90298616000 | -77.05064992000
6/23/10 | 940903 | 1778 | U ST | NW | 6/24/10 | 26113 | 21412 | (Light out) | DA 6-23-10 @ 1125pm C. AShton repaired pole #26113 | High Pressure Sodium | 38.91688186000 | -77.04131949000
6/23/10 | 940806 | 5314 | B ST | SE | 6/24/10 | 75565 | 75565DC | (Light out) | DA 6-24-10 @ 328am T. Richards repaired pole #75565 | High Pressure Sodium | 38.88626314000 | -76.92486984000
6/22/10 | 939658 | 504 | K ST | NW | 6/23/10 | 60470 | 6A104 | (Light out) | DA 6-23-10 @ 226am T. Richards repaired pole #60470 - redirected photocell | High Pressure Sodium | 38.90245334000 | -77.01925493000
6/22/10 | 939505 | 2246 | WISCONSIN AVE | NW | 6/23/10 | 30168 | 3G060 | (Light out) | DA 6-23-10 @ 354am K .Dunton repaired pole #30168 | High Pressure Sodium | 38.92229303000 | -77.07261902000
6/22/10 | 939293 | 1786 | U ST | NW | 6/22/10 | 26114 | 21411 | (Light out) | 10-00213089- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91679078000 | -77.04149873000
6/22/10 | 939291 | 0 | 7TH ST | NW | 6/22/10 | 25706 | 6A832 | (Light out) | DA 6-22-10 @ 410am C >Shton repaired pole #25706 | High Pressure Sodium | 38.91270444000 | -77.02180700000
6/21/10 | 939239 | 1909 | 14TH ST | SE | 6/24/10 | 80533 | 8M017 | (Light out) | DA 6-23-10 @ 10pm K. Simmons pole #80533 light is on and working DA 6-21-10 @ 1045pm K. Simmons pole #80533 N/C Underground | High Pressure Sodium | 38.86657133000 | -76.98511960000
6/21/10 | 939238 | 1909 | 14TH ST | SE | 6/24/10 | 80532 | 8M018 | (Light out) | DA 6-23-10 @ 10pm K. Simmons pole #80532 light is on and working DA 6-21-10 @ 1040pm K. Simmons pole #80532 N/C Underground - (Needs T base door refer to wo #939243) | High Pressure Sodium | 38.86632780000 | -76.98519170000
6/21/10 | 939237 | 2010 | 14TH ST | SE | 6/23/10 | 80528 | 80528DC | (Light out) | DA 6-21-10 @ 1030pm K. Simmons pole #80528 N/C underground - bad neturial | High Pressure Sodium | 38.86553911000 | -76.98531326000
6/21/10 | 939227 | 1017 | H ST | NE | 6/21/10 | 62344 | 6S100 | (Light out) | DA 6-21-10 @ 950pm C. Ashton repaired pole #62344 | High Pressure Sodium | 38.90011948000 | -76.99200979000
6/21/10 | 939193 | 2010 | 14TH ST | SE | 6/24/10 | 80528 | 80528DC | (Light out) | DA 6-23-10 @ 10pm K. Simmons pole #80528 light is on and working DA 6-22-10 @ 1035pm K. Simmon pole #80528 N/C underground - bad neturial Front 10-00213018- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86553911000 | -76.98531326000
6/20/10 | 938290 | 2224 | 18TH ST | NW | 6/21/10 | 11536 | 1G500 | (Light out) | DA 6-21-10 @ 220am C .Ashton repaired pole #11536 | High Pressure Sodium | 38.91934203000 | -77.04175301000
6/20/10 | 938272 | 0 | SHERIDAN RD | SE | 6/21/10 | 81363DC | 8M047 | (Light out) | DA 6-20-10 @ 1055 K. Simmons repaired pole #81363dc | High Pressure Sodium | 38.85928023000 | -76.99335324000
6/20/10 | 938271 | 0 | SHERIDAN RD | SE | 6/21/10 | 81358DC | 8U646 | (Light out) | DA 6-20-10 @ 1010pm K. Simmons pole #81358dc light found on and working | High Pressure Sodium | 38.85784096000 | -76.99320039000
6/20/10 | 938243 | 4500 | SHERIDAN RD | SE | 6/21/10 | 81359DC | 8U644 | (Light out) | DA 6-20-10 @ 1015pm K. Simmons reconnected loose wire in power door pole #81359dc | High Pressure Sodium | 38.85817131000 | -76.99317521000
6/20/10 | 938242 | 0 | STANTON RD | SE | 6/21/10 | 81360DC | 88104 | (Light out) | DA 6-20-10 @ 1020pm K. Simmons repaired pole #81360dc | High Pressure Sodium | 38.85852446000 | -76.99323709000
6/20/10 | 938241 | 2500 | SHERIDAN RD | SE | 6/21/10 | 81361DC | 88103 | (Light out) | DA 6-20-10 @ 1135pm K. Simmons repaired pole #81361dc | High Pressure Sodium | 38.85871022000 | -76.99326612000
6/18/10 | 936808 | 737 | 7TH ST | NW | 6/18/10 | 22450 | 6M647 | (Light out) | DA 6-18-10 @ 201am C. ashton repaired pole #22450 | High Pressure Sodium | 38.89929255000 | -77.02181765000
6/17/10 | 935984 | 2915 | PENNSYLVANIA AVE | SE | 6/18/10 | 78568DC | 7E086DC | (Light out) | DA 6-18-10 @ 402am T. Richards pole #78568dc light is on and working - light blocked by road construction | High Pressure Sodium | 38.87173975000 | -76.96656845000
6/16/10 | 935363 | 3400 | SHERMAN AVE | NW | 6/17/10 | 13071 | 1L295 | (Light out) | DA 6-16-10 @ 1115pm C .Ashton repaired pole #13071 | High Pressure Sodium | 38.93219026000 | -77.02662830000
6/16/10 | 935288 | 900 | 17TH ST | NE | 6/17/10 | 59373 | 5M004 | (Light out) | DA 6-16-10 @ 1040pm K. Simmons repaired pole #59373 | High Pressure Sodium | 38.90100292000 | -76.97890516000
6/16/10 | 935223 | 0 | SHERIDAN RD | SE | 6/18/10 | 81356DC | 8U649 | (Light out) | DA 6-17-10 @ 1015pm K. Simmons repaired pole #81356dc | High Pressure Sodium | 38.85735331000 | -76.99328092000
6/15/10 | 934036 | 0 | 22ND ST | NW | 6/16/10 | 23904 | 2G784 | (Light out) | DA 6-16-10 @ 1209am C .Ashton repaired pole #23904 | High Pressure Sodium | 38.90422508000 | -77.04874413000
6/15/10 | 933984 | 200 | 23RD ST | NW | 6/18/10 | 28319 | 2M276 | (Light out) | DA 6-18-10 @ 1241am C. Ashton repaired pole #28319 | High Pressure Sodium | 38.89259094000 | -77.05025420000
6/15/10 | 933737 | 0 | KENILWORTH AVE | SE | 6/15/10 | 79492 | 7A161 | (Light out) | DA 6-15-10 @ 1218am T Richards repaired pole #79492 | High Pressure Sodium | 38.88905101000 | -76.96038452000
6/14/10 | 933715 | 800 | SOUTH CAPITOL ST | SE | 7/12/10 | 67058 | 68079 | (Light out) | DA 7-11-10 @ 1114pm T .Richards pole #67058 light is on and working DA 6-15-10 @ 152am T. Richards pole #67058 refer to fault crew - A to B 0 volts, A to ground 240, B to ground 240volts (MOT) | High Pressure Sodium | 38.88097735000 | -77.00880298000
6/14/10 | 933555 | 0 | ANACOSTIA FWY | SE | 6/15/10 | 79491 | 7A160 | (Light out) | DA 6-144-10 @ 1145pm T. Richards repaired pole #79491 | High Pressure Sodium | 38.88928656000 | -76.95990942000
6/14/10 | 933554 | 0 | KENILWORTH AVE | NE | 6/15/10 | 79461 | 7A125 | (Light out) | DA 6-15-10 @ 430am T .Richards repaired pole #79461 | High Pressure Sodium | 38.89037514000 | -76.95748332000
6/14/10 | 933538 | 1201 | NEW YORK AVE | NE | 6/15/10 | 56829 | 5M061 | (Light out) | DA 6-14-10 @ 1053pm T. Richards repaired pole #56829 | High Pressure Sodium | 38.91379829000 | -76.99017687000
6/14/10 | 933537 | 0 | NEW YORK AVE | NE | 6/14/10 | 50004 | 5A038 | (Light out) | DA 6-14-10 @ 1020pm T. Richards repaired pole #50004 | High Pressure Sodium | 38.91736785000 | -76.96929432000
6/14/10 | 933178 | 0 | K ST | SE | 6/17/10 | 67657 | 6B470 | (Light out) | DA 6-16-10 @ 1144pm T. Richards pole #67657 not @ this location - all lights are on and working DA 6-16-10 @ 346am T. Richards request for map | High Pressure Sodium | 38.87835831000 | -77.00020892000
6/14/10 | 933138 | 2606 | BOWEN RD | SE | 6/16/10 | 81380DC | 8M044 | (Light out) | DA 6-15-10 @ 1105pm K. Simmons repaired pole #81380dc | High Pressure Sodium | 38.85914186000 | -76.99291332000
6/14/10 | 933015 | 3901 | PENNSYLVANIA AVE | SE | 6/17/10 | 78528DC | 7E131DC | (Light out) | DA 6-17-10 @ 108am T. richards repaired pole #78528dc | High Pressure Sodium | 38.86609981000 | -76.95276035000
6/14/10 | 933013 | 3300 | PENNSYLVANIA AVE | SE | 6/17/10 | 78545DC | 7E113DC | (Light out) | DA 6-17-10 @ 1237am T. Richards pole #78545dc light found on and working | High Pressure Sodium | 38.86843179000 | -76.95846911000
6/14/10 | 933005 | 150 | RHODE ISLAND AVE | NW | 6/15/10 | 59998 | 5A190 | (Light out) | DA 6-14-10 @ 1105pm K. Simmons repaired pole #59998 Front 10-00203025- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91503228000 | -77.01379913000
6/13/10 | 932741 | 2010 | 14TH ST | SE | 6/13/10 | 80528 | 80528DC | (Light out) | DA 6-13-10 @ 1000pm K. Simmons repaired pole #80528 | High Pressure Sodium | 38.86553911000 | -76.98531326000
6/10/10 | 930366 | 2224 | 18TH ST | NW | 8/11/10 | 11536 | 1G500 | (Light out) | DA 6-10-10 @ 1155pm C. Ashton - Bad Address WBlack-6-14-10- this address does not exist | High Pressure Sodium | 38.91934203000 | -77.04175301000
6/10/10 | 930335 | 0 | 1ST ST | NE | 6/11/10 | 61240 | 6A268 | (Light out) | DA 6-11-10 @ 322am T. Richards repaired pole #61240 | High Pressure Sodium | 38.90555245000 | -77.00598444000
6/9/10 | 929344 | 0 | 13TH PL | NW | 7/21/10 | 4J740 | 4U153 | (Light out) | DA 6-9-10 @ 343am R. Warren pole #4j740 N/C underground - 21 volts - needs new wire also | High Pressure Sodium | 38.94182450000 | -77.02958631000
6/8/10 | 928300 | 0 | H ST | NE | 6/10/10 | 68257DC | 68257 | (Light out) | DA 6-10-10 @ 358am T Richards redirected photocell pole #68257dc DA 6-8-10 @ 1058pm K. Dunton -request for map | High Pressure Sodium | 38.90032958000 | -77.00695053000
6/8/10 | 928299 | 600 | 1ST ST | NE | 6/8/10 | 60927 | 6U601 | (Light out) | DA 6-8-10 @ 1053pm K. Dunton repaired pole #60927 | High Pressure Sodium | 38.89824861000 | -77.00746947000
6/8/10 | 928293 | 504 | K ST | NW | 6/9/10 | 60470 | 6A104 | (Light out) | DA 6-8-10 @ 1134pm K .Dunton pole #60470 light found on and working | High Pressure Sodium | 38.90245334000 | -77.01925493000
6/7/10 | 927553 | 900 | 7TH ST | NW | 6/8/10 | 22462 | 6A084 | (Light off/on) | DA 6-7-10 @ 1030pm C .ashton repaired pole #22462 | High Pressure Sodium | 38.90225041000 | -77.02177737000
6/7/10 | 927552 | 0 | 7TH ST | NW | 6/11/10 | 22409 | 6M688 | (Light out) | DA 6-11-10 @ 1220am C. Ashton pole #22409 light found on and working DA 6-9-10 @ 300am C. ashton pole #22409 N/C underground C. AShton repquest for map | High Pressure Sodium | 38.90199325000 | -77.02201951000
6/6/10 | 927150 | 1633 | FORT DUPONT ST | SE | 7/1/10 | 78170DC | 7A341DC | (Light out) |  | High Pressure Sodium | 38.86620718000 | -76.94625361000
6/6/10 | 927140 | 1735 | PENNSYLVANIA AVE | SE | 6/7/10 | 78542DC | 7E117DC | (Light out) | DA 6-7-10 @ 237am K .Dunton repaired pole #78542dc | High Pressure Sodium | 38.86796881000 | -76.95734397000
6/6/10 | 927139 | 3901 | PENNSYLVANIA AVE | SE | 6/7/10 | 78528DC | 7E131DC | (Light out) | DA 6-7-10 @ 256am K. Dunton repaired pole #78528dc - using TLPC refer to wo #723958 | High Pressure Sodium | 38.86609981000 | -76.95276035000
6/6/10 | 927134 | 0 | L ST | SE | 6/7/10 | 67701 | 6A438 | (Light out) | DA 6-7-10 @ 407am T .Richards pole #67701 referred to ddot refer to wo #733746 | High Pressure Sodium | 38.87758258000 | -77.00088038000
6/6/10 | 927131 | 2 | L ST | NE | 6/9/10 | 61201 | 6A240 | (Light out) | DA 6-8-10 @ 1024pm T .Richards redirected photocell pole #61201 | High Pressure Sodium | 38.90378899000 | -77.00858856000
6/6/10 | 927126 | 601 | D ST | NW | 6/9/10 | 60094 | 6S600 | (Light out) | DA 6-8-10 @ 1024pm T .Richards pole #60094 light is on and working - redirected photocell | High Pressure Sodium | 38.89486033000 | -77.02070899000
6/6/10 | 927121 | 1000 | HALF ST | SE | 6/7/10 | 67437 | 6B103 | (Light out) | DA 6-7-10 @ 359am pole #67437 Duplicate ticket refered to ddot - construction site refer to wo #901615 | High Pressure Sodium | 38.87769232000 | -77.00752782000
6/6/10 | 927109 | 1608 | 17TH ST | NW | 6/7/10 | 26735 | 2M064 | (Light out) | DA 6-7-10 @ 125am C. Ashton repaired pole #26735 | High Pressure Sodium | 38.91150195000 | -77.03856920000
6/6/10 | 927095 | 200 | 23RD ST | NW | 6/8/10 | 28319 | 2M276 | (Light out) | DA 6-8-10 @ 1210am C. Ashton repaired loose wire pole #28319 | High Pressure Sodium | 38.89259094000 | -77.05025420000
6/4/10 | 925303 | 0 | 24TH ST | NW | 6/4/10 | 24804 | 2G664 | (Light out) | DA 6-4-10 @ 310am C .Ashton repaired pole #24804 | High Pressure Sodium | 38.90272824000 | -77.05133683000
6/4/10 | 925276 | 300 | C ST | SW | 6/4/10 | 21653 | 6L622 | (Light out) | DA 6-4-10 @ 1220am C.AShton repaired pole #21653 | High Pressure Sodium | 38.88611938000 | -77.01693063000
6/4/10 | 925274 | 504 | K ST | NW | 6/4/10 | 60470 | 6A104 | (Light out) | DA 6-3-10 @ 1030pm C. Ashton repaired pole #60470 | High Pressure Sodium | 38.90245334000 | -77.01925493000
6/3/10 | 923958 | 3901 | PENNSYLVANIA AVE | SE | 6/7/10 | 78528DC | 7E131DC | (Light out) | DA 6-7-10 @ 256am K .Dunton repaired pole #78528dc | High Pressure Sodium | 38.86609981000 | -76.95276035000
6/3/10 | 923731 | 1111 | 14TH ST | NW | 6/9/10 | 27350 | 2M423 | (Light out) | DA 6-9-10 @ 205am C. AShton installed 400 lampdb, fixture, and TLPC - light is on DA 6-3-10 @ 1255am C .Ashton pole #27350 N/C Underground | High Pressure Sodium | 38.90469050000 | -77.03208800000
6/3/10 | 923726 | 0 | P ST | NE | 6/3/10 | 57339 | 5M150 | (Light out) | DA 6-3-10 @ 1245am K. Simmons repaired pole #57339 | High Pressure Sodium | 38.90969884000 | -77.00695225000
6/1/10 | 921878 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 6/7/10 | 71275 | 7A206 | (Light out) | DA 6-6-10 @ 1052pm T. Richards pole #71275 light is on and working DA 6-2-10 @ 150am T. Richards pole #71275 N/C underground | High Pressure Sodium | 38.89829113000 | -76.92838596000
6/1/10 | 921877 | 5034 | NANNIE HELEN BURROUGHS AVE | NE | 6/7/10 | 71277 | 7A209 | (Light out) | DA 6-6-10 @ 1044pm T. Richards pole #71277 light is on and working DA 6-2-10 @ 137am T> Richards pole #71277 N/C underground | High Pressure Sodium | 38.89827977000 | -76.92883394000
6/1/10 | 921876 | 0 | GRANT ST | NE | 6/2/10 | 72339DC | 7A216 | (Light out) | DA 6-2-10 @ 122am T. Richards repaired pole #72339dc | High Pressure Sodium | 38.89843429000 | -76.93131145000
6/1/10 | 921812 | 300 | 3RD ST | SW | 6/7/10 | 21551 | 6A351 | (Light out) | DA 6-67-10 @ 1245am C. Ashton pole #21551 light is on and working DA 6-01-10 @ 1021pm C. Ashton - pole #21551 - has current on neturial but there is an underground problem refer to fault crew | High Pressure Sodium | 38.88562094000 | -77.01510801000
6/1/10 | 921810 | 300 | C ST | SW | 6/1/10 | 21653 | 6L622 | (Light out) | DA 6-1-10 @ 1016pm C Ashton repaired pole #21653 | High Pressure Sodium | 38.88611938000 | -77.01693063000
6/1/10 | 921648 | 2251 | WISCONSIN AVE | NW | 6/1/10 | 30150 | 3G077 | (Light out) | DA 6-01-10 @ 210am K .Dunton repaired pole #30150 | High Pressure Sodium | 38.92040123000 | -77.07172888000
5/31/10 | 921617 | 0 | 7TH ST | NW | 6/2/10 | 22452 | 6M651 | (Light out) | DA 6-2-10 @ 201am C .Ashton repiared pole #22452 | High Pressure Sodium | 38.89955549000 | -77.02182020000
5/31/10 | 921616 | 707 | 7TH ST | NW | 6/3/10 | 22446 | 6M639 | (Light out) | DA 6-3-10 @ 400am C. ashton repaired pole #22446 | High Pressure Sodium | 38.89882117000 | -77.02182001000
5/31/10 | 921608 | 1106 | 14TH ST | NW | 6/3/10 | 27359 | 2M409 | (Light out) | DA 6-3-10 @ 115am C .Ashton pole #27359 light is on and working DA 6-01-10 @ 323am C Ashton pole #27359 N/C underground | High Pressure Sodium | 38.90427482000 | -77.03181498000
5/28/10 | 920194 | 3425 | 14TH ST | NE | 5/28/10 | 51210DC | 5A099DC | (Light out) | DA 5-28-10 @ 235am K. Simmons repaired pole #51210dc | High Pressure Sodium | 38.93246169000 | -76.98640494000
5/28/10 | 920190 | 1101 | 14TH ST | NW | 6/3/10 | 27351 | 2M419 | (Light out) | DA 6-3-10 @ 1245am C. Ashton pole #27351 light is on and working DA 5-28-10 @ 312am C .Ashton pole #27351 N/C underground | High Pressure Sodium | 38.90399643000 | -77.03208460000
5/28/10 | 920189 | 1111 | 14TH ST | NW | 5/28/10 | 27350 | 2M423 | (Light out) | 5-28-10 I.Paraway---repaired (sc) | High Pressure Sodium | 38.90469050000 | -77.03208800000
5/28/10 | 920169 | 0 | SHERIDAN RD | SE | 5/28/10 | 81354DC | 8U653 | (Light out) | DA 5-27-10 @ 1105pm K. Simmons repaired pole #81354dc | High Pressure Sodium | 38.85661920000 | -76.99335308000
5/27/10 | 919537 | 0 | WISCONSIN AVE | NW | 6/1/10 | 37009 | 3G114 | (Light out) | DA 6-01-10 @ 200am K. Dunton repaired pole #37009 | High Pressure Sodium | 38.91709887000 | -77.06871738000
5/26/10 | 919414 | 300 | EASTERN AVE | NE | 5/27/10 | 70026 | 72855 | (Light out) | DA 5-27-10 @ 206am T, Richards pole #70026 defective fixture - refer to wo #805342 | High Pressure Sodium | 38.89394625000 | -76.91101330000
5/26/10 | 918863 | 4540 | 28TH ST | NW | 6/1/10 | 3F401DC | 3A365DC | (Light out) | DA 5-31-10 @ 1145pm K. Dunton relocated photocell pole #3F401DC | High Pressure Sodium | 38.94894480000 | -77.05559405000
5/26/10 | 918606 | 0 | U ST | NW | 6/15/10 | 12575 | 1G545 | (Light out) | DA 5-31-10 @ 1125pm R. Warren light found on and working DA 5-26-10 @ 407am R. Warren - pole tag missing - N/C underground | High Pressure Sodium | 38.91709569000 | -77.02678401000
5/25/10 | 917917 | 1501 | 17TH ST | NW | 5/31/10 | 26708 | 2M015 | (Light out) | DA 5-31-10 @ 1022pm C .Ashton repaired pole #26708 5-26-10 A.Purnell---install base door (sc) | High Pressure Sodium | 38.90973882000 | -77.03840656000
5/25/10 | 917832 | 200 | I ST | SE | 5/28/10 | 67650 | 6A426 | (Light out) | DA 5-28-10 @ 319am T. Richards pole #67650 light is on and working DA 5-25-10 @ 1110pm K. Simmons pole #67650 N/C underground | High Pressure Sodium | 38.87923749000 | -77.00159557000
5/24/10 | 917183 | 1225 | 18TH ST | NW | 5/26/10 | 26763 | 2U514 | (Light out) | DA 5-26-10 @ 125am C.Ashton repaired pole #26763 | High Pressure Sodium | 38.90700407000 | -77.04161752000
5/24/10 | 917181 | 1307 | NEW HAMPSHIRE AVE | NW | 5/28/10 | 24481 | 2G770 | (Light out) | DA 5-28-10 @ 345am C. Ashton repaired pole #24481 | High Pressure Sodium | 38.90814384000 | -77.04473348000
5/24/10 | 917156 | 0 | 23RD ST | NW | 5/25/10 | 28345 | 2M285 | (Light out) | DA 5-25-10 @ 349am . Ashton repaired pole #28345 | High Pressure Sodium | 38.90189255000 | -77.05000095000
5/24/10 | 917153 | 200 | 23RD ST | NW | 5/28/10 | 28319 | 2M276 | (Light out) | DA 5-28-10 @ 331am C .Ashton repaired pole #28319 | High Pressure Sodium | 38.89259094000 | -77.05025420000
5/24/10 | 916769 | 0400 | TAYLOR ST | NE | 5/24/10 | 50084 | 5A065 | (Light out) | DA 5-24-10 @ 325am K. Simmons repaired pole #50084 | High Pressure Sodium | 38.94081181000 | -77.00160841000
5/24/10 | 916728 | 0 | FLORIDA AVE | NE | 5/24/10 | 54443 | 5M132 | (Light out) | DA 5-23-10 @ 1140pm K. Simmons repaired pole #54443 | High Pressure Sodium | 38.90877588000 | -77.00407804000
5/23/10 | 916719 | 2914 | SHERMAN AVE | NW | 5/23/10 | 12529 | 12534 | (Light out) | DA 5-23-10 @ 1008pm C .Ashton repaired pole #12529 | High Pressure Sodium | 38.92730578000 | -77.02611400000
5/23/10 | 916718 | 2914 | SHERMAN AVE | NW |  | 12529 | 12534 | (Light out) |  | High Pressure Sodium | 38.92730578000 | -77.02611400000
5/23/10 | 916703 | 2613 | WISCONSIN AVE | NW | 5/24/10 | 30172 | 3G040 | (Light out) | DA 5-23-10 @ 1040pm K. Dunton repaired pole #30172 | High Pressure Sodium | 38.92393584000 | -77.07307563000
5/23/10 | 916702 | 2844 | WISCONSIN AVE | NW | 5/24/10 | 30179 | 3G010 | (Light off/on) | DA 5-23-10 @ 1050p K. Dunton repaired pole #30179 | High Pressure Sodium | 38.92718446000 | -77.07306789000
5/23/10 | 916680 | 900 | 3RD ST | SE | 5/27/10 | 67530 | 6A454 | (Light out) | DA 5-27-10 @ 249am T Richards pole #67530 light is on and working DA 5-24-10 @ 315am T. Richards pole #67530 N/C underground | High Pressure Sodium | 38.87919095000 | -77.00197695000
5/21/10 | 915343 | 0 | INTERSTATE 395 | SW | 6/4/10 | 21769 | 6A388 | (Light out) | DA 6-4-10 @ 1235am C .Ashton pole #21769 light is on and working DA 5-21-10 @ 405am T. Richards pole #21769 N/C Underground | High Pressure Sodium | 38.88595087000 | -77.01319845000
5/21/10 | 915325 | 423 | NEW YORK AVE | NW | 5/21/10 | 25923 | 6M764 | (Light out) | DA 5-21-10 @ 327am c.AShton repaired pole #25923 | High Pressure Sodium | 38.90450411000 | -77.01761089000
5/20/10 | 914913 | 4303 | OVERLOOK AVE | SW | 5/31/10 | 82103 | 82093 | (Light out) | DA 5-24-10 K. Simmons request for map T Richards request for map | High Pressure Sodium | 38.83860812000 | -77.00983908000
5/17/10 | 912366 | 900 | SHEPHERD ST | NW | 5/19/10 | 4J079 | 4G274 | (Light out) | DA 5-19-10 @ 158am R .Warren repaired pole #4j079 | High Pressure Sodium | 38.93984572000 | -77.02508226000
5/17/10 | 912329 | 2473 | 18TH ST | NW | 5/21/10 | 11406 | 1G478 | (Light out) | DA 5-21-10 @ 354am C .Ashton repaired pole #11406 | High Pressure Sodium | 38.92224805000 | -77.04243267000
5/17/10 | 911777 | 300 | EASTERN AVE | NE | 5/20/10 | 70026 | 72855 | (Light out) | DA 5-20-10 @ 142am T. Richards pole #70026 there are 2 lights in area with this pole # both are on and working - drew map | High Pressure Sodium | 38.89394625000 | -76.91101330000
5/16/10 | 911671 | 0500 | 8TH ST | NW | 5/16/10 | 29609 | 2M397 | (Light off/on) | DA 5-16-10 @ 1106pm C .Ashton repaired pole #29609 | High Pressure Sodium | 38.89684808000 | -77.02304941000
5/16/10 | 911666 | 900 | 2ND ST | SW | 5/19/10 | 68129 | 6A416 | (Light out) | DA 5-19-10 @ 144am T. Richards pole #68129 duplicate ticket to wo #907858 Block 10-00168503-Also lights are out on K St. SE between 3rd and 2nd St Se. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.87878241000 | -77.00287862000
5/16/10 | 911666 | 900 | 2ND ST | SW | 5/19/10 | 68129 | 68621 | (Light out) | DA 5-19-10 @ 144am T. Richards pole #68129 duplicate ticket to wo #907858 Block 10-00168503-Also lights are out on K St. SE between 3rd and 2nd St Se. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90623996000 | -77.01082515000
5/16/10 | 911658 | 1000 | NEW YORK AVE | NW | 5/19/10 | 22948 | 2L032 | (Light out) | DA 5-18-10 @ 1107pm C .Ashton repaired pole #22948 using 400hps kit refer to wo #911650 | High Pressure Sodium | 38.90132896000 | -77.02684244000
5/16/10 | 911650 | 1000 | NEW YORK AVE | NW | 5/19/10 | 22948 | 2L032 | (Light out) | DA 5-18-10 @ 1107pm C .AShton repaired pole #22948 DA 5-17-10 @ 106am C .Ashton installed 400 kit pole #22948 - caught on fire will return tomorrow | High Pressure Sodium | 38.90132896000 | -77.02684244000
5/13/10 | 909548 | 0 | INTERSTATE 395 | SW |  | 21769 | 6A388 | (Light out) |  | High Pressure Sodium | 38.88595087000 | -77.01319845000
5/13/10 | 909536 | 0 | NEW YORK AVE | NW | 5/14/10 | 22914 | 2L029 | (Light out) | DA 5-14-10 @ 1222am C .Ashton rpeaired pole #22914 | High Pressure Sodium | 38.90105629000 | -77.02684066000
5/12/10 | 909121 | 1100 | H ST | NE | 2/8/12 | 62334 | 6S168 | (Light out) | DA 5-12-10 @ 1050pm K. Simmons new poles are being installed @ this location | High Pressure Sodium | 38.90029678000 | -76.99039416000
5/12/10 | 909042 | 1827 | WILTBERGER ST | NW | 5/14/10 | 29507 | 1M014 | (Light out) | DA 5-14-10 @ 337am C .ashton repaired pole #29507 | High Pressure Sodium | 38.91496601000 | -77.02091840000
5/12/10 | 909028 | 0000 | S ST | NW | 5/20/10 | 14384 | 1G603 | (Light out) | DA 5-20-10 @ 1225am K. Dunton pole #14384 light found on and working DA 5-14-10 @ 402am R. Warren pole #14384 N/C underground | High Pressure Sodium | 38.91499293000 | -77.02126455000
5/12/10 | 909026 | 946 | T ST | NW | 5/13/10 | 13448 | 1L365 | (Light out) | DA 5-13-10 @ 104am C .Ashton repaired pole #13448 | High Pressure Sodium | 38.91552297000 | -77.02567379000
5/12/10 | 908973 | 815 | V ST | NW | 5/13/10 | 14236 | 1U040 | (Light out) | DA 5-13-10 @ 114am C .Ashton repaired pole #14236 | Incandescent | 38.91816509000 | -77.02346836000
5/12/10 | 908711 | 1800 | S ST | NW | 5/13/10 | 26212 | 2M114 | (Light out) | DA 5-13-10 @ 354am C .Ashton repaired pole #26212 | High Pressure Sodium | 38.91415158000 | -77.04178551000
5/11/10 | 908295 | 1000 | HALF ST | SE | 5/13/10 | 67437 | 6B103 | (Light out) | DA 5-13-10 @ 150am K. Simmons repaired pole #67437 Alley 10-00162966-The streetlight is in the alley behind 240 9th Street, SE cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.87769232000 | -77.00752782000
5/11/10 | 907858 | 900 | 2ND ST | SW | 5/19/10 | 68129 | 6A416 | (Light out) | DA 5-13-10 @ 345am K. Simmons pole #68129 N/C Underground | High Pressure Sodium | 38.87878241000 | -77.00287862000
5/11/10 | 907858 | 900 | 2ND ST | SW | 5/19/10 | 68129 | 68621 | (Light out) | DA 5-13-10 @ 345am K. Simmons pole #68129 N/C Underground | High Pressure Sodium | 38.90623996000 | -77.01082515000
5/11/10 | 907855 | 0 | I ST | SE | 6/12/12 | 67647 | 6A423 | (Light out) | 06-12-12 Darrell Dixon and Damien Smith Deenergized. (WP) DA 5-12-10 @ 200am K. Simmons pole #67647 N/C underground | High Pressure Sodium | 38.87920166000 | -77.00270681000
5/11/10 | 907854 | 0 | I ST | SE | 5/19/10 | 67649 | 6B448 | (Light out) | DA 5-12-10 @ 200am K. Simmons pole #67649 N/C underground | High Pressure Sodium | 38.87935007000 | -77.00191429000
5/11/10 | 907853 | 900 | 3RD ST | SE | 5/19/10 | 67529 | 6A457 | (Light out) | DA 5-12-10 @ 200am K. Simmons pole #67529 N/C underground | High Pressure Sodium | 38.87896332000 | -77.00211088000
5/11/10 | 907852 | 900 | 3RD ST | SW | 5/19/10 | 68144 | 6A461 | (Light out) | DA 5-12-10 @ 250am K. Simmons pole #68144 N/C underground | High Pressure Sodium | 38.87851901000 | -77.00211175000
5/11/10 | 907821 | 1500 | PENNSYLVANIA AVE | SE | 5/12/10 | 65364 | 6U668 | (Light out) | DA 5-12-10 @ 350am K. Simmons repaired pole #65364 | High Pressure Sodium | 38.87910251000 | -76.98200727000
5/10/10 | 907689 | 0 | SHERMAN AVE | NW | 5/10/10 | 12587 | 1G451 | (Light off/on) | DA 5-10-10 @ 1033pm C. Ashton repaired pole #12587 | High Pressure Sodium | 38.92300485000 | -77.02549655000
5/9/10 | 906749 | 0 | 13TH PL | NW | 5/12/10 | 4J740 | 4U153 | (Light out) | DA 5-12-10 @ 306am C. Ashton repaired pole #4j740 | High Pressure Sodium | 38.94182450000 | -77.02958631000
5/9/10 | 906718 | 1601 | 18TH ST | NW | 2/9/12 | 26773 | 2M145 | (Light out) | DA 5-10-10 @ 1046pm C. Ashton pole #26773 N/C Underground | High Pressure Sodium | 38.91132223000 | -77.04173550000
5/9/10 | 906717 | 1218 | CONNECTICUT AVE | NW | 2/9/12 | 24532 | 2U519 | (Light out) | DA 5-10-10 @ 149am C .Ashton pole #24532 N/C underground | High Pressure Sodium | 38.90651643000 | -77.04185036000
5/7/10 | 905253 | 0 | NEW YORK AVE | NE | 5/7/10 | 56856 | 5M133 | (Light out) | DA 5-7-10 @ 255am K. Simmons repaired pole #56856 | High Pressure Sodium | 38.90889349000 | -77.00418950000
5/6/10 | 904395 | 0 | H ST | NE | 5/7/10 | 61632 | 6S219 | (Light off/on) | DA 5-6-10 @ 1140pm K. Dunton repaired pole #61632 | High Pressure Sodium | 38.90029661000 | -76.99965221000
5/6/10 | 904289 | 0 | MONROE ST | NE | 5/6/10 | 56155DC | 5U724 | (Light out) | DA 5-6-10 @ 355am K. Simmons repaired pole #56155dc | High Pressure Sodium | 38.93229394000 | -76.99724081000
5/5/10 | 903437 | 0 | 8TH ST | NW | 5/5/10 | 22981 | 2M388 | (Light out) | DA 5-5-10 @ 1040pm K. Simmons repaired pole #22981 - adjusted TL photocell | High Pressure Sodium | 38.90076702000 | -77.02288069000
5/5/10 | 903431 | 504 | K ST | NW | 5/7/10 | 60470 | 6A104 | (Light out) | DA 5-7-10 @ 240am K. Dunton pole #60470 light found on and working | High Pressure Sodium | 38.90245334000 | -77.01925493000
5/5/10 | 903234 | 2121 | WISCONSIN AVE | NW | 5/5/10 | 30158 | 3G102 | (Light out) | DA 5-5-10 @ 115am C.ashton repaired pole #30158 | High Pressure Sodium | 38.91818441000 | -77.06963611000
5/4/10 | 902300 | 0 | SHERIDAN RD | SE | 5/4/10 | 81358DC | 8U646 | (Light out) | DA 5-4-10 @ 405am K. Simons repaired pole #81358dc | High Pressure Sodium | 38.85784096000 | -76.99320039000
5/3/10 | 901615 | 1000 | HALF ST | SE |  | 67437 | 6B103 | (Light out) | DA 5-4-10 @ 122am T. Richards 3rd party contractor - Skanska Construction - light behind fence | High Pressure Sodium | 38.87769232000 | -77.00752782000
5/3/10 | 901482 | 1600 | 18TH ST | NW | 6/15/10 | 26776 | 2M135 | (Light out) | S. Manning completed on 6-15-10 Installed pole tag number 26776 DA 5-3-10 @ 1155pm K. Simmons repaired pole tag missing | High Pressure Sodium | 38.91253906000 | -77.04173486000
4/30/10 | 899976 | 1601 | 18TH ST | NW | 2/9/12 | 26773 | 2M145 | (Light out) | DA 4-30-10 @ 347am c. Ashton pole #26773 N/C Underground | High Pressure Sodium | 38.91132223000 | -77.04173550000
4/30/10 | 899957 | 0 | SEDGWICK ST | NW | 4/30/10 | 30008DC | 3A368DC | (Light off/on) | DA 4-30-10 @ 1205am K, Dunton repaired pole #30008dc | Incandescent | 38.94040143000 | -77.09254074000
4/29/10 | 899931 | 3200 | KENYON PL | NW | 2/8/12 | 14683 | 1G052 | (Light out) | DA 4-29-10 @ 1039pm C. Ashton pole #14683 N/C underground | High Pressure Sodium | 38.93003166000 | -77.03236323000
4/29/10 | 899090 | 1600 | OATES ST | NE | 2/8/12 | 52808 | 5B259 | (Light out) | DA 4-29-10 @ 1150pm K. Simmons pole #52808 in the process of being replaced | High Pressure Sodium | 38.90288129000 | -76.98206430000
4/29/10 | 899058 | 601 | KENNEDY ST | NW | 4/30/10 | 4M067 | 4M067DC | (Light out) | DA 4-30-10 @ 1216am R. Warren repaired pole #4m067 | High Pressure Sodium | 38.95648496000 | -77.02110063000
4/29/10 | 899054 | 0 | 13TH PL | NW | 4/30/10 | 4J740 | 4U153 | (Light out) | DA 4-30-10 @ 255am R. Warren repaired pole #4j740 | High Pressure Sodium | 38.94182450000 | -77.02958631000
4/28/10 | 898105 | 1428 | TOBIAS DR | SE | 4/29/10 | 81783 | 88060 | (Light out) | DA 4-29-10 @ 310am K. simmons repaired pole #81783 | High Pressure Sodium | 38.85014068000 | -76.98274637000
4/28/10 | 898000 | 1411 | 37TH ST | NW | 4/29/10 | 21142 | 2G206 | (Light out) | DA 4-28-10 @ 1110pm C. Ashton repaired pole #21142 | High Pressure Sodium | 38.90801099000 | -77.07168004000
4/28/10 | 897958 | 3859 | PENNSYLVANIA AVE | SE | 4/29/10 | 77881DC | 7E010 | (Light out) | DA 4-29-10 @ 1215am K. Dunton pole #77881dc light found on and working | High Pressure Sodium | 38.86525460000 | -76.95024453000
4/28/10 | 897800 | 1112 | Q ST | NW | 4/28/10 | 29306DC | 2U047DC | (Light off/on) | DA 4-28-10 @ 212am C. Ashton repaired pole #29306dc | Incandescent | 38.91083084000 | -77.02756095000
| 897733 | 1005 | 1ST ST | NE | 4/28/10 | 61231 | 6S439 | (Light out) | West Side 10-00145506- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90311217000 | -77.00596908000
4/26/10 | 896344 | 0 | 8TH ST | NW | 4/27/10 | 4M075 | 4M075DC | (Light out) | DA 4-27-10 @ 234am R. Warren repaired pole #4m075 | High Pressure Sodium | 38.95640844000 | -77.02396296000
4/26/10 | 896301 | 200 | RIGGS RD | NW | 4/27/10 | 4A002 | 4J683 | (Light out) | DA 4-26-10 @ 1102pm R. Warren repaired pole #4A002 - Address is correct 200 riggs rd. / 1st pl. | High Pressure Sodium | 38.93966490000 | -77.03282752000
4/26/10 | 896252 | 801 | D ST | NW |  | 60176 | 2M330 | (Light out) | DA 4-26-10 @ 1040pm K. Dunton pole #60176 New teardrop fixture refer to ddot | High Pressure Sodium | 38.89474698000 | -77.02312090000
4/26/10 | 896251 | 504 | K ST | NW | 4/28/10 | 60470 | 6A104 | (Light out) | DA 4-2-10 @ 1202am T. Richards repaired pole #60470 | High Pressure Sodium | 38.90245334000 | -77.01925493000
4/26/10 | 895940 | 1420 | 9TH ST | NW | 4/26/10 | 25470 | 6U457 | (Light off/on) | DA 4-26-10 @ 318am C .Ashton repaired pole #25470 | High Pressure Sodium | 38.90930620000 | -77.02386532000
4/23/10 | 894827 | 0 | LEE ST | NE | 4/23/10 | 70327 | 7M082 | (Light out) | DA 4-23-10 @ 115am T. Richards repaired pole #70327 | High Pressure Sodium | 38.90317749000 | -76.94336293000
4/21/10 | 893650 | 0 | MASSACHUSETTS AVE | NW | 6/7/10 | 24285 | 2A056 | (Light out) | DA 4-23-10 1243am C. Ashton pole #24285 N/C underground FRONT 10-00137479-LIGHTS ON THE NORTH SIDE OF THE STREET ARE ALL OUT TOTALING ABOUT 4 OR 5 STREET LIGHT cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91137439000 | -77.04863511000
4/21/10 | 893623 | 504 | K ST | NW | 4/22/10 | 60470 | 6A104 | (Light out) | DA 4-22-10 @ 414am T. Richards repaired pole #60470 | High Pressure Sodium | 38.90245334000 | -77.01925493000
4/20/10 | 892823 | 0000 | 22ND ST | SE | 4/16/12 | 68332 | 6M820 | (Light out) | DA 4-27-10 @ 1014pm T. Richards pole #68332 light found on and working DA 4-21-10 @ 1220am K. Dunton pole #68332 N/C underground | High Pressure Sodium | 38.88856033000 | -76.97379932000
4/20/10 | 892632 | 0 | U ST | NW | 4/20/10 | 11722 | 1G527 | (Light off/on) | DA 4-20-10 @ 419am C. Ashton repaired pole #11722 | High Pressure Sodium | 38.91709757000 | -77.02977696000
4/19/10 | 892359 | 1301 | 20TH ST | NW | 3/10/11 | 24830 | 2A017 | (Light out) | DA 4-20-10 @ 200am C. Ashton pole #24830 N/C underground East Side 10-00134637- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90756285000 | -77.04480461000
4/19/10 | 892358 | 4540 | 28TH ST | NW | 4/20/10 | 3F401DC | 3A365DC | (Light out) | DA 4-20-10 @ 1220am K. Dunton repaired pole #3f401dc Alley 10-00134635-ALLEYLIGHT BURNT OUT. cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.94894480000 | -77.05559405000
4/15/10 | 891050 | 1230 | SUMNER RD | SE | 4/20/10 | 81565DC | 8A351 | (Light out) | vw 4-20-10 I Paraway/Barclay replaced 1-150 hps lamp & TLP | High Pressure Sodium | 38.86063641000 | -76.99700502000
4/15/10 | 890562 | 0 | MONROE ST | NE | 4/20/10 | 56156DC | 5U726 | (Light out) | DA 4-20-10 @ 1206am T. Richards pole #56156dc N/C to overhead - refer to wo #884508 | High Pressure Sodium | 38.93229333000 | -76.99681527000
4/14/10 | 890329 | 3903 | PENNSYLVANIA AVE | SE | 4/16/10 | 78521DC | 7E144DC | (Light out) | DA 4-16-10 @ 410am T. Richards repaired pole #78521dc | High Pressure Sodium | 38.86474391000 | -76.94943658000
4/14/10 | 890318 | 2929 | PENNSYLVANIA AVE | SE | 4/15/10 | 78564DC | 7E091DC | (Light out) | DA 4-15-10 @ 317am T, Richards repaired pole #78564dc | High Pressure Sodium | 38.87102343000 | -76.96484298000
4/13/10 | 888865 | 0 | 13TH ST | NW | 4/15/10 | 12572 | 1G529 | (Light out) | DA 4-15-10 @ 135am K. Simmons repaired pole #12572 | High Pressure Sodium | 38.91713413000 | -77.02951570000
4/12/10 | 888690 | 0 | U ST | NW | 3/10/11 | 12575 | 1G545 | (Light out) | DA 4-13-10 @ 115am K. Simmons pole #12575 N/C Underground | High Pressure Sodium | 38.91709569000 | -77.02678401000
4/12/10 | 888678 | 2450 | 37TH ST | NW | 4/22/10 | 36869 | 3G057 | (Light out) | DA 4-14-10 @ 1255am K. Dunton pole #36869 N/C Underground | High Pressure Sodium | 38.92247432000 | -77.07310675000
4/12/10 | 888660 | 2219 | WISCONSIN AVE | NW | 4/13/10 | 30173 | 3G036 | (Light out) | DA 4-13-10 @ 405am K. Dunton repaired pole #30173 | High Pressure Sodium | 38.92436846000 | -77.07307407000
4/12/10 | 888589 | 709 | H ST | NW | 4/14/10 | 22630 | 2M424 | (Light out) | DA 4-14-10 @ 1047pm T. Richards redirected photocell pole #22630 | High Pressure Sodium | 38.89990397000 | -77.02240296000
4/12/10 | 888569 | 1101 | 11TH ST | NW | 4/16/10 | 25275 | 2M265 | (Light out) | DA 4-16-10 @ 105am K. Dunton pole #25275 pole has been removed | High Pressure Sodium | 38.90450748000 | -77.02715607000
4/12/10 | 888568 | 1126 | 11TH ST | NW | 4/16/10 | 25276 | 2M262 | (Light out) | DA 4-16-10 @ 105am K. Dunton pole #25276 pole has been removed | High Pressure Sodium | 38.90502429000 | -77.02715562000
4/12/10 | 888567 | 1206 | 11TH ST | NW | 2/8/12 | 25278 | 2M257 | (Light out) | DA 4-13-10 @ 215am K. Simmons pole #25278 N/C underground - these lights may be getting ready to get changed | High Pressure Sodium | 38.90611370000 | -77.02715419000
4/12/10 | 888566 | 1217 | 11TH ST | NW | 2/8/12 | 25261 | 2M231 | (Light out) | DA 4-13-10 @ 215am K. Simmons pole #25261 N/C Underground - lights may be getting ready to be changed | High Pressure Sodium | 38.90622963000 | -77.02692296000
4/12/10 | 888565 | 1231 | 11TH ST | NW | 2/8/12 | 25260 | 2M233 | (Light out) | DA 4-13-10 @ 215am K. Simmons pole #25260 N?C Underground - these lights may be getting ready to be changed | High Pressure Sodium | 38.90681635000 | -77.02692053000
4/12/10 | 888236 | 1600 | 18TH ST | NW | 4/12/10 | 26776 | 2M135 | (Light out) | DA 4-12-10 @ 145am C. Ashton repaired pole #26776 | High Pressure Sodium | 38.91253906000 | -77.04173486000
4/11/10 | 888176 | 0 | NEW YORK AVE | NW | 4/13/10 | 22914 | 2L029 | (Light out) | DA 4-13-10 @ 347am T. Richards pole #22914 light found on and working | High Pressure Sodium | 38.90105629000 | -77.02684066000
4/11/10 | 888175 | 1000 | NEW YORK AVE | NW | 4/13/10 | 22948 | 2L032 | (Light out) | DA 4-13-10 @ 400a, T> Richards pole #22948 light found on and working | High Pressure Sodium | 38.90132896000 | -77.02684244000
4/9/10 | 887635 | 0 | 1ST ST | NE | 6/7/10 | 61238 | 6A261 | (Light out) | DA 6-7-10 @ 303am T. Richards pole #61238 light is on and working DA 4-12-10 @ 1210am T Richards pole #61238 N?C Underground (open ticket wo #874728) Front 10-00124881-metal pool streetlight is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90488153000 | -77.00596863000
4/9/10 | 886947 | 0000 | H ST | NE | 4/9/10 | 68246DC | 68246 | (Light off/on) | DA 4-9-10 @ 1254am T> Richards repaired pole #68246dc | High Pressure Sodium | 38.90004454000 | -77.00552357000
4/9/10 | 886946 | 0000 | H ST | NE | 4/9/10 | 68244DC | 68244 | (Light off/on) | DA 4-9-10 @ 1254am T. Richards repaired pole #68244dc | High Pressure Sodium | 38.90006002000 | -77.00655445000
4/9/10 | 886945 | 0 | H ST | NE | 4/9/10 | 68257DC | 68257 | (Light off/on) | DA 4-9-10 @ 1254am T. Richards repaired pole #68257dc | High Pressure Sodium | 38.90032958000 | -77.00695053000
4/9/10 | 886941 | 0 | RIGGS RD | NE | 4/9/10 | 4P557DC | 4U181 | (Light out) | DA 4-9-10 @ 225am K. Simmons repaired pole #4p557dc | High Pressure Sodium | 38.95788979000 | -77.00189601000
4/8/10 | 886917 | 1720 | 18TH ST | NW | 4/12/10 | 26897 | 2M125 | (Light out) | DA 4-12-10 @ 200am C, ashton repaired pole #26897 SW Corner 10-00123269-light bulb needs to be replaced cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91329133000 | -77.04170854000
4/8/10 | 886910 | 0 | INTERSTATE 295 | SE |  | 68019 | 6L894 | (Light out) | BCM - 4-9-10 - Feed form outbound side has been cut feeding Inbound side of bridge from Main Disconnect by 3rd party contactor(MC Dean). DA 4-8-10 @ 1121pm T. Richards - (9 lights out) N/C underground - | High Pressure Sodium | 38.87329255000 | -76.99048281000
4/8/10 | 886909 | 4303 | OVERLOOK AVE | SW | 4/13/10 | 82103 | 82093 | (Light out) | DA 4-12-10 @ 110am K. Simmons request for map DA 4-8-10 @ 1006pm T. Richards could not locate request for map | High Pressure Sodium | 38.83860812000 | -77.00983908000
4/8/10 | 886904 | 0 | 12TH ST EXPY | SW | 4/16/12 | 28757 | 68651 | (Light out) | DA 4-9-10 @ 320am T. Richards pole #28757 N/C underground | High Pressure Sodium | 38.88694943000 | -77.02777713000
4/8/10 | 886620 | 0 | H ST | NE | 4/11/10 | 62357 | 6M719 | (Light out) | DA 4-11-10 @ 1055pm T. Richards repaired pole #62357 | High Pressure Sodium | 38.90010373000 | -76.98416791000
4/8/10 | 886305 | 0 | PIERCE ST | NE | 4/9/10 | 61236 | 6A258 | (Light out) | DA 4-9-10 @ 1246am C. Ashton repaired pole #61236 | High Pressure Sodium | 38.90445580000 | -77.00596738000
4/8/10 | 886230 | 1425 | H ST | NE | 2/8/12 | 62325 | 6M714 | (Light out) | DA 4-11-10 @ 1046pm T. Richards pole #62325 N/C underground - pole marked | High Pressure Sodium | 38.90029705000 | -76.98474424000
4/8/10 | 886225 | 0 | H ST | NE | 4/26/10 | 62345 | 6S103 | (Light out) | DA 4-9-10 @ 1229am R. Warren installed TL Socket and TLPC - Needs new t abse - pole #62345 TRAFFIC COMBO. POLE | High Pressure Sodium | 38.90012051000 | -76.99138683000
4/8/10 | 886178 | 1393 | 44TH PL | SE | 4/9/10 | 76880 | 76880DC | (Light out) | DA 4-9-10 @ 430am K. Dunton repaired pole #76880 | High Pressure Sodium | 38.87348554000 | -76.93599877000
4/6/10 | 884725 | 3623 | O ST | NW | 4/8/10 | 21090 | 2G153 | (Light out) | DA 4-8-10 @ 1240am C. Ashton pole #21090 light found on and working | High Pressure Sodium | 38.90774375000 | -77.07124202000
4/6/10 | 884508 | 0 | MONROE ST | NE | 4/21/10 | 56156DC | 5U726 | (Light out) | DA 4-6-10 @ 130am K. Simmons pole #56156dc N/C to Overhead | High Pressure Sodium | 38.93229333000 | -76.99681527000
4/5/10 | 884015 | 4608 | NANNIE HELEN BURROUGHS AVE | NE | 4/7/10 | 71300DC | 7A234 | (Light out) | DA 4-7-10 @ 350am T. Richards repaired harness connection pole #71300dc | High Pressure Sodium | 38.89940450000 | -76.93569847000
4/5/10 | 884014 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 4/7/10 | 71270 | 71270DC | (Light out) | DA 4-7-10 Been referred to pepco wo #735419 | High Pressure Sodium | 38.89827347000 | -76.92679095000
4/5/10 | 884013 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 4/7/10 | 71269 | 7A201 | (Light out) | DA 4-7-10 Been referred to pepco wo #735419 | High Pressure Sodium | 38.89826963000 | -76.92624974000
4/5/10 | 884012 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 4/7/10 | 72645 | 7S073 | (Light out) | DA 4-7-10 Been referred to pepco wo #735419 | High Pressure Sodium | 38.89826452000 | -76.92554310000
4/5/10 | 884011 | 5214 | NANNIE HELEN BURROUGHS AVE | NE | 4/7/10 | 72646 | 7A198 | (Light out) | DA 4-7-10 Been referred to pepco wo #735419 | High Pressure Sodium | 38.89827561000 | -76.92455911000
4/5/10 | 884010 | 5403 | NANNIE HELEN BURROUGHS AVE | NE | 4/7/10 | 72648 | 7A191 | (Light out) | DA 4-7-10 Been referred to pepco wo #735419 | High Pressure Sodium | 38.89829839000 | -76.92250388000
4/5/10 | 884009 | 5516 | NANNIE HELEN BURROUGHS AVE | NE | 4/7/10 | 72651 | 7A184 | (Light out) | DA 4-7-10 Been referred to pepco wo #735419 | High Pressure Sodium | 38.89830423000 | -76.92065348000
4/5/10 | 883974 | 38 | NEW YORK AVE | NE | 4/9/10 | 61254 | 6A287 | (Light out) | DA 4-9-10 @ 124am R. Warren repaired pole #61254 | High Pressure Sodium | 38.90772223000 | -77.00767643000
4/5/10 | 883847 | 900 | 3RD ST | SE | 4/6/10 | 67530 | 6A454 | (Light out) | DA 4-6-10@ 334am R ,Warren repaired pole #67530 | High Pressure Sodium | 38.87919095000 | -77.00197695000
4/4/10 | 883558 | 0 | NEW HAMPSHIRE AVE | NW | 4/5/10 | 23871 | 2G754 | (Light out) | DA 4-4-10 @ 1121pm C. AShton repaired pole #23871 | High Pressure Sodium | 38.90624217000 | -77.04652003000
4/4/10 | 883540 | 3859 | PENNSYLVANIA AVE | SE | 4/7/10 | 77881DC | 7E010 | (Light out) | DA 4-6-10 @ 1130pm T. Richards repaired pole #77881dc DA 4-6-10 @ 311am T. Richards unsafe to repair due to activity | High Pressure Sodium | 38.86525460000 | -76.95024453000
4/4/10 | 883537 | 3127 | PARK DR | SE | 4/8/10 | 74760DC | 7A074DC | (Light out) | DA 4-6-10 1055PM T. RICHARDS pole #74760DC - per B.Black - Pepco installed new pole and overhead lines but did not install arm or fixture - refer to overhead crew | High Pressure Sodium | 38.85948088000 | -76.95794149000
4/1/10 | 881275 | 0 | 13TH PL | NW | 4/2/10 | 4J740 | 4U153 | (Light out) | DA 4-2-10 @ 256am R. Warren repaired pole #4j740 | High Pressure Sodium | 38.94182450000 | -77.02958631000
4/1/10 | 881240 | 1200 | 11TH ST | SE | 4/2/10 | 67740 | 6L938 | (Light out) | DA 4-1-10 @ 1154pm T. Richards repaired pole #67740 | High Pressure Sodium | 38.87633690000 | -76.99165150000
4/1/10 | 881218 | 4611 | NORTH CAPITOL ST | NE | 4/2/10 | 4R755 | 4A796 | (Light out) | DA 4-1-10 @ 1147pm R. Warren repaired pole #4r755 | High Pressure Sodium | 38.94780081000 | -77.00876904000
3/31/10 | 880498 | 5000 | NANNIE HELEN BURROUGHS AVE | NE | 4/2/10 | 71278DC | 7A212 | (Light out) | DA 4-2-10 @ 640am T. Richards repaired pole #71278dc | High Pressure Sodium | 38.89843573000 | -76.92937719000
3/30/10 | 879968 | 1509 | TUBMAN RD | SE | 3/31/10 | 81803 | 88080 | (Light out) | DA 3-31-10 @ 220am K. Simmons repaired pole #81803 | High Pressure Sodium | 38.84827859000 | -76.98210715000
3/30/10 | 879702 | 0000 | H ST | NE | 3/31/10 | 68244DC | 68244 | (Light out) | DA 3-31-10 @ 118am T. Richards pole #68244dc light found on and woking | High Pressure Sodium | 38.90006002000 | -77.00655445000
3/30/10 | 879677 | 900 | 3RD ST | SE | 3/31/10 | 67530 | 6A454 | (Light out) | DA 3-31-10 @ 348am T. Richards repaired pole #67530 - reset photocell | High Pressure Sodium | 38.87919095000 | -77.00197695000
3/30/10 | 879667 | 4202 | BENNING RD | NE | 4/1/10 | 73867DC | 73867 | (Light out) | DA 4-1-10 @ 1220am T. Richards recoonected overhead feed pole #73867dc | High Pressure Sodium | 38.89298310000 | -76.94251439000
3/29/10 | 879297 | 5700 | CHILLUM PL | NE | 3/29/10 | 4P516DC | 4U174 | (Light out) | DA 3-29-10 @ 1052pm R. Warren repaired pole #4p516dc using 400hps lamp refer to wo #877719 | High Pressure Sodium | 38.95893594000 | -77.00160441000
3/29/10 | 879296 | 0 | RIGGS RD | NE | 3/31/10 | 4P557DC | 4U181 | (Light out) | DA 3-29-10 @ 1101pm R. Warren pole #4p557dc needs 400 hps powerdoor | High Pressure Sodium | 38.95788979000 | -77.00189601000
3/29/10 | 879277 | 601 | KENNEDY ST | NW | 4/1/10 | 4M067 | 4M067DC | (Light out) | DA 4-1-10 @ 1236am R. Warren repaired pole #4m067 | High Pressure Sodium | 38.95648496000 | -77.02110063000
3/26/10 | 877719 | 5700 | CHILLUM PL | NE | 3/29/10 | 4P516DC | 4U174 | (Light out) | DA 3-29-10 @ 1052pm R. Warren repaired pole #4p516dc na 10-00105418-the ploe is the side of the house cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.95893594000 | -77.00160441000
3/25/10 | 876951 | 3127 | PARK DR | SE | 3/29/10 | 74760DC | 7A074DC | (Light out) | DA 3-29-10 @ 1241am T. Richards - Bad address / pole #74760dc not @ this location/ Google maps has pole located @ 3346 Camden St. - open work order for this pole refer to wo #846540 | High Pressure Sodium | 38.85948088000 | -76.95794149000
3/25/10 | 876635 | 0 | WILTBERGER ST | NW | 3/25/10 | 29509 | 1M010 | (Light out) | DA 3-25-10 @ 1001pm C. Ashton repaired pole #29509 Front 10-00103198- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91554664000 | -77.02082826000
3/24/10 | 876377 | 1557 | EASTERN AVE | NE | 3/25/10 | 71134 | 7S083 | (Light out) | DA 3-25-10 @ 231am T. Richards repaired pole #71134 | High Pressure Sodium | 38.91069029000 | -76.93223850000
3/24/10 | 876368 | 4612 | 12TH ST | NE | 3/25/10 | 51256DC | 5A150DC | (Light out) | DA 3-25-10 @ 250am K. Simmons repaired pole #51256dc | High Pressure Sodium | 38.94542966000 | -76.99072288000
3/24/10 | 876345 | 3100 | PENNSYLVANIA AVE | SE | 3/28/10 | 78562DC | 7E092DC | (Light out) | DA 3-28-10 @ 1110pm T. Richards repaired pole #78562dc | High Pressure Sodium | 38.87088102000 | -76.96446252000
3/24/10 | 876344 | 3000 | PENNSYLVANIA AVE | SE | 3/28/10 | 78561DC | 7E093DC | (Light out) | DA 3-28-10 @ 1118pm T. Richards repaired pole #78561dc | High Pressure Sodium | 38.87074474000 | -76.96412983000
3/24/10 | 876278 | 4608 | NANNIE HELEN BURROUGHS AVE | NE | 3/25/10 | 71300DC | 7A234 | (Light out) | DA 3-25-10 @ 1243am T. Richards repaired loose connection powerdoor pole #71300dc unknown 10-00102642-Light come on for a while and then goes out, need repairing and/or replacing cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89940450000 | -76.93569847000
3/24/10 | 875566 | 3424 | P ST | NW | 3/24/10 | 21006 | 2G131 | (Light out) | DA 3-24-10 @ 151am C. Ashton repaired pole #21006 | High Pressure Sodium | 38.90869051000 | -77.06861216000
3/22/10 | 874728 | 0 | 1ST ST | NE | 9/2/10 | 61238 | 6A261 | (Light out) | DA 3-24-10 @ 1110pm T. Richards pole #61238 N/C underground (open ticket 873344) Front 10-00099102-street light has physical damages /please replace cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90488153000 | -77.00596863000
3/22/10 | 874604 | 3623 | O ST | NW | 3/23/10 | 21090 | 2G153 | (Light out) | DA 3-23-10 @ 202am C. Ashton repaired pole #21090 | High Pressure Sodium | 38.90774375000 | -77.07124202000
3/22/10 | 874581 | 1100 | 11TH ST | SE | 3/24/10 | 66052 | 6L994 | (Light out) | DA 3-24-10 @ 108am T. Richards repaired pole #66052 | High Pressure Sodium | 38.87726467000 | -76.99133320000
3/22/10 | 874573 | 800 | I ST | SW | 3/24/10 | 66789 | 6S044 | (Light out) | DA 3-24-10 @ 311am T. Richards repaired pole #66789 - redirected photocell | High Pressure Sodium | 38.87920957000 | -77.01739223000
3/22/10 | 873967 | 900 | 3RD ST | SE | 3/24/10 | 67530 | 6A454 | (Light out) | DA 3-24-10 @ 218am T. Richards repaired pole #67530 | High Pressure Sodium | 38.87919095000 | -77.00197695000
3/22/10 | 873966 | 0 | 9TH ST | NW | 3/22/10 | 25436 | 2L559 | (Light out) | DA 3-22-10 @ 1125pm C. Ashton repaired pole #25436 | High Pressure Sodium | 38.90407457000 | -77.02409965000
3/22/10 | 873958 | 926 | MASSACHUSETTS AVE | NW | 3/22/10 | 25940 | 2L549 | (Light out) | DA 3-22-10 @ 957PM C. Ashton repaired pole #25940 | High Pressure Sodium | 38.90348081000 | -77.02543634000
3/22/10 | 873926 | 1133 | CONNECTICUT AVE | NW | 3/22/10 | 27219 | 2U550 | (Light off/on) | DA 3-22-10 @ 100am C. Ashton repaired pole #27219 | High Pressure Sodium | 38.90491369000 | -77.04052615000
3/21/10 | 873905 | 3407 | MINNESOTA AVE | SE | 3/25/10 | 76578DC | 7S023 | (No Current to Over Head) |  | High Pressure Sodium | 38.88422000000 | -76.95717076000
3/21/10 | 873904 | 3407 | MINNESOTA AVE | SE | 3/25/10 | 76578DC | 7S023 | (No Current to Over Head) |  | High Pressure Sodium | 38.88422000000 | -76.95717076000
3/21/10 | 873897 | 1147 | CONNECTICUT AVE | NW | 3/22/10 | 27220 | 2U544 | (Light out) | DA 3-22-10 @ 105am C. Ashton repaired pole #27220 | High Pressure Sodium | 38.90537241000 | -77.04079316000
3/21/10 | 873882 | 1333 | NEW HAMPSHIRE AVE | NW | 5/25/10 | 24473 | 2G775 | (Light out) | DA 5-24-10 @ 1139pm C .Ashton ran 90 ft wire pole #24473 DA 3-22-10 @ 205am C. Ashton pole #24473 N/C underground | High Pressure Sodium | 38.90894364000 | -77.04422669000
3/21/10 | 873870 | 1021 | 17TH ST | NE | 3/22/10 | 59346 | 59346 | (Light out) | DA 3-21-10 @ 1145pm K. Simmons repaired pole #59346 | High Pressure Sodium | 38.90312888000 | -76.97890387000
3/19/10 | 873344 | 0 | 1ST ST | NE | 6/5/10 | 61238 | 6A261 | (Light out) | DA 3-23-10 @ 1235am K. Simmons pole #61238 N/C underground Front 10-00096503-metal pole streetlight is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90488153000 | -77.00596863000
3/18/10 | 872518 | 0 | H ST | NE | 3/18/10 | 62345 | 6S103 | (Light out) | DA 3-18-10 @ 956pm C. AShton repaired pole #62345 | High Pressure Sodium | 38.90012051000 | -76.99138683000
3/18/10 | 872301 | 1358 | H ST | NE | 3/21/10 | 62328 | 6S145 | (Light out) | DA 3-21-10 @ 1000pm T .Richards repaired pole #62328 | High Pressure Sodium | 38.90029528000 | -76.98645500000
3/18/10 | 872293 | 1222 | 1ST ST | NE | 3/22/10 | 61245 | 6A276 | (Light out) | DA 3-22-10 @ 147am T. Richards pole #61245 light on prior to arrival - replaced 400 hps lamp | High Pressure Sodium | 38.90699632000 | -77.00596394000
3/18/10 | 872292 | 903 | 4TH ST | NW | 3/22/10 | 60452 | 6S492 | (Light out) | DA 3-22-10 @ 311am T .Richards pole #60452 light found on and working | High Pressure Sodium | 38.90212698000 | -77.01625073000
3/18/10 | 872194 | 1393 | 44TH PL | SE | 3/19/10 | 76880 | 76880DC | (Light out) | i paraway---replaced 400 hps lamp--3-19-2010 | High Pressure Sodium | 38.87348554000 | -76.93599877000
3/18/10 | 872189 | 0 | SHERIDAN RD | SE | 3/19/10 | 81364DC | 8M048 | (Light out) | DA 3-18-10 @ 1105pm K. Simmons repaired pole #81364dc | High Pressure Sodium | 38.85942886000 | -76.99337741000
3/18/10 | 872067 | 0 | 7TH ST | NW | 3/19/10 | 25700 | 6A808 | (Light out) | DA 3-19-10 @ 1244am C.AShton repaired pole #25700 | High Pressure Sodium | 38.90973823000 | -77.02182543000
3/18/10 | 872042 | 415 | 4TH ST | SW | 2/8/12 | 21568 | 6A343 | (Light out) | DA 3-18-10 @ 1026pm C. Ashton pole #21568 N/C underground | High Pressure Sodium | 38.88359675000 | -77.01766488000
3/18/10 | 871985 | 710 | 58TH ST | NE | 3/19/10 | 72629DC | 7A175 | (Light out) | 3-19-10 I.Paraway---repaired (sc) | High Pressure Sodium | 38.89849072000 | -76.91770107000
3/17/10 | 871314 | 4205 | 9TH ST | NW | 3/19/10 | 4K019 | 4G324 | (Light out) | DA 3-19-10 @ 1246am R. Warren repaired pole #4k019 | High Pressure Sodium | 38.94229289000 | -77.02515003000
3/17/10 | 871312 | 4129 | 9TH ST | NW | 3/24/10 | 4J791 | 4G329 | (Light out) | DA 3-19-10 @ 1255am R. Warren pole #4j791 N/C underground | High Pressure Sodium | 38.94153002000 | -77.02498893000
3/17/10 | 871310 | 4121 | 9TH ST | NW | 4/12/10 | 4J792 | 4G328 | (Light out) | DA 3-19-10 @ 100am R. Warren pole #4j792 N/C underground | High Pressure Sodium | 38.94134498000 | -77.02510288000
3/17/10 | 871308 | 0 | IOWA AVE | NW | 3/19/10 | 4K496 | 4U128 | (Light out) | DA 3-18-10 @ 1118pm R. Warren repaired pole #4k496 | High Pressure Sodium | 38.94605354000 | -77.02957834000
3/17/10 | 870768 | 0 | 1ST ST | NE | 6/5/10 | 61238 | 6A261 | (Light out) | DA 3-18-10 @ 338am T. Richards pole #61238 N/C Underground - refer to wo #865246 Front 10-00091280- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90488153000 | -77.00596863000
3/16/10 | 870528 | 946 | T ST | NW | 3/17/10 | 13448 | 1L365 | (Light out) | DA 3-17-10 @ 134am C. Ashton repaired pole #13448 | High Pressure Sodium | 38.91552297000 | -77.02567379000
3/16/10 | 870302 | 809 | EASTERN AVE | NE | 3/18/10 | 79475 | 7A139 | (Light out) | DA 3-18-10 @ 1250am T. Richards repaired pole #79475 - redirected photocell | High Pressure Sodium | 38.88244563000 | -76.96384495000
3/15/10 | 869647 | 0 | BRANDYWINE ST | NW | 8/15/11 | 3A230DC | 3A230 | (Light out) | DA 3-16-10 @ 250am K/ Dunton pole #3a230dc defective 250mv fixture refer to ddot Field inspection by FOD determined all other lights in the area to be 400 watt hps, bkenney approved keeping all lights consistent. 9/30/10. Removed 250w MV and installed 40 | High Pressure Sodium | 38.94974018000 | -77.08081828000
3/15/10 | 868955 | 1262 | NEW HAMPSHIRE AVE | NW | 3/16/10 | 23852 | 2G757 | (Light out) | DA 3-15-10 @ 1128pm C. Ashton repaired pole #23852 | High Pressure Sodium | 38.90669938000 | -77.04633627000
3/12/10 | 867837 | 0 | INTERSTATE 295 | SE | 3/25/10 | 86510 | 8L768 | (No current) |  | High Pressure Sodium | 38.86566546000 | -76.99168893000
3/11/10 | 867319 | 4608 | NANNIE HELEN BURROUGHS AVE | NE | 3/15/10 | 71300DC | 7A234 | (Light out) | DA 3-15-10 @ 228am R. Warren repaired pole #71200dc DA 3-12-10 Needs fixture | High Pressure Sodium | 38.89940450000 | -76.93569847000
3/10/10 | 866021 | 0500 | 8TH ST | NW | 3/10/10 | 29609 | 2M397 | (Light out) | DA 3-10-10 @ 105am C. Ashton repaired pole #29609 Right Fixture | High Pressure Sodium | 38.89684808000 | -77.02304941000
3/9/10 | 865462 | 2838 | BLADENSBURG RD | NE | 3/11/10 | 51238DC | 5A134DC | (Light out) | DA 3-11-10 @ 550amK. Simmons repaired pole #51238dc | High Pressure Sodium | 38.92682989000 | -76.96333203000
3/9/10 | 865246 | 0 | 1ST ST | NE | 4/16/12 | 61238 | 6A261 | (Light out) | DA 3-11-10 @ 505am T. Richards pole #61238 N/C underground Front 10-00080440- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90488153000 | -77.00596863000
3/8/10 | 865094 | 3100 | PENNSYLVANIA AVE | SE | 3/9/10 | 78560DC | 7E094DC | (Light out) | DA 3-9-10 @ 200am T. Richards repaired pole #78560dc | High Pressure Sodium | 38.87059877000 | -76.96377234000
3/8/10 | 865091 | 3127 | PARK DR | SE | 3/24/10 | 74760DC | 7A074DC | (Light out) |  | High Pressure Sodium | 38.85948088000 | -76.95794149000
3/8/10 | 864958 | 1352 | U ST | SE | 3/11/10 | 80946 | 8M020 | (Light out) | 3-11-10 M.Craig---repaired (sc) | High Pressure Sodium | 38.86598601000 | -76.98548666000
3/8/10 | 864225 | 1019 | U ST | NW | 3/8/10 | 13287 | 1G546 | (Light off/on) | DA 3-8-10 @ 349am C. Ashton repaired pole #13287 | High Pressure Sodium | 38.91691721000 | -77.02655744000
3/8/10 | 864224 | 1357 | U ST | NW | 3/8/10 | 11720 | 1G519 | (Light off/on) | DA 3-8-10 @ 341am C. Ashton repaired pole #11720 | High Pressure Sodium | 38.91709765000 | -77.03113418000
3/8/10 | 864222 | 0 | 8TH ST | NW | 3/11/10 | 22981 | 2M388 | (Light out) | DA 3-10-10 @ 1255am C. Ashton repaired pole tag missing | High Pressure Sodium | 38.90076702000 | -77.02288069000
3/8/10 | 864221 | 0 | 8TH ST | NW | 3/11/10 | 22981 | 2M388 | (Light out) | DA 3-10-10 @ 1249am C. Ashton repaired pole tag missing | High Pressure Sodium | 38.90076702000 | -77.02288069000
3/8/10 | 864179 | 0 | MARYLAND AVE | NE | 2/8/12 | 59540 | 5M240 | (Light off/on) | DA 3-8-10 @ 1252am K. Simmons pole #59540 N/C underground | High Pressure Sodium | 38.90068564000 | -76.98183306000
3/7/10 | 864141 | 1000 | NEW YORK AVE | NW | 3/10/10 | 22948 | 2L032 | (Light out) | DA 3-10-10 @ 1228am C. Ashton pole #22948 light found on and working | High Pressure Sodium | 38.90132896000 | -77.02684244000
3/7/10 | 864136 | 0500 | 8TH ST | NW | 3/10/10 | 29609 | 2M397 | (Light out) | DA 3-10-10 @ 102am C. Ashton repaired pole #29609 | High Pressure Sodium | 38.89684808000 | -77.02304941000
3/7/10 | 864132 | 715 | H ST | NW | 3/10/10 | 22567 | 2M435 | (Light out) | DA 3-10-10 @ 217am C. Ashton repaired pole #22567 | High Pressure Sodium | 38.89973194000 | -77.02259727000
3/7/10 | 864131 | 0 | 7TH ST | NW | 3/10/10 | 22410 | 6M686 | (Light out) | DA 3-10-10 @ 1141pm C. Ashton repaired pole #22410 | High Pressure Sodium | 38.90182112000 | -77.02201817000
3/7/10 | 864122 | 777 | 6TH ST | NE | 3/8/10 | 68454 | 6S588 | (Light out) | DA 3-8-10 T. Richards pole #68454 - refer to wo # 800332 | High Pressure Sodium | 38.89954137000 | -77.01979685000
3/5/10 | 863568 | 3400 | 14TH ST | NE | 3/8/10 | 51209DC | 5A098DC | (Light out) | DA 3-8-10 @ 312am K. Simmons repaired pole #51209dc Front 10-00077380-7th and webster cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93218051000 | -76.98638139000
3/4/10 | 862391 | 1748 | EAST CAPITOL ST | NE | 3/5/10 | 63712 | 6A501 | (Light out) | DA 3-5-10 @ 1130pm T. Richards repaired pole #63712 | High Pressure Sodium | 38.88973040000 | -76.97991030000
3/4/10 | 862375 | 38 | NEW YORK AVE | NE | 3/8/10 | 61254 | 6A287 | (Light out) | DA 3-8-10 @ 222am T Richards repaired pole #61254 | High Pressure Sodium | 38.90772223000 | -77.00767643000
3/4/10 | 862374 | 425 | I ST | NW | 3/8/10 | 60476 | 6B414 | (Light out) | DA 3-8-10 @ 134am T. Richards repaired pole #60476 | High Pressure Sodium | 38.90138391000 | -77.01760653000
3/4/10 | 862342 | 1100 | 1ST ST | NE | 3/8/10 | 61235 | 6S233 | (Light out) | DA 3-8-10 @ 158am T. Richards redirected photocell pole #61235 | High Pressure Sodium | 38.90411117000 | -77.00597136000
3/4/10 | 862340 | 909 | H ST | NE | 3/8/10 | 62341 | 6S091 | (Light out) | DA 3-8-10 @ 340am T. Richards repaired pole #62341 | High Pressure Sodium | 38.90011988000 | -76.99361661000
3/3/10 | 861661 | 2914 | SHERMAN AVE | NW | 3/10/10 | 12529 | 12534 | (Light out) | DA 3-5-10 @ 1205am K. Dunton pole #12529 N/C underground | High Pressure Sodium | 38.92730578000 | -77.02611400000
3/3/10 | 861569 | 1000 | NEW YORK AVE | NW | 3/4/10 | 22948 | 2L032 | (Light out) | DA 3-4-10 @ 421am C, Ashton repaired pole #22948 | High Pressure Sodium | 38.90132896000 | -77.02684244000
3/3/10 | 861526 | 0 | E ST | SW | 2/8/12 | 21609 | 6A340 | (Light out) | between 4th and 6th 10-00073451-I have listed one of the five light poles that need to be made safe for demolition. I would like to meet someone onsite to review all five locations. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.88331015000 | -77.01862717000
3/2/10 | 861103 | 0 | L ST | NW | 3/2/10 | 29222 | 2M215 | (Light off/on) | DA 3-2-10 @ 1143pm C. Ashton repaired pole #29222 | High Pressure Sodium | 38.90380035000 | -77.02723524000
3/2/10 | 860794 | 0 | MASSACHUSETTS AVE | NW | 3/4/10 | 22464 | 6A978 | (Light out) | DA 3-4-10 @ 1010pm C. Ashton repaired pole #22464 (100 ballast) | High Pressure Sodium | 38.90214093000 | -77.02159297000
3/2/10 | 860715 | 3407 | MINNESOTA AVE | SE | 3/11/10 | 76578DC | 7S023 | (Light out) | DA 3-4-10 @ 103am T. Richards pole #76578dc N/C to Overhead - there are no overhead lines on pole | High Pressure Sodium | 38.88422000000 | -76.95717076000
3/2/10 | 860445 | 805 | KENNEDY ST | NW | 3/3/10 | 4M077 | 4M077DC | (Light out) | DA 3-3-10 @ 140am K. Dunton repaired pole #4m077dc using 400 hps lamp, powerdoor and TLPC refer to wo #859939 N/A 10-00071161-light out ,,,metal pole cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.95638695000 | -77.02437107000
3/1/10 | 859939 | 805 | KENNEDY ST | NW | 3/3/10 | 4M077 | 4M077DC | (Light out) | DA 3-3-10 @ 140am K. Dunton repaired pole #4m077 | High Pressure Sodium | 38.95638695000 | -77.02437107000
3/1/10 | 859938 | 601 | KENNEDY ST | NW | 3/3/10 | 4M067 | 4M067DC | (Light out) | DA 3-3-10 @ 135am K. Dunton pole #4m067 light found on and working | High Pressure Sodium | 38.95648496000 | -77.02110063000
3/1/10 | 859842 | 232 | CARROLL ST | NW | 3/2/10 | 4H568DC | 4H568 | (Light out) | DA 3-2-10 @ 102am R. Warren repaired pole #4h568dc | High Pressure Sodium | 38.97499707000 | -77.01542228000
3/1/10 | 859822 | 0 | CARROLL ST | NW | 3/2/10 | 4H569DC | 4H569 | (Light out) | DA 3-2-10 @ 1237am R. Warren repaired pole #4h569dc | High Pressure Sodium | 38.97497351000 | -77.01515190000
3/1/10 | 859818 | 4700 | NORTH CAPITOL ST | NE | 3/4/10 | 4R754 | 4A795 | (Light out) | DA 3-4-10 @ 315am K. Simmons repaired pole #4r754 | High Pressure Sodium | 38.94814388000 | -77.00879153000
2/25/10 | 858020 | 800 | SOUTH CAPITOL ST | SE | 3/1/10 | 67058 | 68079 | (Light out) | DA 3-1-10 per billy - T. Richards bad address 2-26-10 T. Richards request for map | High Pressure Sodium | 38.88097735000 | -77.00880298000
2/25/10 | 857801 | 1101 | 11TH ST | NW | 3/1/10 | 25275 | 2M265 | (Light out) | DA 3-1-10 @ 108am C, Ashton repaired pole #25275 | High Pressure Sodium | 38.90450748000 | -77.02715607000
2/25/10 | 857777 | 1357 | U ST | NW | 3/8/10 | 11720 | 1G519 | (Light out) | DA 2-25-10 @ 1030pm K. Dunton pole #11720 N/C underground | High Pressure Sodium | 38.91709765000 | -77.03113418000
2/25/10 | 857759 | 600 | MONROE ST | NE | 2/26/10 | 56157DC | 5U728 | (Light out) | DA 2-26-10 @ 236am K. Simmons repaired pole #56157dc | High Pressure Sodium | 38.93229248000 | -76.99632168000
| 857705 | 1301 | 20TH ST | NW | 8/16/10 | 24830 | 2A017 | (Light out) | DA 8-16-10 @ 100am K. Dunton pole #24830 light found on and working R Rapolla, 3-15-2010. Reason SLPT# doesnt come up under 24730 is becuase it is 24830, DA 3-1-10 @ 1210am C. Ashton pole #24730 N/C underground 100 feet 10-00065602- cwDesc: STREETLI | High Pressure Sodium | 38.90756285000 | -77.04480461000
2/25/10 | 857297 | 707 | BARNES ST | NE | 2/25/10 | 72461DC | 7A475 | (Light off/on) | DA 2-24-10 @ 1143pm T. Richards repaired pole #72461dc | High Pressure Sodium | 38.90128978000 | -76.95054969000
2/24/10 | 857161 | 3127 | PARK DR | SE | 2/25/10 | 74760DC | 7A074DC | (Light out) | DA 2-25-10 @ 305am T. Richards pole #74760dc- new pole installed, arm and fixture need to be transfered to new pole refer to wo #846540 | High Pressure Sodium | 38.85948088000 | -76.95794149000
2/24/10 | 856549 | 0 | M ST | NW | 2/24/10 | 23719 | 2G722 | (Light out) | DA 2-24-10 @ 1030pmC. Ashton repaired pole #23719 | High Pressure Sodium | 38.90557300000 | -77.04706313000
2/24/10 | 856544 | 0 | 17TH ST | NW | 2/25/10 | 26728 | 2M083 | (Light out) | DA 2-25-10 @ 345am C. Ashton repaired pole #26728 | High Pressure Sodium | 38.90851181000 | -77.03858203000
2/24/10 | 856543 | 1701 | 17TH ST | NW | 2/26/10 | 26736 | 2M062 | (Light out) | DA 2-26-10 @ 1150pm C. Ashton repaired pole #26736 | High Pressure Sodium | 38.91179662000 | -77.03856951000
2/24/10 | 856531 | 2914 | SHERMAN AVE | NW | 2/24/10 | 12529 | 12534 | (Light off/on) | DA 2-24-10 @ 1228am C. Ashton repaired pole #12529 | High Pressure Sodium | 38.92730578000 | -77.02611400000
2/23/10 | 856378 | 5326 | CONNECTICUT AVE | NW | 2/24/10 | 30542 | 3E017 | (Light out) | DA 2-24-10 @ 315am K. Dunton pole #30542 light found on and working 5400-5700 10-00062716-Several Streetlights Out from 5400-5700 Connecticut Ave NW on both sides. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.96076273000 | -77.07303810000
2/23/10 | 856090 | 705 | ANACOSTIA AVE | NE | 2/24/10 | 72356DC | 7A478 | (Light out) | DA 2-24-10 @ 1130pm T. Richards repaired pole #72356dc | High Pressure Sodium | 38.90141616000 | -76.95127149000
2/22/10 | 855668 | 0 | 1ST ST | NE | 2/8/12 | 61238 | 6A261 | (Light out) | DA 2-23-10 @ 244am T. Richards pole #61238 N/C underground Front 10-00061161- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90488153000 | -77.00596863000
2/22/10 | 855357 | 1500 | KEARNEY ST | NE | 2/24/10 | 59986 | 5A177 | (Light out) | DA 2-23-10 @ 115am K. Simmons pole #59986 N/C underground Alley 10-00060432- cwDesc: ALLEYLIGHT REPAIR | High Pressure Sodium | 38.91401980000 | -77.01759054000
2/22/10 | 855043 | 0000 | 22ND ST | SE | 2/8/12 | 68335 | 6M814 | (Light out) | DA 2-23-10 @ 344am T. Richards pole #68335 N/C underground | High Pressure Sodium | 38.88810813000 | -76.97400907000
2/21/10 | 854982 | 0 | D ST | SW | 3/3/10 | 21625 | 6L714 | (Light out) | DA 2-22-10 @ 359am V. Cooke pole #21625 N/C underground | High Pressure Sodium | 38.88478652000 | -77.01928219000
2/21/10 | 854923 | 601 | KENNEDY ST | NW | 2/23/10 | 4M067 | 4M067DC | (Light out) | DA 2-23-10 @ 1218am R. Warren repaired pole #4m067 | High Pressure Sodium | 38.95648496000 | -77.02110063000
2/19/10 | 854015 | 418 | NEW YORK AVE | NW | 2/19/10 | 60064 | 6A170 | (Light off/on) | DA 2-19-10 @ 400am T. Richards repaired pole #60064 | High Pressure Sodium | 38.90422287000 | -77.01773238000
2/19/10 | 854003 | 100 | FLORIDA AVE | NE | 2/10/12 | 56987 | 5M122 | (Light out) | DA 2-19-10 @ 1250am K. Simmons pole #56987 Traffic Pole - has been hit t base damaged , fixture missing - pole needs repair before new fixture can be installed - Refer to DDOT | High Pressure Sodium | 38.90908053000 | -77.00524436000
2/18/10 | 853842 | 3127 | PARK DR | SE | 2/22/10 | 74760DC | 7A074DC | (Light out) | DA 2-22-10 @ 1209am T. Richards pole #74760dc new pole installed arm and fixture need to be transfered to new pole refer to open wo #846540 | High Pressure Sodium | 38.85948088000 | -76.95794149000
2/18/10 | 853819 | 4479 | F ST | SE | 2/22/10 | 75749 | 75749DC | (Light out) | DA 2-22-10 @ 1253am T. Richards repaired pole #75749 | High Pressure Sodium | 38.88184868000 | -76.93731162000
2/18/10 | 853817 | 4651 | BENNING RD | SE | 2/22/10 | 75822 | 75822DC | (Light out) | DA 2-22-10 @ 1233am T. Richards repaired pole #75822 | High Pressure Sodium | 38.87611644000 | -76.93130301000
2/18/10 | 853802 | 946 | T ST | NW | 2/19/10 | 13448 | 1L365 | (Light out) | DA 2-19-10 @ 318am C. Ashton repaired pole #13448 | High Pressure Sodium | 38.91552297000 | -77.02567379000
2/18/10 | 853766 | 3100 | SHERMAN AVE | NW | 3/4/10 | 12820 | 1L255 | (Light out) | DA 2-18-10 @ 1050pm C. Ashton pole #12820 N/C Underground | High Pressure Sodium | 38.92892725000 | -77.02615558000
2/18/10 | 853508 | 60 | FLORIDA AVE | NE | 2/19/10 | 56991 | 5M143 | (Light out) | DA 2-19-10 @ 115am K. Simmons repaired pole #56991 Front 10-00055540- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90995698000 | -77.00685274000
2/17/10 | 853416 | 0 | WISCONSIN AVE | NW | 2/18/10 | 30137 | 3G019 | (Light out) | DA 2-17-10 @ 1110pm K. Dunton repaired pole #30137 | High Pressure Sodium | 38.92630371000 | -77.07330137000
2/17/10 | 853412 | 1000 | H ST | NW | 2/18/10 | 22618 | 2G962 | (Light off/on) | DA 2-17-10 @ 1042pm C. Ashton repaired pole #22618 right fixture | High Pressure Sodium | 38.89990719000 | -77.02660550000
2/17/10 | 853411 | 1000 | H ST | NW | 2/18/10 | 22618 | 2G962 | (Light off/on) | DA 2-17-10 @ 1036pm C. Ashton repaired pole #22618 left fixture | High Pressure Sodium | 38.89990719000 | -77.02660550000
2/17/10 | 853410 | 0 | H ST | NW | 2/18/10 | 22619 | 2G963 | (Light out) | DA 2-17-10 @ 1028pm C. Ashton repaired pole #22619 right fixture | High Pressure Sodium | 38.89990649000 | -77.02637602000
2/17/10 | 853379 | 3400 | 14TH ST | NE | 2/18/10 | 51208DC | 5A097DC | (Light out) | DA 2-18-10 @ 310am K. Simmons repaired pole #51208dc | High Pressure Sodium | 38.93195155000 | -76.98636408000
2/16/10 | 852917 | 0 | NEW YORK AVE | NW | 2/18/10 | 22911 | 2L053 | (Light out) | DA 2-17-10 @ 1011pm C. Ashton repaired pole #22911 | High Pressure Sodium | 38.90141042000 | -77.02582476000
2/16/10 | 852916 | 0 | H ST | NW | 2/18/10 | 22619 | 2G963 | (Light out) | DA 2-17-10 @ 1025pm C. Ashton repaired pole #22619 - left fixture | High Pressure Sodium | 38.89990649000 | -77.02637602000
2/16/10 | 852898 | 0 | M ST | NW | 2/19/10 | 23739 | 2G718 | (Light out) | DA 2-18-10 @ 155am C. Ashton repaired pole #23739 | High Pressure Sodium | 38.90513126000 | -77.04778068000
2/16/10 | 852894 | 1200 | NEW HAMPSHIRE AVE | NW | 2/17/10 | 23857 | 2G721 | (Light out) | DA 2-17-10 @ 154am C. Ashton repaired pole #23857 | High Pressure Sodium | 38.90549424000 | -77.04744210000
2/16/10 | 852884 | 2335 | 18TH ST | NW | 2/18/10 | 10259 | 1G494 | (Light out) | DA 2-18-10 @ 104am C. Ashton pole #10259 N/C underground | High Pressure Sodium | 38.92037631000 | -77.04180732000
2/15/10 | 852485 | 1218 | CONNECTICUT AVE | NW | 2/10/12 | 24532 | 2U519 | (Light out) | DA 2-15-10 @ 1101pm C. Ashton pole #24532 N/C @ fixture - No Access to base due to Snow | High Pressure Sodium | 38.90651643000 | -77.04185036000
2/15/10 | 852418 | 3859 | PENNSYLVANIA AVE | SE | 2/15/10 | 77881DC | 7E010 | (Light out) | 2-15-10 - bcm- H. Lancaster repaired pole | High Pressure Sodium | 38.86525460000 | -76.95024453000
2/15/10 | 852407 | 4651 | BENNING RD | SE | 2/15/10 | 75822 | 75822DC | (Light out) | 2-15-10 - bcm- H. Lancaster repaired pole | High Pressure Sodium | 38.87611644000 | -76.93130301000
2/14/10 | 852332 | 0000 | MICHIGAN AVE | NE | 3/25/12 | 50071 | 2A058 | (Light out) | DA 2-15-10 @ 245am K. Simmons pole # 50071 N/C underground Front 10-00051363-need a repair cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90029517000 | -77.03986681000
2/11/10 | 852156 | 737 | 7TH ST | NW | 2/15/10 | 22450 | 6M647 | (Light out) | DA 2-15-10 @ 330am C. Ashton adjusted and secured lens pole #22450 front 10-00047571-lamp covering is dangling and looks like it will fall really soon.. requesting to have lamp covering fixed as soon as possible cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89929255000 | -77.02181765000
2/5/10 | 851748 | 1526 | 17TH ST | NW | 2/5/10 | 26733 | 2M019 | (Light off/on) | DA 2-5-10 @ 336am C. Ashton repaired pole #26733 | High Pressure Sodium | 38.91050765000 | -77.03840258000
2/5/10 | 851741 | 1724 | 17TH ST | NW | 2/5/10 | 26740 | 2M054 | (Light off/on) | DA 2-5-10 @ 327am C. Ashton repaired pole #26740 | High Pressure Sodium | 38.91352294000 | -77.03857053000
2/4/10 | 851703 | 0000 | MICHIGAN AVE | NE | 3/25/12 | 50071 | 2A058 | (Light out) | DA 2-4-10 @ 1124pm K. Simmons pole #50071 N/C Underground | High Pressure Sodium | 38.90029517000 | -77.03986681000
2/4/10 | 851465 | 409 | K ST | NW | 2/4/10 | 60464 | 6A119 | (Light out) | DA 2-4-10 @ 1010pm V. Cooke repaired pole #60464 | High Pressure Sodium | 38.90260440000 | -77.01732153000
2/4/10 | 851442 | 214 | L ST | NE | 2/5/10 | 61364 | 6B081 | (Light out) | 2-5-10 D.Brown---repaired (sc) | High Pressure Sodium | 38.90368595000 | -77.00276993000
2/4/10 | 850982 | 1000 | NEW YORK AVE | NW | 2/4/10 | 22948 | 2L032 | (Light out) | DA 2-4-10 @ 1121pm C. Ashton repaired pole #22948 DA 2-4-10 @ 237am C. Ashton pole #22948 - Needs conversion kit | High Pressure Sodium | 38.90132896000 | -77.02684244000
2/4/10 | 850981 | 0 | NEW YORK AVE | NW | 2/4/10 | 22913 | 2L062 | (Light out) | DA 2-4-10 @ 213am C .Ashton repaired pole #22913 | High Pressure Sodium | 38.90113457000 | -77.02657407000
2/4/10 | 850979 | 0 | 11TH ST | NW | 2/4/10 | 23368 | 2L033 | (Light off/on) | DA 2-4-10 @ 209am C. Ashton repaired pole #23368 | High Pressure Sodium | 38.90140330000 | -77.02724355000
2/2/10 | 849529 | 1412 | 33RD ST | NW | 2/2/10 | 20731 | 2G186 | (Light off/on) | DA 2-2-10 @ 300am C. Ashton repaired pole #20731 | High Pressure Sodium | 38.90826387000 | -77.06601588000
2/2/10 | 849518 | 1404 | H ST | NE | 2/5/10 | 62326 | 6S139 | (Light out) | DA 2-5-10 @ 1245am T. Richards repaired pole #62326 | High Pressure Sodium | 38.90029477000 | -76.98535817000
1/28/10 | 847610 | 635 | 20TH ST | NE | 2/2/10 | 70021 | 7A022 | (Light off/on) | DA 2-2-10 @ 241am T. Richards repaired pole #70021 | High Pressure Sodium | 38.89707182000 | -76.97589261000
1/28/10 | 847586 | 44 | H ST | NW | 2/1/10 | 60398 | 6A199 | (Light out) | DA 2-1-10 @ 1010pm C. Ashton repaired pole #60398 DA 1-29-10 C. Ashton request for map | High Pressure Sodium | 38.90030973000 | -77.01534450000
1/28/10 | 847530 | 0 | CAMDEN ST | SE | 2/2/10 | 74761DC | 7A075DC | (Light out) | DA 2-1-10 @ 1145pm T. Richards repired pole #74761dc (2 split bolts) DA 1-29-10 @ 120am T. Richards pole #74761dc - pepco installed new overhead wires - NEEDS LARGE SPLIT BOLT | High Pressure Sodium | 38.85947446000 | -76.95731462000
1/28/10 | 847316 | 801 | P ST | NW | 2/1/10 | 25808 | 6U460 | (No current) | vw 2-1-2010 Greenfield/Brewer - made splices in T -Base - complete | High Pressure Sodium | 38.90960163000 | -77.02357636000
1/27/10 | 846540 | 3127 | PARK DR | SE | 4/14/10 | 74760DC | 7A074DC | (Light out) | DA 1-28-10 @ 1234am T. Richards pole #74760dc new pole installed arm and fixture need to be transfered to new pole MD Side 10-00029265-light near alley cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.85948088000 | -76.95794149000
1/26/10 | 845333 | 1200 | 18TH ST | NW | 1/27/10 | 24762 | 2U525 | (Light out) | DA 1-26-10 @ 1100pm K. Dunton repaired pole #24762 | High Pressure Sodium | 38.90604331000 | -77.04159886000
1/26/10 | 844246 | 618 | H ST | NW | 1/26/10 | 22561 | 6M699 | (Light off/on) | DA 1-26-10 @ 339am V. Cooke repaired pole #22561 | High Pressure Sodium | 38.89973495000 | -77.02087482000
1/26/10 | 844233 | 0 | L ST | NW | 1/26/10 | 24637 | 2G783 | (Light off/on) | DA 1-26-10 @ 235am V. Cooke repaired pole #24637 | High Pressure Sodium | 38.90367717000 | -77.04866329000
1/25/10 | 843871 | 3301 | SHERMAN AVE | NW | 1/27/10 | 12874 | 1L279 | (Light out) | DA 1-26-10 @ 1050pm R. Warren repaired pole #12874 1-26-2010 A Johnson - Replaced T-Base 100% complete | High Pressure Sodium | 38.93089776000 | -77.02642978000
1/25/10 | 843189 | 2101 | WISCONSIN AVE | NW | 1/25/10 | 29803 | 3G117 | (Light off/on) | DA 1-25-10 @ 245am V. Cooke repaired pole #29803 | High Pressure Sodium | 38.91692553000 | -77.06883584000
1/22/10 | 841445 | 0 | NEW YORK AVE | NE | 5/6/10 | 56856 | 5M133 | (Light out) | DA 1-22-10 @ 252am K. Simmons pole #56856 Traffic pole needs arm repaired or tightened / arm is very loose | High Pressure Sodium | 38.90889349000 | -77.00418950000
1/22/10 | 841434 | 2038 | 18TH ST | NW | 1/22/10 | 11414 | 1G510 | (Light out) | DA 1-22-10 @ 1235am R. Warren repaired pole #11414 | High Pressure Sodium | 38.91777981000 | -77.04149864000
1/22/10 | 841430 | 0 | 18TH ST | NW | 1/22/10 | 11502 | 1G477 | (Light out) | DA 1-22-10 @ 1208am R ,Warren repaired pole #11502 - adjusted TLPC | High Pressure Sodium | 38.92245024000 | -77.04270127000
1/21/10 | 840308 | 0 | FLORIDA AVE | NE | 2/8/12 | 62313 | 5M114 | (Light out) | DA 1-21-10 @ 1220am K. Simmons pole #62313 NC underground | High Pressure Sodium | 38.90860897000 | -77.00417478000
1/21/10 | 840306 | 64 | NEW YORK AVE | NE | 1/21/10 | 56752 | 5M127 | (Light out) | DA 1-21-10 @ 1215am K. Simmons repaired pole #56752 | High Pressure Sodium | 38.90868561000 | -77.00559893000
1/21/10 | 840305 | 100 | FLORIDA AVE | NE | 2/10/12 | 56987 | 5M122 | (Light out) | DA 1-21-10 @ 1211am K. Simmons pole #56987 needs t base (Traffic pole refer to ddot) | High Pressure Sodium | 38.90908053000 | -77.00524436000
1/20/10 | 839592 | 5322 | ASTOR PL | SE | 1/21/10 | 75569 | 75569DC | (Light out) | DA 1-21-10 @ 314am T. Richards repaired pole #75569 | High Pressure Sodium | 38.88655037000 | -76.92533812000
1/20/10 | 839570 | 4431 | F ST | SE | 1/21/10 | 75747 | 75747DC | (Light out) | DA 1-21-10 @ 1031pm T. Richards pole #75747 light found on and working | High Pressure Sodium | 38.88175349000 | -76.93806754000
1/19/10 | 838715 | 214 | L ST | NE | 1/20/10 | 61364 | 6B081 | (Light out) | DA 1-20-10 @ 213am T. Ricards pole 61364 ligt found on and working | High Pressure Sodium | 38.90368595000 | -77.00276993000
1/19/10 | 838689 | 1447 | MARYLAND AVE | NE | 2/8/12 | 63606 | 6M740 | (Light out) | JWB - 1/22/10 - New poles being installed by third party contractor. Existing poles are to be removed. DA 1-19-10 @ 1008pm T. Richards pole #63606 N/C underground | High Pressure Sodium | 38.89979680000 | -76.98400772000
1/18/10 | 838239 | 0 | INTERSTATE 295 | SE | 1/18/10 | 86513 | 8L772 | (Light off/on) | DA 1-18-10 @ 1051pm K.Simmons repaired pole #86513 | High Pressure Sodium | 38.86640747000 | -76.99106026000
1/18/10 | 838237 | 0 | INTERSTATE 295 | SE |  | 86513 | 8L772 | (Light off/on) |  | High Pressure Sodium | 38.86640747000 | -76.99106026000
1/18/10 | 838236 | 0 | INTERSTATE 295 | SE | 6/16/11 | 86513 | 8L772 | (Light off/on) |  | High Pressure Sodium | 38.86640747000 | -76.99106026000
1/18/10 | 838196 | 712 | 15TH ST | NE | 2/8/12 | 62906 | 6M748 | (Light out) | DA 1-19-10 @ 1058pm T. Richards pole #62906 N/C undeground (new poles installed) JWB - 1/22/09 - New poles being installed by third party contractor. Existing poles are to be removed. | High Pressure Sodium | 38.89952311000 | -76.98355707000
1/15/10 | 836649 | 515 | NEW YORK AVE | NE | 1/18/10 | 56841 | 5A428 | (Light out) | DA 1-14-10 @ 1020pm R. Warren pole #56841 N/C underground | High Pressure Sodium | 38.91151960000 | -76.99667276000
1/14/10 | 836623 | 2400 | WISCONSIN AVE | NW | 1/15/10 | 30148 | 3G069 | (Light off/on) | DA 1-15-10 @ 110am K. Dunton repaired pole #30148 | High Pressure Sodium | 38.92126773000 | -77.07224581000
1/14/10 | 836614 | 2420 | WISCONSIN AVE | NW | 1/15/10 | 30147 | 3G067 | (Light out) | DA 1-15-10 @ 305am K. Dunton adjusted photocell pole #30147 | High Pressure Sodium | 38.92145383000 | -77.07236458000
1/14/10 | 836007 | 4520 | HOBAN RD | NW | 1/15/10 | 35822DC | 35822 | (Light out) | DA 1-15-10 @ 215am K. Dunton repaired pole #35822dc Front 10-00013020-top of the road....oneway street....globe is leaning to the bottom cwDesc: STREETLIGHT REPAIR | Incandescent | 38.91433459000 | -77.08526855000
| 835707 | 0 | BANGOR ST | SE | 2/24/10 | 74834DC | 7A097DC | (Light out) | DA 1-19-10 @ 109am T. Richards rpaired pole #74834dc Front 10-00012565-WOODEN POLE cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86054896000 | -76.96121450000
1/13/10 | 835277 | 2800 | LINCOLN RD | NE | 1/13/10 | 50065 | 5A056 | (Light out) | DA 1-13-10 @ 1050pm K. Simmons repaired pole #50065 | High Pressure Sodium | 38.92549974000 | -77.00275988000
1/12/10 | 834384 | 0 | 23RD ST | NW | 1/14/10 | 28342 | 2M279 | (Light out) | DA 1-14-10 @ 230am V. Cooke pole #28342 light found on and working | High Pressure Sodium | 38.90081677000 | -77.05001410000
1/12/10 | 834362 | 1801 | P ST | NW | 1/14/10 | 26339 | 2M169 | (Light out) | DA 1-114-10 @ 1240am V. Cooke repaired pole #26339 | High Pressure Sodium | 38.90971066000 | -77.04178765000
1/11/10 | 833603 | 3600 | STERLING ST | SE | 1/11/10 | 85309DC | 8M013DC | (Light out) | DA 1-11-10 @ 1037pm K. Simmons repaired ole #85309dc | High Pressure Sodium | 38.83967824000 | -77.00530403000
1/10/10 | 832885 | 301 | K ST | SE | 1/13/10 | 67660 | 6A449 | (Light out) | DA 1-13-10 @ 105am K. Dunton repaired pole #67660 | High Pressure Sodium | 38.87835619000 | -77.00175680000
1/7/10 | 831925 | 0 | 15TH ST | NE | 4/16/12 | 63608 | 6M752 | (Light out) | BCM - 4/16/2012 - LIGHT ON - POLE REMOVED DA 1-10-10 @ 1015pm T .Richards pole #63608 - N/C Underground | High Pressure Sodium | 38.90000576000 | -76.98341256000
1/7/10 | 831922 | 1000 | M ST | SE | 1/12/10 | 67367 | 6L939 | (Light out) | DA 1-12-10 @ 1213am K. Simmons repaired pole #67367 | High Pressure Sodium | 38.87641377000 | -76.99123690000
1/7/10 | 831911 | 0 | INTERSTATE 395 | SW |  | 28688 | 6A579 | (Light out) | DA 1-13-10 @ 3334am T. Richards pole #28688 N/C underground - t base is buried at bottem of pole ) | High Pressure Sodium | 38.88293251000 | -77.01275060000
1/7/10 | 831908 | 0 | SOUTH CAPITOL ST | SE | 1/8/10 | 82044 | 8M062 | (Light out) | DA 1-07-10 @ 1132pm T. Richards repaired pole #82044 | High Pressure Sodium | 38.86042806000 | -77.00347620000
1/7/10 | 831892 | 0 | INTERSTATE 295 | SE | 1/13/10 | 68023 | 6L973 | (Light out) | DA 1-13-10@ 420am T. Richards repaired pole #68023 | High Pressure Sodium | 38.87812257000 | -76.99325914000
1/6/10 | 830701 | 601 | D ST | NW | 2/8/12 | 60094 | 6S600 | (Light out) | DA 1-07-10 @ 227am T. Richards pole #60094 N/C underground - (3rd party contractor) Front 10-00004138-no street lights at all in this block,needs immediate attention cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89486033000 | -77.02070899000
1/6/10 | 830673 | 0 | MAINE AVE | SW | 1/7/10 | 28711 | 6M436 | (Light off/on) | DA 1-06-10 @ 1100pm V. Cooke repaired pole #28711 | High Pressure Sodium | 38.88301916000 | -77.03142349000
1/6/10 | 830369 | 0 | 18TH ST | NW |  | 11502 | 1G477 | (Light out) |  | High Pressure Sodium | 38.92245024000 | -77.04270127000
1/5/10 | 829948 | 1818 | 14TH ST | NW | 1/6/10 | 26564 | 2A084 | (Light out) | DA 1-05-10 @ 1045pm V. Cooke repaired pole #26564 | High Pressure Sodium | 38.91478338000 | -77.03206538000
1/5/10 | 829858 | 0 | 13TH PL | NW | 1/11/10 | 4J740 | 4U153 | (Light out) | DA 1-11-11 @ 1218am R. Warren repaired pole #4j740 | High Pressure Sodium | 38.94182450000 | -77.02958631000
1/5/10 | 829787 | 0 | K ST | NE | 1/6/10 | 59553 | 5B232 | (Light out) | DA 1-06-10 @ 1209am K. Simmons repaired pole #59553 | High Pressure Sodium | 38.90270633000 | -76.98150420000
| 829133 | 639 | NEW YORK AVE | NW | 1/7/10 | 25975 | 6A087 | (Light out) | DA 1-06-10 @ 1030pm V. Cooke repaired pole #25975 Front 10-00001886- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90309208000 | -77.02099074000
1/4/10 | 829012 | 3641 | GEORGIA AVE | NW | 1/5/10 | 11243 | 1G225 | (Light out) | DA 1-05-10 @ 123am R. Warren repaired pole #11243 | High Pressure Sodium | 38.93558413000 | -77.02406687000
1/4/10 | 828990 | 941 | T ST | NW | 1/7/10 | 13449 | 1L366 | (Light out) | DA 1-07-10 @ 145am K. Dunton pole #13449 N/C underground | High Pressure Sodium | 38.91563302000 | -77.02547606000
1/4/10 | 828978 | 0 | SHERMAN AVE | NW | 1/8/10 | 12587 | 1G451 | (Light out) | DA 1-04-10 @@ 1112pm R. Warren pole #12587 N/C underground | High Pressure Sodium | 38.92300485000 | -77.02549655000
1/4/10 | 828965 | 815 | V ST | NW | 1/7/10 | 14235 | 1U030 | (Light off/on) | DA 1-07-10 @ 250am K. Dunton adjusted TLPC pole 14235 | High Pressure Sodium | 38.91785954000 | -77.02338967000
1/4/10 | 828899 | 3126 | PENNSYLVANIA AVE | SE | 1/6/10 | 78555DC | 7E100DC | (Light out) | DA 1-06-10 @ 316am T. Richards repaired pole #78555dc | High Pressure Sodium | 38.86992937000 | -76.96211991000
1/4/10 | 828897 | 3300 | PENNSYLVANIA AVE | SE | 1/6/10 | 78544DC | 7E115DC | (Light out) | DA 1-06-10 @ 322am T. Richards repaired pole #78544dc | High Pressure Sodium | 38.86824545000 | -76.95800685000
1/4/10 | 828894 | 2000 | FORT DAVIS ST | SE | 1/6/10 | 78523DC | 7E142 | (Light out) | DA 1-06-10 @ 1237am T. Richards repaired pole #78523dc | High Pressure Sodium | 38.86502980000 | -76.95013502000
1/3/10 | 828280 | 4577 | NANNIE HELEN BURROUGHS AVE | NE | 1/3/10 | 71302DC | 7A237 | (Light off/on) | DA 1-03-10 @ 1119pm T. Richards repaired pole #71302dc | High Pressure Sodium | 38.89961652000 | -76.93660108000
1/3/10 | 828266 | 2420 | WISCONSIN AVE | NW | 1/4/10 | 30147 | 3G067 | (Light out) | DA 1-04-10 @ 355am K. Dunton secured t base door pole #30147 2418 wisconsin ave nw 10-00000303-streetlight at this address - metal cover at base of pole is not secured; can you please fix this; wires are exposed to weather and children; thank you cwDesc | High Pressure Sodium | 38.92145383000 | -77.07236458000
12/30/09 | 827605 | 0 | PIERCE ST | NE | 12/30/09 | 61236 | 6A258 | (Light out) | DA 12-30-9 @ 1022pm T. Richards installed missing TLPC pole #61236 | High Pressure Sodium | 38.90445580000 | -77.00596738000
| 827543 | 1100 | 1ST ST | NE | 12/30/09 | 61235 | 6S233 | (Light out) | DA 12-30-09 @ 1016pm T. Richards installed missing TLPC Pole #61235 Front 09-03188657- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90411117000 | -77.00597136000
12/30/09 | 827328 | 0 | 23RD ST | NW | 2/23/10 | 28345 | 2M285 | (Light out) | DA 12-31-09 @ 1235am V. Cooke repaired pole tag missing | High Pressure Sodium | 38.90189255000 | -77.05000095000
12/30/09 | 827276 | 4308 | NANNIE HELEN BURROUGHS AVE | NE | 1/3/10 | 71312DC | 7A246 | (Light out) | DA 1-03-10 @ 1113pm T. Richards repaired pole #71312dc | High Pressure Sodium | 38.90072786000 | -76.93937809000
12/30/09 | 827275 | 0 | GRANT ST | NE | 12/31/09 | 72339DC | 7A216 | (Light out) | DA 12-31-09 @303am T. Richards pole 72339dc light found on and working | High Pressure Sodium | 38.89843429000 | -76.93131145000
12/30/09 | 827200 | 0 | NEW YORK AVE | NW | 1/4/10 | 22951 | 2L065 | (Light out) | DA 1-03-10 @ 1155pm V. Cooke pole #22951 light found on and working | High Pressure Sodium | 38.90154741000 | -77.02618337000
12/30/09 | 827177 | 1442 | WISCONSIN AVE | NW | 12/31/09 | 20512 | 2G151 | (Light out) | DA 12-30-09 @ 1144pm V. Cooke repaired pol #20512 | High Pressure Sodium | 38.90878897000 | -77.06418248000
12/29/09 | 826388 | 0 | C ST | SW | 1/6/10 | 21748 | 6A386 | (Light out) | DA 1-03-09 @ 1025pmV. Cooke pole #21748 N/C underground DA 12-29-09 @ 1140pm V. Cooke pole #21748 Needs 400 MV bulb | High Pressure Sodium | 38.88607059000 | -77.01250580000
12/29/09 | 826374 | 618 | H ST | NW | 12/30/09 | 22561 | 6M699 | (Light out) | DA 12-30-09 @ 240an V Cooke pole #22561 light found on and working | High Pressure Sodium | 38.89973495000 | -77.02087482000
12/29/09 | 826369 | 601 | D ST | NW | 1/11/10 | 60174 | 6S597 | (Light out) | DA 12-29-09 1109pm T. Richards pole #60174 N/C Underground | High Pressure Sodium | 38.89474946000 | -77.02020412000
12/29/09 | 826362 | 1025 | 4TH ST | NW | 1/6/10 | 60456 | 6S480 | (Light out) | Light in Constuction Area - being replaced by third party (Capitol Paving - Carlos Avila - 202-529-7225) DA 12-29-09 @ 1135pm T. Richards pole #60456 N/C underground | High Pressure Sodium | 38.90380410000 | -77.01611081000
12/29/09 | 826360 | 709 | H ST | NW | 12/30/09 | 22630 | 2M424 | (Light out) | DA 12+-30-09 @ 225am V. Cooke repaired pole #22630 | High Pressure Sodium | 38.89990397000 | -77.02240296000
12/29/09 | 826354 | 0 | MASSACHUSETTS AVE | NW | 12/30/09 | 22469 | 6A983 | (Light out) | DA 12-30-09 @ 210am V .Cooke repaired pole #22469 | High Pressure Sodium | 38.90162590000 | -77.02008550000
12/29/09 | 826353 | 900 | 6TH ST | NW | 1/5/10 | 60538 | 6S551 | (Light out) | DA 12-29-09 @ 1124pm T. Richards pole #60538 N/C underground | High Pressure Sodium | 38.90101088000 | -77.01979021000
12/29/09 | 825818 | 1818 | 14TH ST | NW | 12/29/09 | 26564 | 2A084 | (Light off/on) | DA 12-29-09 @ 155am V. Cooke repaired pole #26564 | High Pressure Sodium | 38.91478338000 | -77.03206538000
12/29/09 | 825817 | 2425 | 14TH ST | NW | 12/29/09 | 12046 | 1A049 | (Light off/on) | DA 12-29-09 @ 140am V. Cooke repaired pole #12046 | High Pressure Sodium | 38.92156215000 | -77.03202917000
12/28/09 | 825790 | 0000 | H ST | NE | 12/28/09 | 68252DC | 68252 | (Light out) | DA 12-28-09 @ 1014pm T. Richards repaired pole #68252dc | High Pressure Sodium | 38.90032915000 | -77.00287599000
12/28/09 | 825064 | 1063 | 3RD ST | NE |  | 61352 | 6S416 | (No current) |  | High Pressure Sodium | 38.90320663000 | -77.00197013000
12/28/09 | 825060 | 0 | NEW YORK AVE | NE |  | 61252 | 5M104 | (Light out) | DA 12-28-09 @ 105am K. Simmons pole #61252 N/C underground | High Pressure Sodium | 38.90823571000 | -77.00619583000
12/27/09 | 824996 | 3030 | 14TH ST | NW | 3/10/11 | 15022 | 1G010 | (Light out) | DA 12-29-09 @ 1250am V. Cooke pole #15022 defective teardrop fixture | High Pressure Sodium | 38.92847462000 | -77.03272597000
12/24/09 | 824586 | 3943 | PENNSYLVANIA AVE | SE | 12/28/09 | 78579DC | 7E003DC | (Light off/on) | DA 12-27-09 @ 1141pm K. Simmons repaired pole #78579dc | High Pressure Sodium | 38.86417025000 | -76.94760339000
12/23/09 | 823908 | 1801 | P ST | NW | 12/23/09 | 26339 | 2M169 | (Light off/on) | DA 12-23-09 @ 355am V. Cooke repaired pole #26339 | High Pressure Sodium | 38.90971066000 | -77.04178765000
12/23/09 | 823907 | 0 | P ST | NW | 12/23/09 | 26340 | 2M170 | (Light off/on) | DA 12-23-09 @ 335am V. Cooke repaired pole #26340 | High Pressure Sodium | 38.90959184000 | -77.04155598000
12/23/09 | 823906 | 0 | 18TH ST | NW | 12/23/09 | 26759 | 2M165 | (Light off/on) | DA 12-23-09 @ 320am V. Cooke repaired pole #26759 | High Pressure Sodium | 38.91001359000 | -77.04161294000
12/23/09 | 823884 | 0 | NEW YORK AVE | NE | 1/6/10 | 56832 | 5M053 | (Light out) | DA 12-22-09 @ 1115pm V. Cooke pole #56832 N/C underground | High Pressure Sodium | 38.91324438000 | -76.99169504000
12/17/09 | 821851 | 401 | I ST | SE | 12/18/09 | 67653 | 6B422 | (Light out) | DA 12-17-09 @ 1154pm T. Richards pole #67653 -- N/C underground | High Pressure Sodium | 38.87922775000 | -77.00050346000
12/14/09 | 819185 | 0 | NEW YORK AVE | NE | 12/14/09 | 50011 | 5A045 | (Light out) | DA 12-14-09 @ 1033pm T. Richards repaied pole #50011 | High Pressure Sodium | 38.91707776000 | -76.96424700000
12/14/09 | 818185 | 810 | 5TH ST | NW | 12/16/09 | 60077 | 68300 | (Light off/on) | DA 12-14-09 @ 1219am T. Richards repaired pole tag missing 12-15-09 S.Manning---previously tagged | High Pressure Sodium | 38.89994449000 | -77.01884166000
12/13/09 | 818170 | 789 | 5TH ST | NE | 12/14/09 | 61723 | 6S059 | (Light out) | DA 12-13-09 @ 1129pm T. Richards repaired pole #61723 | High Pressure Sodium | 38.90011815000 | -76.99935657000
12/13/09 | 818160 | 0 | 23RD ST | NW | 2/2/12 | 28318 | 2M274 | (Light out) | DA 12-14-09 @ 220am V. Cooke pole #28318 N/C Underground | High Pressure Sodium | 38.89313901000 | -77.05025238000
12/13/09 | 818148 | 1063 | 3RD ST | NE | 12/13/09 | 61352 | 6S416 | (Light out) | East Side 09-03170253- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90320663000 | -77.00197013000
12/13/09 | 818147 | 44 | H ST | NW | 12/14/09 | 60397 | 68450 | (Light out) | DA 12-1-09 @ 1228am T. Ricards repaired pole #60397 south side of bridge 09-03170252- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90030196000 | -77.01493317000
12/11/09 | 817228 | 1101 | 11TH ST | NW | 12/11/09 | 25275 | 2M265 | (Light out) | 12-10-09 I.Paraway---repaired (sc) | High Pressure Sodium | 38.90450748000 | -77.02715607000
12/11/09 | 817126 | 1653 | BENNING RD | NE | 12/13/09 | 63612 | 6M773 | (Light out) | DA 12-13-09 @ 1007pm T. Richards repaired pole #63612 | High Pressure Sodium | 38.89933568000 | -76.97960563000
12/10/09 | 817056 | 0 | WISCONSIN AVE | NW | 12/11/09 | 30145 | 3G056 | (Light out) | DA 12-10-09 @ 1045pm K. Dunton pole #30145 light found on and working | High Pressure Sodium | 38.92250517000 | -77.07302857000
12/10/09 | 817055 | 2420 | WISCONSIN AVE | NW | 12/15/09 | 30147 | 3G067 | (Light out) | DA 12-15-09 @ 330am K. Dunton repaired pole #30147 | High Pressure Sodium | 38.92145383000 | -77.07236458000
12/10/09 | 816030 | 1200 | S ST | SE | 12/10/09 | 81006 | 8L854 | (Light out) | DA 12-10-09 @ 1035pm K. Simmons repaired pole #81006 | High Pressure Sodium | 38.86833500000 | -76.98809085000
12/10/09 | 816028 | 1000 | M ST | SE | 12/14/09 | 67376 | 6L940 | (Light out) | DA 12-10-09 @ 1110pm T. Richards pole #67376 - lights are on but all lights @ this intersection are Cycling - bad neturial underground - Traffic poles - shareing common ducts | High Pressure Sodium | 38.87660025000 | -76.99171847000
12/10/09 | 816027 | 1100 | 11TH ST | SE | 12/10/09 | 67613 | 6L941 | (Light out) | DA 12-10-09 @ 1115pm T. Richards repaired pole #67613 | High Pressure Sodium | 38.87665520000 | -76.99137008000
12/9/09 | 815959 | 0 | WISCONSIN AVE | NW | 12/10/09 | 30145 | 3G056 | (Light out) | DA 12-09-9 @ 1110pm K. Dunton repaired pole #30145 | High Pressure Sodium | 38.92250517000 | -77.07302857000
12/7/09 | 814145 | 100 | FLORIDA AVE | NE | 2/10/12 | 56987 | 5M122 | (Light out) | DA 12-08-09 @ 1227am K. Simmons pole #56987 - Traffic pole with t base damaged | High Pressure Sodium | 38.90908053000 | -77.00524436000
12/7/09 | 813983 | 4608 | NANNIE HELEN BURROUGHS AVE | NE | 12/8/09 | 71300DC | 7A234 | (Light out) | DA 12-07-09 @ 1048pm T. Richards repaired pole #71300dc | High Pressure Sodium | 38.89940450000 | -76.93569847000
12/7/09 | 813118 | 134 | L ST | NW | 12/7/09 | 61099 | 6S251 | (Light out) | DA 12-07-09 @ 300am K. Simmons repaired pole #61099 | High Pressure Sodium | 38.90367396000 | -77.01345330000
12/3/09 | 812094 | 1100 | 11TH ST | SE | 12/4/09 | 67613 | 6L941 | (Light out) | DA 12-04-09 @ 140am T. Richards pole #67613 light found on and working | High Pressure Sodium | 38.87665520000 | -76.99137008000
12/3/09 | 812088 | 1200 | 11TH ST | SE | 12/4/09 | 67740 | 6L938 | (Light out) | DA 12-04-09 @ 154am T. Richards pole #67740 light found on and working | High Pressure Sodium | 38.87633690000 | -76.99165150000
12/3/09 | 812013 | 4308 | NANNIE HELEN BURROUGHS AVE | NE | 12/7/09 | 71312DC | 7A246 | (Light out) | DA 12-07-09 @ 111am T. Richards repaired pole #71312dc | High Pressure Sodium | 38.90072786000 | -76.93937809000
12/2/09 | 811588 | 5516 | NANNIE HELEN BURROUGHS AVE | NE | 12/3/09 | 72651 | 7A184 | (Light out) | DA 12-02-09 @ 1102pm R. Warren repaired pole #72651 | High Pressure Sodium | 38.89830423000 | -76.92065348000
12/2/09 | 811352 | 0 | RHODE ISLAND AVE | NE | 12/4/09 | 50104 | 56340 | (Light off/on) | DA 12-04-09 @ 1255am K. Simmons repaired pole #50104dc | High Pressure Sodium | 38.91934333000 | -77.00215180000
12/2/09 | 811153 | 777 | 6TH ST | NE | 12/3/09 | 68454 | 6S588 | (Light out) | DA 12-03-09 @ 1205am T. Richards pole #68454 N/C Underground refer to wo #800332 | High Pressure Sodium | 38.89954137000 | -77.01979685000
12/2/09 | 810935 | 508 | MELLON ST | SE | 12/2/09 | 86496 | 8A358 | (Light out) | DA 12-02-09 @ 1246am K. Simmons repaired pole #86496 | High Pressure Sodium | 38.86233552000 | -77.00031519000
12/2/09 | 810933 | 0000 | OVERLOOK AVE | SE | 12/2/09 | 81806 | 85793 | (Light off/on) | DA 12-1-09 @ 1041pm T. Richards installed transformer pole #81806 | High Pressure Sodium | 38.82907587000 | -77.01730772000
12/1/09 | 810335 | 601 | KENNEDY ST | NW | 12/2/09 | 4M067 | 4M067DC | (Light out) | DA 12-02-09 @ 406am R. Warren repaired pole #4m067 | High Pressure Sodium | 38.95648496000 | -77.02110063000
11/30/09 | 810072 | 0 | SHERMAN AVE | NW | 12/1/09 | 12527 | 12503 | (Light out) | DA 11-30-09 @ 1145pm V. Cooke repaired pole #12527-Pole does have pole Tag | High Pressure Sodium | 38.92696258000 | -77.02586411000
11/30/09 | 809882 | 2022 | 14TH ST | SE | 12/1/09 | 80525 | 80525DC | (Light out) | DA 11-30-09 @ 1118pm . Simmons repaired pole #80525 | High Pressure Sodium | 38.86531307000 | -76.98537942000
11/30/09 | 809302 | 0 | NEW HAMPSHIRE AVE | NW | 12/1/09 | 28346 | 2G683 | (Light out) | DA 12-01-09 @ 210am V. Cooke repaired pole #28346 | High Pressure Sodium | 38.90205645000 | -77.05068674000
11/30/09 | 809280 | 2914 | SHERMAN AVE | NW | 12/1/09 | 12529 | 12534 | (Light out) | DA 11-30-09 @ 1155pm V. Cooke repaired pole #12529 Front 09-03154019- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.92730578000 | -77.02611400000
11/25/09 | 808548 | 2218 | WISCONSIN AVE | NW | 12/1/09 | 30161 | 3G086 | (Light out) | DA 12-01-09 @ 335am K. Dunton repaired pole #30161 | High Pressure Sodium | 38.91961236000 | -77.07085524000
11/21/09 | 806359 | 3960 | PENNSYLVANIA AVE | SE | 11/25/09 | 78580DC | 7E006DC | (Light out) | DA 11-25-09 @ 1241am T. Richards repaired pole #78580dc DA 11-23-009 @ 1149pm K. Simmons installed 250hps lamp still needs repair (rain) Front 09-03148315-wooden pole streetlight is out cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86466564000 | -76.94882256000
11/19/09 | 805713 | 0 | H ST | NE | 11/23/09 | 62350 | 6S120 | (Light out) | DA 11-23-09 @ 345am T. Richards pole #62350 refer to wo #782807 | High Pressure Sodium | 38.90011633000 | -76.98846372000
11/19/09 | 805709 | 0 | WASHINGTON AVE | SW | 11/23/09 | 21662 | 6A381 | (Light out) | DA 11-22-09 @ 1125pm V. Cooke repaired pole #21662 | High Pressure Sodium | 38.88686324000 | -77.01343008000
11/19/09 | 805705 | 601 | 4TH ST | NW |  | 60437 | 6P013 | (Light out) | DA 11-22-09 @ 1125pm T. Richards pole #60437 - could not extend bucket far enough to reach light construction in area _ Phelps Consrution Co. | High Pressure Sodium | 38.89517291000 | -77.01624618000
11/19/09 | 805342 | 300 | EASTERN AVE | NE | 4/12/11 | 70026 | 72855 | (Light out) | DA 11-19-09 Two lights @ location with the same pole #70026 - 400hps cut off on and working, the teardrop fixture is defective and needs repair | High Pressure Sodium | 38.89394625000 | -76.91101330000
11/19/09 | 805233 | 1225 | 18TH ST | NW | 11/23/09 | 26764 | 2U516 | (Light out) | DA 11-23-09 @ 250am V, Cooke repaired pole #26764 North Bound 09-03145332-Street pole light is out, it's blink off and on cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90679324000 | -77.04161488000
11/18/09 | 805183 | 388 | H ST | NE | 2/6/12 | 61522 | 6S224 | (Light out) | DA 11-23-09 @ 321am T. Richards pole #61522 is a temp pole Near the bus stop, west side of street, right next to alley. 09-03145251- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90030233000 | -77.00072209000
11/16/09 | 803367 | 1411 | MONROE ST | NE | 11/17/09 | 51216DC | 5A106DC | (Light out) | DA 1-17-09 @ 1216am K. Simmons repaired pole #51216dc Front 09-03142131- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93277123000 | -76.98556571000
11/16/09 | 803177 | 1416 | BELMONT ST | NW | 11/17/09 | 12051 | 1A043 | (Light out) | DA 11-17-09-@ 330am K. Simmons repaired pole #12051 | High Pressure Sodium | 38.92062514000 | -77.03244172000
11/16/09 | 802404 | 1200 | 11TH ST | SE | 11/16/09 | 67740 | 6L938 | (Light out) | DA 11-16-09 @ 343am T. Richards repaired pole #67740 reset TLPC | High Pressure Sodium | 38.87633690000 | -76.99165150000
11/16/09 | 802403 | 1000 | M ST | SE | 11/16/09 | 67376 | 6L940 | (Light out) | DA 11-16-09 @ 333am T. Richards repaired pole #67376 reset TLPC | High Pressure Sodium | 38.87660025000 | -76.99171847000
11/15/09 | 802331 | 1209 | U ST | NW | 11/18/09 | 13284 | 1G534 | (Light out) | DA 11-18-09 @ 1229am K. Simmons repaired pole #13284 | High Pressure Sodium | 38.91691923000 | -77.02846873000
11/15/09 | 802328 | 1673 | PARK RD | NW | 11/20/09 | 10108 | 1G338 | (Light out) | DA 11-19-09 @ 200am K. Simmons could not locate | High Pressure Sodium | 38.93247114000 | -77.03842826000
11/15/09 | 802327 | 1500 | PARK RD | NW | 11/20/09 | 12959 | 1G362 | (Light out) | DA 11-19-09 @ 150am K. Simmons could not locate | High Pressure Sodium | 38.93151986000 | -77.03595981000
11/15/09 | 802326 | 3200 | KENYON PL | NW | 2/6/12 | 14683 | 1G052 | (Light out) | DA 11-17-09 @ 301am K. Simmons pole #14683 N/C underground | High Pressure Sodium | 38.93003166000 | -77.03236323000
11/15/09 | 802325 | 3030 | 14TH ST | NW |  | 15022 | 1G010 | (Light out) | DA 11-17-09 @ 319am K. Simmons pole #15022 refer to ddot defective 250 teardrop fixture | High Pressure Sodium | 38.92847462000 | -77.03272597000
11/12/09 | 801699 | 2 | MASSACHUSETTS AVE | NE | 11/12/09 | 60928 | 6U602 | (Light out) | DA 11-12-09 @ 1017pm T. Richards repaired pole #60928 - reconnected loose harrness | High Pressure Sodium | 38.89801466000 | -77.00755371000
11/12/09 | 801633 | 1300 | 1ST ST | NE | 11/12/09 | 61247 | 6A279 | (Light out) | DA 11-12-09 @ 1045pm T. Richards pole #61247 light on and in working condition Front 09-03139038-caller req. that the base of the light is corroded cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90758804000 | -77.00596758000
11/10/09 | 800332 | 777 | 6TH ST | NE | 2/6/12 | 68454 | 6S588 | (Light out) | DA 11-12-09 @ 110am T. Richards pole #68454 N/C underground - recent work order has been closed | High Pressure Sodium | 38.89954137000 | -77.01979685000
11/10/09 | 800168 | 627 | I ST | NW | 11/12/09 | 22475 | 2M309 | (Light out) | DA 11-12-09 @ 200am V. Cooke pole #22475 light is not cycling - light is on and working THE 600 BLOCK OF I ST N.W. | High Pressure Sodium | 38.90094324000 | -77.02098771000
11/10/09 | 800151 | 0 | SHERMAN AVE | NW | 11/11/09 | 12586 | 1G459 | (Light out) | DA 11-11-09 @ 1039pm V. Cooke repaired pole #12586 | High Pressure Sodium | 38.92223537000 | -77.02543083000
11/10/09 | 800150 | 0 | SHERMAN AVE | NW | 11/13/09 | 12527 | 12503 | (Light out) | CP - 11/13 - K Greenfield DA 11-11-09 @ 1026pm V. Cooke pole #12527 N/C underground | High Pressure Sodium | 38.92696258000 | -77.02586411000
11/10/09 | 800110 | 1701 | M ST | NW | 11/10/09 | 26411 | 2U750 | (Light out) | Da 11-10-09 @ 235am V. Cooke repaired pole #26411 | High Pressure Sodium | 38.90572284000 | -77.03887684000
11/9/09 | 800065 | 2655 | FIRTH STERLING AVE | SE | 11/9/09 | 81553DC | 8M073 | (Light out) | DA 11-09-09 @ 1125pm K. Simmons repaired pole #81553dc | High Pressure Sodium | 38.86105336000 | -77.00133681000
11/8/09 | 799335 | 300 | EASTERN AVE | NE | 11/10/09 | 70026 | 72855 | (Light out) | DA 11-10-09 @ 224am T. Richards repaired pole #70026 | High Pressure Sodium | 38.89394625000 | -76.91101330000
11/8/09 | 799332 | 5516 | NANNIE HELEN BURROUGHS AVE | NE | 11/10/09 | 72651 | 7A184 | (Light out) | DA 11-10-09 @ 123am Refer to wo 758761 | High Pressure Sodium | 38.89830423000 | -76.92065348000
| 799183 | 0 | 18TH ST | NW | 11/9/09 | 24534 | 2U529 | (Light out) | DA 11-09-09 @ 320am V. Cooke repaired pole #24534 SW Corner 09-03134319-street light is blinking cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90591907000 | -77.04143681000
11/4/09 | 798030 | 5920 | GEORGIA AVE | NW | 11/6/09 | 4E219 | 4A824 | (Light out) | DA 11-06-09 @ 114am R. Warren repaird pole #4e219 unk 09-03130971-METAL POLE cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.96170865000 | -77.02785877000
11/4/09 | 797437 | 0 | SEATON ST | NW | 2/6/12 | 11451 | 1A100 | (Light out) | SE Corner 09-03129684-The light does not need to be repaired. It has been located 4-5ft from my bedroom window. I would like if some type of reflective element could be put on the light casing so the light does not flood my room during the evening cwDesc | High Pressure Sodium | 38.91753869000 | -77.04044580000
11/3/09 | 797284 | 1423 | 36TH ST | NW | 11/5/09 | 21000 | 2G201 | (Light out) | DA 11-05-09 @ 125am V. Cooke repaired pole #21000 Front 09-03129113- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90835025000 | -77.07043482000
11/3/09 | 796695 | 300 | EASTERN AVE | NE | 11/4/09 | 70026 | 72855 | (Light out) | DA 11-04-09 @ 333am T. Richards redirected photocell pole #70026 | High Pressure Sodium | 38.89394625000 | -76.91101330000
11/2/09 | 796558 | 0 | NEW YORK AVE | NE | 11/2/09 | 50005 | 5A039 | (Light out) | DA 11-02-09 @ 1052pm T. Ricards repaired pole #50005 | High Pressure Sodium | 38.91734425000 | -76.96859446000
11/2/09 | 796557 | 0 | NEW YORK AVE | NE | 11/2/09 | 50008 | 5A042 | (Light out) | DA 11-02-09 @ 1042pm T. Richards repaired pole #50008 | High Pressure Sodium | 38.91724347000 | -76.96648514000
11/2/09 | 796553 | 0 | NEW YORK AVE | NE | 11/2/09 | 50011 | 5A045 | (Light out) | DA 11-02-09 @ 1032pm T. Richards repaired pole #50011 | High Pressure Sodium | 38.91707776000 | -76.96424700000
11/2/09 | 796519 | 1217 | CONNECTICUT AVE | NW | 11/3/09 | 27223 | 2U520 | (Light out) | DA 11-003-09 @ 1215am V. Cooke repaired pole #27223 Front 09-03126816- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90639779000 | -77.04139143000
11/2/09 | 796241 | 4612 | 12TH ST | NE | 11/3/09 | 51256DC | 5A150DC | (Light out) | DA 11-03-09 @ 1222am K.Simmons repaired pole #51256dc | High Pressure Sodium | 38.94542966000 | -76.99072288000
11/2/09 | 795740 | 0 | EASTERN AVE | NE | 11/2/09 | 52382DC | 5L703 | (Light out) | DA 11-02-09 @ 425am K. Simmons repaired pole #52382dc | High Pressure Sodium | 38.93906027000 | -76.96826153000
11/2/09 | 795735 | 0000 | DAVENPORT ST | NW | 11/2/09 | 30009DC | 3A246DC | (Light out) | DA 11-02-09 @ 315am K. Dunton repaired pole #30009dc | Mercury Vapor | 38.95206814000 | -77.08071551000
10/30/09 | 795017 | 0 | KENILWORTH AVE | NE | 10/30/09 | 79463 | 7A127 | (Light out) | DA 10-30-09 @ 246am T. Richards repaired pole #79463 | High Pressure Sodium | 38.88994563000 | -76.95813630000
10/30/09 | 795002 | 0000 | OVERLOOK AVE | SE | 11/3/09 | 81806 | 85793 | (Light out) | DA 10-30-09 @ 1202am pole #81806 Needs Transformer | High Pressure Sodium | 38.82907587000 | -77.01730772000
10/29/09 | 794982 | 0000 | BLADENSBURG RD | NE | 11/15/09 | 50091 | 5M218 | (Light out) | DA 10-30-09 @ 427am R. Warren repaired could not read pole tag 11-4-09 S.Manning---already tagged also needs tree trim cannot see tag with all the vines (sc) | High Pressure Sodium | 38.92522195000 | -76.96493267000
10/29/09 | 794854 | 3418 | O ST | NW | 11/2/09 | 21098 | 2G164 | (Light off/on) | DA 11-02-09 @ 210am V. Cooke repaired pole #21098 | High Pressure Sodium | 38.90770216000 | -77.06850706000
10/29/09 | 794104 | 1209 | U ST | NW | 10/30/09 | 13284 | 1G534 | (Light out) | 10-30-09 I Paraway/Barclay no action taken | High Pressure Sodium | 38.91691923000 | -77.02846873000
10/28/09 | 794058 | 1800 | Q ST | NW | 10/29/09 | 26293 | 2M148 | (Light out) | DA 10-28-09 @ 1115pm V. Cooke repaired pole #26293 Front 09-03119643- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91118563000 | -77.04218793000
10/28/09 | 793702 | 1765 | NEW YORK AVE | NE | 10/29/09 | 50060 | 5A051 | (Light out) | DA 10-29-09 @ 125am K. Simmons repaired ple #50060 | High Pressure Sodium | 38.91711198000 | -76.97897966000
10/27/09 | 792890 | 1016 | 3RD ST | SW | 10/29/09 | 68142 | 6A466 | (Light out) | DA 10-29-09 @ 203am T. Richards repaired pole #68142 East Side 09-03117573- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.87797923000 | -77.00197859000
10/27/09 | 792883 | 0 | FLORIDA AVE | NE | 10/30/09 | 62313 | 5M114 | (Light out) | DA 10-27-09 @ 1015pm T. Richards pole #62313 N/C underground REPEAT | High Pressure Sodium | 38.90860897000 | -77.00417478000
10/27/09 | 792735 | 2336 | WISCONSIN AVE | NW | 10/29/09 | 30149 | 3G073 | (Light out) | 2334 Wisconsin Ave 09-03117009-metal cover at base of pole is not properly secured - exposing wires to weather and kids cwDesc: STREETLIGHT REPAIR 10-29-09 A.Purnell---repaired (sc) | High Pressure Sodium | 38.92085423000 | -77.07199482000
| 792736 | 2336 | WISCONSIN AVE | NW | 10/29/09 | 30149 | 3G073 | (Light out) | 2334 Wisconsin Ave 09-03117007-metal cover at base of pole is not properly secured - exposing wires to weather and kids cwDesc: STREETLIGHT REPAIR 10-29-09 A.Purnell---repaired (sc) | High Pressure Sodium | 38.92085423000 | -77.07199482000
10/27/09 | 792060 | 200 | K ST | NE | 12/10/09 | 61351 | 6B087 | (Light out) | NCSC - H Lancaster - 10/29 DA 10-27-09 @ 1033pm T. Richards pole #61351 (NE Corner) N/C underground na 09-03115590-1000 BLOCK OF 3RD STREET NE...NE CORNER.. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90302176000 | -77.00210340000
10/27/09 | 792025 | 200 | K ST | NE | 10/27/09 | 61351 | 6B087 | (Light out) | DA 10-27-09 @ 1033pm T. Richards pole #61351 (NWCorner) light is on and working | High Pressure Sodium | 38.90302176000 | -77.00210340000
10/26/09 | 791775 | 1000 | HALF ST | SE | 10/28/09 | 67437 | 6B103 | (Light out) | DA 10-28-09 @ 244am T. Richards redirected photocell pole #67437 | High Pressure Sodium | 38.87769232000 | -77.00752782000
10/26/09 | 791756 | 1016 | 3RD ST | SW | 10/27/09 | 68142 | 6A466 | (Light out) | DA 10-27-09 @ 258am T. Richards all lights found on and working | High Pressure Sodium | 38.87797923000 | -77.00197859000
10/26/09 | 791755 | 900 | 4TH ST | SE | 2/6/12 | 67538 | 6B424 | (Light out) | DA 10-28-09 T. Richards pole #67538 -N/C Underground - new development / Capitol Corners Phone # (202)484-0360 | High Pressure Sodium | 38.87880040000 | -77.00050803000
10/26/09 | 791754 | 900 | 4TH ST | SE | 2/6/12 | 67541 | 6B425 | (Light out) | DA 10-28-09 T. Richards pole #67541 -N/C Underground - new development / Capitol Corners Phone # (202)484-0360 | High Pressure Sodium | 38.87860117000 | -77.00051529000
10/26/09 | 791752 | 1000 | M ST | SE | 10/28/09 | 67376 | 6L940 | (Light out) | DA 10-28-09 @ 137am T. Richards repaired pole #67376 | High Pressure Sodium | 38.87660025000 | -76.99171847000
10/26/09 | 791738 | 1200 | 11TH ST | SE | 10/28/09 | 67740 | 6L938 | (Light out) | DA 10-28-09 @ 103am T. Richards repaired pole #67740 | High Pressure Sodium | 38.87633690000 | -76.99165150000
10/26/09 | 791689 | 1100 | 1ST ST | NE | 10/26/09 | 61235 | 6S233 | (Light out) | DA 10-26-09 @ 1128pm T. Richards repaired pole #61235 | High Pressure Sodium | 38.90411117000 | -77.00597136000
10/25/09 | 791032 | 5335 | B ST | SE | 10/26/09 | 75564 | 75564DC | (Light out) | 10-26-09 M Brewer installed 150w hps flat lens DA 10-25-09 @ 1036pm T. Richards repaired pole #75564 needs lens | High Pressure Sodium | 38.88622800000 | -76.92459483000
10/25/09 | 791027 | 0 | 18TH ST | NW | 10/26/09 | 11502 | 1G477 | (Light off/on) | DA 10-26-09 @ 245am T. Richards repaired pole #11502 | High Pressure Sodium | 38.92245024000 | -77.04270127000
10/25/09 | 791026 | 2038 | 18TH ST | NW | 10/26/09 | 11414 | 1G510 | (Light off/on) | DA 10-25-09 @ 1157pm R. Warren repaired pole #11414 | High Pressure Sodium | 38.91777981000 | -77.04149864000
10/22/09 | 789910 | 4644 | EASY PL | SE | 10/23/09 | 75823 | 75823DC | (Light out) | DA 10-23-09 @ 332am T. Richards repaired pole #75823 | Incandescent | 38.87603394000 | -76.93184557000
10/22/09 | 789887 | 2611 | POMEROY RD | SE | 10/23/09 | 81349DC | 8U662 | (Light out) | DA 10-23-09 @ 1200am K. Simmons repaired pole #81349dc | High Pressure Sodium | 38.85564643000 | -76.99229526000
10/22/09 | 789167 | 0 | 23RD ST | NW | 10/29/09 | 28318 | 2M274 | (Light out) | DA 10-21-09 @ 1135pm V. Cooke repaired pole tag missing 10-28-09 S.Manning---install tag (sc) | High Pressure Sodium | 38.89313901000 | -77.05025238000
10/21/09 | 789099 | 0 | WASHINGTON AVE | SW | 10/22/09 | 21662 | 6A381 | (Light out) |  | High Pressure Sodium | 38.88686324000 | -77.01343008000
10/20/09 | 787784 | 0 | SHERMAN AVE | NW | 10/21/09 | 12587 | 1G451 | (Light out) | wblack-n/c was completed and light is now on | High Pressure Sodium | 38.92300485000 | -77.02549655000
10/20/09 | 787667 | 0 | NEW YORK AVE | NE | 10/21/09 | 61252 | 5M104 | (Light out) | DA 10-20-09 @ 1109pm T. Richards redirected photocell pole #61252 | High Pressure Sodium | 38.90823571000 | -77.00619583000
10/20/09 | 787664 | 1400 | FLORIDA AVE | NE | 2/6/12 | 54410 | 5M289 | (Light out) | DA 10-20-09 @ 1126pm K. Simmons pole #54410 still N/C underground H. Lancaster on 10/21/09 Pole was just serviced for a no current on 10/3/2009 | High Pressure Sodium | 38.90051673000 | -76.98498235000
10/20/09 | 787663 | 1400 | FLORIDA AVE | NE | 4/16/12 | 54409 | 5M287 | (Light out) | DA 10-20-09 @ 1118pm K. Simmons pole #54409 still N/C underground Pole was just serviced for a no current on 10/3/2009 | High Pressure Sodium | 38.90038000000 | -76.98467707000
10/19/09 | 786810 | 0 | WASHINGTON AVE | SW | 10/20/09 | 21662 | 6A381 | (Light out) | DA 10-20-09 @ 200am V. Cooke repaired pole #21662 | High Pressure Sodium | 38.88686324000 | -77.01343008000
10/18/09 | 786065 | 0 | SHERMAN AVE | NW | 10/20/09 | 12587 | 1G451 | (Light out) | DA 10-18-09 @ 1140pm V. Cooke pole #12587 N/C underground | High Pressure Sodium | 38.92300485000 | -77.02549655000
10/18/09 | 786058 | 200 | K ST | NE | 10/18/09 | 61351 | 6B087 | (Light out) | DA 10-18-09 @ 1026pm T. Richards repaired loose connection in T Base ( 1 split bolt and electrical tape ) | High Pressure Sodium | 38.90302176000 | -77.00210340000
10/16/09 | 785619 | 900 | U ST | NW | 10/18/09 | 13983 | 1G551 | (Light out) | DA 10-18-09 @ 1000pm V. Cooke repaired pole #13983 | High Pressure Sodium | 38.91713116000 | -77.02591861000
10/16/09 | 785617 | 1209 | U ST | NW | 10/18/09 | 13284 | 1G534 | (Light out) | DA 10-18-09 @ 1040pm V. Cooke repaired pole #13284 | High Pressure Sodium | 38.91691923000 | -77.02846873000
10/16/09 | 785297 | 3408 | WISCONSIN AVE | NW | 10/20/09 | 38772 | 3U402 | (Light out) | DA 10-19-09 @ 1050pm K. Dunton adjusted TLPC | High Pressure Sodium | 38.93510623000 | -77.07282513000
10/16/09 | 785279 | 3850 | GEORGIA AVE | NW | 4/21/10 | 4J355 | 4G260 | (Light out) | 10-16-09 D.Dixon---no current to underground (sc) | High Pressure Sodium | 38.93855929000 | -77.02474527000
10/16/09 | 785261 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 10/21/09 | 72645 | 7S073 | (Light out) | DA 10-16-09 @ 300am T. Richards pole #72645 N/Cunderground | High Pressure Sodium | 38.89826452000 | -76.92554310000
10/16/09 | 785260 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 10/21/09 | 71269 | 7A201 | (Light out) | DA 10-16-09 @ 250am T. Richards pole #71269 N/C underground | High Pressure Sodium | 38.89826963000 | -76.92624974000
10/16/09 | 785259 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 10/21/09 | 71270 | 71270DC | (Light out) | DA 10-16-09 @ 243am T. Richards pole #71270 N/C underground | High Pressure Sodium | 38.89827347000 | -76.92679095000
10/14/09 | 784399 | 0 | EAST CAPITOL ST | NE | 10/15/09 | 73560 | 73560DC | (Light out) | DA 10-15-09 @ 156am T. Richards repaired pole #73560 | High Pressure Sodium | 38.88963991000 | -76.91490257000
10/14/09 | 784397 | 5800 | NANNIE HELEN BURROUGHS AVE | NE | 10/15/09 | 79661 | 72656 | (Light out) | DA 10-15-09 @ 112am T. Richards pole #79661 light found on and working | High Pressure Sodium | 38.89830700000 | -76.91763472000
10/13/09 | 783780 | 3408 | WISCONSIN AVE | NW | 10/14/09 | 38772 | 3U402 | (Light out) |  | High Pressure Sodium | 38.93510623000 | -77.07282513000
10/13/09 | 783762 | 1129 | NEW HAMPSHIRE AVE | NW | 10/14/09 | 23867 | 2G717 | (Light out) | DA 10-13-09 @ 1056pm V. Cooke repaired pole #23867 | High Pressure Sodium | 38.90496279000 | -77.04772094000
10/11/09 | 782841 | 0 | NEW YORK AVE | NE | 10/13/09 | 56790 | 5M031 | (Light out) |  | High Pressure Sodium | 38.91355367000 | -76.99280870000
10/10/09 | 782806 | 0 | H ST | NE | 2/6/12 | 62350 | 6S120 | (Light out) | DA 10-11-09 @ 1036pm T. Richards pole #62350 N/C underground corner 09-03089930-Streetlight need to be repair metal pole cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90011633000 | -76.98846372000
| 782807 | 0 | H ST | NE | 2/6/12 | 62350 | 6S120 | (Light out) | DA 10-11-09 @ 1036pm T. Richards pole #62350 N/C underground Front 09-03089931-streetlight pole need to be repair. metal pole cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90011633000 | -76.98846372000
10/9/09 | 782568 | 3209 | ALABAMA AVE | SE | 10/12/09 | 74836DC | 7A100DC | (Light out) | DA 10-12+-09 @ 245am T. Richards repaired pole #74836dc Front 09-03089434-WOOD POLE. LIGHT IS ON AND OFF, THIS IS THE SECOND CALL. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.86132638000 | -76.96088830000
10/9/09 | 782310 | 3429 | 14TH ST | NW | 10/12/09 | 13804 | 1G082 | (Light out) | DA 10-11-09 @ 1145pm V. Cooke repaired pole #13804 na 09-03088598-Caller reporting streetlight on a metal pole is on all the time and needs to be inspected asap. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.93260036000 | -77.03283470000
10/7/09 | 780792 | 777 | H ST | NE | 10/8/09 | 61993 | 6S193 | (Light out) | DA 10-08-09 @ 1057pm T. Richards repaired pole #61993 | High Pressure Sodium | 38.90029929000 | -76.99512291000
10/7/09 | 780186 | 0 | SOUTH CAPITOL ST | SE | 10/8/09 | 82044 | 8M062 | (Light out) | DA 10-08-09 @ 309am T. Richards pole #82044 light found on and working | High Pressure Sodium | 38.86042806000 | -77.00347620000
10/7/09 | 780149 | 1000 | HALF ST | SE | 10/9/09 | 67437 | 6B103 | (Light out) | DA 10-09-09 @ 309am T. Richards repaired pole #67437 - redirected photocell | High Pressure Sodium | 38.87769232000 | -77.00752782000
10/6/09 | 779251 | 1300 | MAINE AVE | SW | 10/6/09 | 66532 | 6M444 | (Light out) | DA 10-06-09 @ 202am T, Richards repaired pole #66532 - needs ears | High Pressure Sodium | 38.88170964000 | -77.02793900000
10/6/09 | 779250 | 0 | MAINE AVE | SW | 10/6/09 | 28714 | 6M440 | (Light out) | DA 10-06-09 @ 148am T. Richards repaired pole #28714 | High Pressure Sodium | 38.88228166000 | -77.02954169000
10/5/09 | 779022 | 2319 | PENNSYLVANIA AVE | NW | 10/6/09 | 24653 | 2G667 | (Light out) | DA 10-06-09 @ 205am V. Cooke light found on and working Front 09-03079870-metal pole cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90301348000 | -77.05112594000
10/5/09 | 778299 | 2311 | 18TH ST | NW | 10/8/09 | 11409 | 1G496 | (Light out) | DA 10-06-09 @ 226am R, Warren ran 100ft wire refer to fault crew | High Pressure Sodium | 38.92009844000 | -77.04170982000
10/5/09 | 778296 | 2319 | PENNSYLVANIA AVE | NW | 10/6/09 | 24653 | 2G667 | (Light out) | DA 10-06-09 @ 1255am V. Cooke repaired ole #24653 | High Pressure Sodium | 38.90301348000 | -77.05112594000
10/5/09 | 778286 | 100 | 3RD ST | SE | 10/5/09 | 6A002 | 6A002 | (Light out) | DA 10-05-09 @ 252am T. Richards repaired pole #6a002 tightened loose 150lamp | Incandescent | 38.87703665000 | -77.00445216000
10/1/09 | 777046 | 0 | NEW YORK AVE | NW | 10/6/09 | 22911 | 2L053 | (Light out) | DA 10-06-09 @ 345am V/ Cooke repaired pole #22911 | High Pressure Sodium | 38.90141042000 | -77.02582476000
10/1/09 | 777026 | 1222 | 1ST ST | NE | 10/5/09 | 61244 | 6A275 | (Light out) | DA 10-04-09 @ 1010pm T. Richards repaired pole #61244 (rubber and black tape, scotch kote) | High Pressure Sodium | 38.90676525000 | -77.00596728000
10/1/09 | 776946 | 3850 | GEORGIA AVE | NW |  | 4J355 | 4G260 | (Light out) | DA 10-02-09 @ 202am R. Warren pole #4j355 N/C underground | High Pressure Sodium | 38.93855929000 | -77.02474527000
9/30/09 | 775701 | 444 | 7TH ST | NW | 9/30/09 | 60649 | 6M624 | (Light out) | DA 9-30-09 @ 149am T. Richards repaired pole #60649 - east side | High Pressure Sodium | 38.89571105000 | -77.02201326000
9/29/09 | 775475 | 1400 | FLORIDA AVE | NE | 10/3/09 | 54408 | 5M281 | (Light out) | DA 9-30-09 @ 123am K. Simmons pole #54408 N/C underground | High Pressure Sodium | 38.90042110000 | -76.98451944000
9/29/09 | 775474 | 1400 | FLORIDA AVE | NE | 10/3/09 | 54409 | 5M287 | (Light out) | DA 9-30-09 @ 1235am K. Simmons pole #54409 N/C underground | High Pressure Sodium | 38.90038000000 | -76.98467707000
9/29/09 | 775473 | 1400 | FLORIDA AVE | NE | 10/3/09 | 54410 | 5M289 | (Light out) | DA 9-30-09 @ 1235am K. Simmons pole #54410 N/C underground | High Pressure Sodium | 38.90051673000 | -76.98498235000
9/29/09 | 775472 | 0 | BENNING RD | NE | 9/29/09 | 59545 | 5M229 | (Light out) |  | High Pressure Sodium | 38.90020801000 | -76.98298142000
9/29/09 | 775471 | 0 | BENNING RD | NE | 9/29/09 | 59599 | 5M220 | (Light out) | CLOSED NO ACTION. SEE WO# 733633. | High Pressure Sodium | 38.89996191000 | -76.98156127000
9/29/09 | 775445 | 0 | WESTMORELAND CIR | NW | 9/30/09 | 34382 | 3M040 | (Light out) | DA 9-29-09 @ 1040pm K. Dunton pole #34382 N/C underground | Mercury Vapor | 38.94886883000 | -77.10158329000
9/29/09 | 775444 | 0 | WESTMORELAND CIR | NW | 9/30/09 | 34383 | 3M033 | (Light out) | DA 9-29-09 @ 1110pm K. Dunton pole #34383- pole has been removed | High Pressure Sodium | 38.94846544000 | -77.10111316000
9/29/09 | 775183 | 0 | EAST CAPITOL ST | NE | 2/10/12 | 74205DC | 7A063DC | (Light out) | DA 10-01-09 @ 1232am T. Richards pole #74205dc - N/C underground traffic pole Benning Road & East Capital Street 09-03068406- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89216210000 | -76.94254713000
9/28/09 | 774290 | 4246 | LANE PL | NE |  | 70320 | 7M076 | (Light out) | DA 9-30-09 @ 1249am T Richards pole #70320 this is temp pole refer to ddot | High Pressure Sodium | 38.90452719000 | -76.94154286000
9/27/09 | 773925 | 200 | K ST | NE | 9/30/09 | 61351 | 6B087 | (Light out) | DA 930-09 @ 109am T, Richards pole #61351 N/C underground | High Pressure Sodium | 38.90302176000 | -77.00210340000
9/27/09 | 773924 | 0 | FLORIDA AVE | NE | 9/30/09 | 62313 | 5M114 | (Light out) | DA 9-30-09 @ 133am T. Richards pole #62313 light found on and working | High Pressure Sodium | 38.90860897000 | -77.00417478000
9/27/09 | 773911 | 601 | 4TH ST | NW | 9/30/09 | 60437 | 6P013 | (Light out) | DA 9-30-09 Open ticket refered to ddot - refer to wo #764272 | High Pressure Sodium | 38.89517291000 | -77.01624618000
9/27/09 | 773908 | 444 | 7TH ST | NW | 9/30/09 | 60649 | 6M624 | (Light out) | DA 9-30-09 @ 149am T. Richards repaired pole #60649 | High Pressure Sodium | 38.89571105000 | -77.02201326000
9/24/09 | 772743 | 0 | 18TH ST | NW | 9/30/09 | 11502 | 1G477 | (Light off/on) | 9-29-09 D.Webb---install tag//light foundok no action needed (sc) | High Pressure Sodium | 38.92245024000 | -77.04270127000
9/22/09 | 770789 | 200 | L ST | SE | 10/20/09 | 67695 | 6A414 | (Light out) | 10-20-09 M.Craig---repaired (sc) | Incandescent | 38.87766628000 | -77.00287950000
9/22/09 | 770345 | 900 | UPSHUR ST | NW | 9/23/09 | 4J744 | 4G330 | (Light out) | DA 9-22-09 @ 1104pm R. Warren pole #4j744 N/C underground | High Pressure Sodium | 38.94182164000 | -77.02494834000
9/22/09 | 769968 | 3307 | O ST | NW | 9/24/09 | 21105 | 2G169 | (Light out) | (9-24-09 M Brewer inst pc and drilled holes) DA 9-24-09 @ 400am V. Cooke repaired pole #21105 - needs hole drilled for photocell | High Pressure Sodium | 38.90785307000 | -77.06621385000
9/22/09 | 769967 | 3525 | O ST | NW | 9/24/09 | 21095 | 2G156 | (Light out) | DA 9-24-09 @ 1125pm V. Cooke repaired pole #21095 (9-24-09 I Paraway/Barclay need 150w hps kit)) 9-24-09 D.Dixon---need new 150hps kit (sc) | High Pressure Sodium | 38.90766972000 | -77.07002828000
9/21/09 | 769940 | 0 | MORSE ST | NE | 9/21/09 | 59547 | 5M234 | (Light out) | DA 9-21-09 @ 1120pm K. Simmons repaired pole #59547 | High Pressure Sodium | 38.90050216000 | -76.98268829000
9/21/09 | 769648 | 0 | BENNING RD | NE |  | 59545 | 5M229 | (Light out) | DA 9-21-09 @ 1105pm K. Simmons pole #59545 N/C underground | High Pressure Sodium | 38.90020801000 | -76.98298142000
9/21/09 | 769647 | 0 | BENNING RD | NE |  | 59597 | 5M275 | (Light out) | DA 9-21-09 @ 1055pm K. simmons pole #59597 N/C underground | High Pressure Sodium | 38.90028965000 | -76.98347853000
9/21/09 | 769626 | 0 | WASHINGTON CIR | NW | 9/24/09 | 24803 | 2G686 | (Light out) | 9-24-09 I.Paraway---repaired (sc) | High Pressure Sodium | 38.90250780000 | -77.05091312000
9/20/09 | 768994 | 0 | WESTMORELAND CIR | NW | 9/23/09 | 34384 | 3M034 | (Light out) | DA 9-23-09 @ 1250am K. Dunton repaired pole #34384 | High Pressure Sodium | 38.94850754000 | -77.10070565000
9/20/09 | 768993 | 0 | WESTMORELAND CIR | NW | 9/28/09 | 34381 | 3M039 | (Light out) | (9-22-09 M Brewer MV need to be converted over REFER to DDOT) | Incandescent | 38.94928386000 | -77.10138540000
9/20/09 | 768983 | 0 | WISCONSIN AVE | NW | 9/22/09 | 3A061DC | 3A061 | (Light out) | DA 9-22-09 2 140am K. dunton repaired pole #3a061dc | High Pressure Sodium | 38.94998940000 | -77.08058258000
9/20/09 | 768975 | 1801 | WILTBERGER ST | NW | 9/21/09 | 29505 | 1M018 | (Light out) | DA 9-21-09 @ 105am V. Cooke repaired pole #29505 | High Pressure Sodium | 38.91425550000 | -77.02092154000
9/20/09 | 768974 | 1835 | WILTBERGER ST | NW | 9/21/09 | 29508 | 1M012 | (Light off/on) | DA 9-21-9 @ 111am V. Cooke repaired pole #29508 | High Pressure Sodium | 38.91528456000 | -77.02091849000
9/20/09 | 768973 | 635 | T ST | NW | 9/21/09 | 14389 | 1M006 | (Light off/on) | DA 9-21-09 @ 404am R, Warren repaired pole #14389 | High Pressure Sodium | 38.91563319000 | -77.02130285000
9/17/09 | 768062 | 1025 | 4TH ST | NW | 11/20/09 | 60456 | 6S480 | (Light out) | (9-30-09 A Johnson/Fike inst 15" TBase 100% complete) DA 9-17-09 @ 1121pm T. Richards repaired pole #60456 | High Pressure Sodium | 38.90380410000 | -77.01611081000
9/17/09 | 768058 | 3943 | PENNSYLVANIA AVE | SE | 9/29/09 | 78579DC | 7E003DC | (Light off/on) | DA 9-18-09 @ 1236am T. Richards repaired pole #78579dc - Needs major tree trimming | High Pressure Sodium | 38.86417025000 | -76.94760339000
9/16/09 | 767013 | 0 | NEW YORK AVE | NE | 10/12/09 | 61252 | 5M104 | (Light out) | 10-2-09 G Edwards - inst 40' pole, 2-400hps fix, 2-8' arm, 2- TLP, 120' #10 wire need pole tag) (10-1-09 GEdwards - Removed 28' pole, 15"TBase, 8' arm,250hps fix new foundation needed) (9-29-09 G Edwards SEE BELOW COMMENTS) Front 09-03043222-corod | High Pressure Sodium | 38.90823571000 | -77.00619583000
9/16/09 | 766142 | 777 | NORTH CAPITOL ST | NE | 9/17/09 | 68241DC | 68241 | (Light out) | DA 9-15-09 @ 1043pm T. Richards pole #68241dc (pole is a metal pole not wood on the SW Corner H street and North capitol street traffic pole - N/C underground | High Pressure Sodium | 38.90010486000 | -77.00885876000
9/15/09 | 766092 | 1400 | BRENTWOOD PKY | NE |  | 52559 | 5M037 | (Light out) |  | High Pressure Sodium | 38.91138782000 | -76.99222307000
9/15/09 | 766091 | 0 | 9TH ST | NE |  | 52562 | 5M035 | (Light out) |  | High Pressure Sodium | 38.91202820000 | -76.99202987000
9/15/09 | 766089 | 0 | MOUNT OLIVET RD | NE |  | 54272 | 5M044 | (Light out) |  | High Pressure Sodium | 38.91240042000 | -76.99153361000
9/15/09 | 766084 | 0 | NEW YORK AVE | NE |  | 56832 | 5M053 | (Light out) |  | High Pressure Sodium | 38.91324438000 | -76.99169504000
9/15/09 | 765786 | 0 | GARFIELD ST | NW | 9/16/09 | 35100 | 3A377 | (Light out) | (9-16-09 D Dixin inst 150w hps lamp) | High Pressure Sodium | 38.92674181000 | -77.05525746000
9/15/09 | 765604 | 3407 | MINNESOTA AVE | SE | 9/15/09 | 76578DC | 7S023 | (Light out) | DA 9-15-9 @ 956pm K. Simmons repaired pole #76578dc | High Pressure Sodium | 38.88422000000 | -76.95717076000
9/14/09 | 764445 | 3200 | KENYON PL | NW | 2/6/12 | 14683 | 1G052 | (Light out) | DA 9-15-09 @ 150am K. Dunton pole #14683 N/C underground | High Pressure Sodium | 38.93003166000 | -77.03236323000
9/14/09 | 764371 | 0 | NEW YORK AVE | NE | 2/23/10 | 50013 | 5A048 | (Light out) | DA 9-16-09 N/C underground | High Pressure Sodium | 38.91696428000 | -76.96182720000
9/14/09 | 764370 | 0 | NEW YORK AVE | NE | 2/23/10 | 50012 | 5A046 | (Light out) | DA 9-16-09 N/C underground | High Pressure Sodium | 38.91703724000 | -76.96344782000
9/14/09 | 764369 | 0 | NEW YORK AVE | NE | 2/23/10 | 50009 | 5A043 | (Light out) | DA 9-16-09 N/C underground | High Pressure Sodium | 38.91719217000 | -76.96575011000
9/14/09 | 764368 | 0 | NEW YORK AVE | NE | 2/23/10 | 50007 | 5A041 | (Light out) | DA 9-16-09 N/C underground | High Pressure Sodium | 38.91727852000 | -76.96718437000
9/14/09 | 764367 | 0 | NEW YORK AVE | NE | 10/1/09 | 50005 | 5A039 | (Light out) | DA 9-16-09 N/C underground | High Pressure Sodium | 38.91734425000 | -76.96859446000
9/14/09 | 764366 | 0 | NEW YORK AVE | NE | 2/23/10 | 50004 | 5A038 | (Light out) | DA 9-16-09 N/C underground | High Pressure Sodium | 38.91736785000 | -76.96929432000
9/14/09 | 764365 | 0 | NEW YORK AVE | NE | 2/23/10 | 50003 | 5A037 | (Light out) | DA 9-16-09 N/C underground | High Pressure Sodium | 38.91737165000 | -76.96995714000
9/14/09 | 764364 | 0 | NEW YORK AVE | NE | 9/25/09 | 50001 | 5A035 | (Light out) | DA 9-19-09 N/C underground | High Pressure Sodium | 38.91733557000 | -76.97140198000
9/14/09 | 764312 | 0 | FLORIDA AVE | NE | 9/16/09 | 62313 | 5M114 | (Light out) | DA 9-6-09 @ 129am T. Richards repaired ole #62313 respliced neturial - rubber , black tape and scotch kote DA 9-15-09 @ 423am T. Richards pole #62313 broken netural, Ran out of wire | High Pressure Sodium | 38.90860897000 | -77.00417478000
9/14/09 | 764308 | 900 | 2ND ST | SW | 9/15/09 | 68129 | 6A416 | (Light out) | DA 9-15-09 @ 149am T. Richards repaired pole #68129 | High Pressure Sodium | 38.87878241000 | -77.00287862000
9/14/09 | 764308 | 900 | 2ND ST | SW | 9/15/09 | 68129 | 68621 | (Light out) | DA 9-15-09 @ 149am T. Richards repaired pole #68129 | High Pressure Sodium | 38.90623996000 | -77.01082515000
9/14/09 | 764272 | 601 | 4TH ST | NW |  | 60437 | 6P013 | (Light out) | DA 9-16-09 @ 306am T. Richards pole #60437 in construction area boom won't extend far enough to reach pole - Hensel Phelps construction | High Pressure Sodium | 38.89517291000 | -77.01624618000
9/14/09 | 764269 | 801 | D ST | NW | 9/16/09 | 60087 | 2M371 | (Light out) | DA 9-16-09 @ 251am T. Richards repaired pole #60087 | High Pressure Sodium | 38.89493542000 | -77.02306697000
9/14/09 | 764268 | 777 | 6TH ST | NE |  | 68454 | 6S588 | (Light out) | DA 9-16-09 @ 214am T. Richards pole #68454 N/C underground | High Pressure Sodium | 38.89954137000 | -77.01979685000
9/14/09 | 764026 | 1222 | 1ST ST | NE | 9/16/09 | 61244 | 6A275 | (Light out) | DA 9-16-09 @ 116am T. Richards repaired pole #61244 | High Pressure Sodium | 38.90676525000 | -77.00596728000
9/14/09 | 764020 | 1401 | LAWRENCE ST | NE | 9/14/09 | 52485DC | 5A156DC | (Light out) | DA 9-14-09 @ 318am K. Simmons repaired pole #52485dc | High Pressure Sodium | 38.93175822000 | -76.98604463000
9/13/09 | 763999 | 715 | ANACOSTIA AVE | NE | 9/15/09 | 72359DC | 7A482 | (Light out) | DA 9-15-09 @ 326am R. Warren repaired pole 72359dc | High Pressure Sodium | 38.90218502000 | -76.95030078000
9/13/09 | 763957 | 0 | NEW YORK AVE | NE | 9/15/09 | 56832 | 5M053 | (Light out) | DA 9-14-09 @ 244am K. Simmons pole #56832 N/C underground | High Pressure Sodium | 38.91324438000 | -76.99169504000
9/13/09 | 763952 | 1400 | BRENTWOOD PKY | NE | 9/15/09 | 52559 | 5M037 | (Light out) | DA 9-13-09 @ 1012pm K. Simmons pole #52559 N/C underground - | High Pressure Sodium | 38.91138782000 | -76.99222307000
9/13/09 | 763949 | 1901 | 9TH ST | NE | 3/10/11 | 51319DC | 5M023 | (Light off/on) | (9-18-09- G Edwards PEPCO pole REFER to PEPCO) DA 9-13-09 @ 1020pm K. Simmons pole leaning pole #51319dc | High Pressure Sodium | 38.91566226000 | -76.99357657000
9/13/09 | 763947 | 0 | 9TH ST | NE | 9/15/09 | 52562 | 5M035 | (Light out) | DA 9-13-09 @ 1045pm K. Simmons pole #52562 N/C underground - | High Pressure Sodium | 38.91202820000 | -76.99202987000
9/13/09 | 763946 | 0 | MOUNT OLIVET RD | NE | 9/15/09 | 54272 | 5M044 | (Light out) | DA 9-13-09 @ 1012pm K. Simmons pole #54272 N/C underground - | High Pressure Sodium | 38.91240042000 | -76.99153361000
9/13/09 | 763930 | 2700 | 33RD PL | NE |  | 58654 | 5M178 | (Light out) | DA 9-14-09 K. Simmons not our light yet refer to Day Crews - | High Pressure Sodium | 38.92034560000 | -76.95743168000
9/11/09 | 763497 | 200 | K ST | NE | 9/13/09 | 61351 | 6B087 | (Light out) | DA 9-13-09 @ 1121pm T. Richards all lights are on nad working na 09-03034485-even side of 1000 block of 3rd street nw.. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90302176000 | -77.00210340000
9/10/09 | 762952 | 0 | 7TH ST | NW | 9/10/09 | 25656 | 6U467 | (Light out) | DA 9-10-09 @ 1115pm V. Cooke reaired pole #25656 | High Pressure Sodium | 38.90956587000 | -77.02202768000
9/10/09 | 762951 | 1700 | P ST | NW | 9/11/09 | 26348 | 2M075 | (Light out) | DA 9-11-09 @ 130am V. Cooke repired pole #26348 | High Pressure Sodium | 38.90971134000 | -77.03863962000
9/10/09 | 762452 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 9/11/09 | 71269 | 7A201 | (Light out) | DA 9-11-09 @ 115am T. Richards pole #71269 Already marked with N/C tape - Waiting for Pepco to install new Transformer | High Pressure Sodium | 38.89826963000 | -76.92624974000
9/10/09 | 762451 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 9/11/09 | 72645 | 7S073 | (Light out) | DA 9-11-09 @ 115am T. Richards pole #72645 Already marked with N/C tape - Waiting for Pepco to install new Transformer | High Pressure Sodium | 38.89826452000 | -76.92554310000
9/10/09 | 762413 | 5403 | NANNIE HELEN BURROUGHS AVE | NE | 9/11/09 | 72648 | 7A191 | (Light out) | DA 9-11-09 @ 115am T. Richards pole #72648 Already marked with N/C tape - Waiting for Pepco to install new Transformer | High Pressure Sodium | 38.89829839000 | -76.92250388000
9/10/09 | 762344 | 0 | CHILLUM PL | NE | 9/14/09 | 4P517DC | 4U175 | (Light out) | DA 9-14-09 @ 145am R. Warren repaired pole #4p517dc | High Pressure Sodium | 38.95886157000 | -77.00144501000
9/10/09 | 761802 | 200 | K ST | NE | 9/10/09 | 61351 | 6B087 | (Light out) | DA 9-10-09 @ 1033pm T. Richards redirected photocell pole #61351 | High Pressure Sodium | 38.90302176000 | -77.00210340000
9/9/09 | 761233 | 4700 | NORTH CAPITOL ST | NE | 9/10/09 | 4R754 | 4A795 | (Light out) | DA 9-10-09 @ 200am K. Dunton pole #4r754 N/C underground | High Pressure Sodium | 38.94814388000 | -77.00879153000
9/8/09 | 760334 | 437 | NEW YORK AVE | NW | 9/9/09 | 25922 | 29736 | (Light out) | BCM - response team was sent at 11am 9-9-09 - Refere to Work Order# 761070 9-03026817-This pole was knocked down by a police car on 9/4. It is lying on the sidewalk and needs to be removed and a replacement pole installed. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90478024000 | -77.01680666000
9/3/09 | 758944 | 0 | 7TH ST | NW | 9/7/09 | 22417 | 6M672 | (Light out) | DA 9-7-09 @ 1020pm V. Cooke repaired pole #22417 | High Pressure Sodium | 38.90076677000 | -77.02201803000
9/3/09 | 758943 | 0 | 8TH ST | NW | 9/4/09 | 25501 | 2M196 | (Light out) | 9-4-09 I Paraway Respliced wires inside T-Base) | High Pressure Sodium | 38.91218874000 | -77.02287935000
| 758767 | 5338 | NANNIE HELEN BURROUGHS AVE | NE | 2/23/10 | 72647 | 7A196 | (Light out) | DA 9-4-09 @ 343am K. Simmons pole #72647 N/C underground Front 09-03016561- cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89828319000 | -76.92411425000
9/3/09 | 758761 | 5516 | NANNIE HELEN BURROUGHS AVE | NE | 2/23/10 | 72651 | 7A184 | (Light out) | DA 9-4-09 @ 347am K. Simmons pole #72651 N/C underground RONT OF THIS ADDRESS 09-03015157-METAL AND WOODEN POLES LIGHTS ARE OUT cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.89830423000 | -76.92065348000
| 758032 | 0 | 7TH ST | NW | 9/8/09 | 14394 | 1M003 | (Light out) | DA 9-7-09 @ 1020pm K. Dunton repaired pole #14394 Block 09-03012868-CITYWORKS TESTING FOR ISLIMS cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91567433000 | -77.02182460000
9/2/09 | 757795 | 1936 | EAST CAPITOL ST | NE | 2/6/12 | 63721 | 6M804 | (Light out) | DA 9-4-09 @ 148am T. Richards pole #63721 N/C underground | High Pressure Sodium | 38.88960987000 | -76.97672435000
| 757632 | 60 | FLORIDA AVE | NE | 9/3/09 | 56991 | 5M143 | (Light out) | DA 9-3-09 @ 1242am K. Simmons pole #56991 light found on and working N/A 09-03003587-street light on metal pole is on and off cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.90995698000 | -77.00685274000
9/2/09 | 757600 | 1720 | 18TH ST | NW | 9/8/09 | 26897 | 2M125 | (Light out) | DA 9-8-09 @ 1010pm V. Cooke repaired pole #26897 SW Corner 09-03002684-STREET LIGHT ON METAL POLE. cwDesc: STREETLIGHT REPAIR | High Pressure Sodium | 38.91329133000 | -77.04170854000
9/2/09 | 757537 | 777 | NORTH CAPITOL ST | NE | 9/7/09 | 68241DC | 68241 | (Light out) | DA 9-7-09 @ 1012pm T. Richards repaired pole #68241dc DA 9-3-09 Needs Big Boom | High Pressure Sodium | 38.90010486000 | -77.00885876000
9/2/09 | 757135 | 0 | KENILWORTH AVE | NE | 9/2/09 | 79461 | 7A125 | (Light out) | DA 9-02-09 @ 1230a T. Rihards repaired pole #79461 | High Pressure Sodium | 38.89037514000 | -76.95748332000
9/1/09 | 757108 | 4520 | HOBAN RD | NW | 9/3/09 | 35821DC | 35821 | (Light out) | DA 9-3-09 @1205am K. Dunton repaired pole #35821dc | Incandescent | 38.91422302000 | -77.08546138000
9/1/09 | 757106 | 1808 | HOBAN RD | NW | 9/3/09 | 35823DC | 35823 | (Light out) | DA 9-3-09 @1210am K. Dunton repaired pole #35823dc | Incandescent | 38.91448031000 | -77.08497341000
9/1/09 | 757047 | 0 | 23RD ST | NW | 9/10/09 | 28306 | 2L462 | (Light out) | DA 9-3-09 @ 1040pm V. Cooke pole #28306 ran wire, new 400hps lamp, powerdoor - pole #28306 still only has 45 volts - refer to fau;t crew | High Pressure Sodium | 38.90131405000 | -77.05023193000
8/31/09 | 755303 | 0 | O ST | NW | 8/31/09 | 29268 | 6A852 | (Light out) | DA 8-31-09 @ 112am T Richards repaired pole #29268 | Incandescent | 38.90837595000 | -77.02348678000
8/31/09 | 755284 | 931 | 7TH ST | NW | 8/31/09 | 22414 | 6M678 | (Light out) | DA 831-9 @ 1228am T. Richards repaired pole #22414 | High Pressure Sodium | 38.90128473000 | -77.02201329000
8/31/09 | 755283 | 0 | 7TH ST | NW | 8/31/09 | 22412 | 6M682 | (Light out) | DA 8-31-09 @ 1216am T. Richards repaired pole #22412 | High Pressure Sodium | 38.90153465000 | -77.02201827000
8/31/09 | 755269 | 60 | FLORIDA AVE | NE | 8/31/09 | 56991 | 5M143 | (Light out) | DA 8-30-09 @ 1113pm K. Simmons repaired pole #56991 | High Pressure Sodium | 38.90995698000 | -77.00685274000
8/28/09 | 754065 | 1332 | 35TH ST | NW | 8/28/09 | 20903 | 2G192 | (Light out) | DA 8-28-09 @ 133am T. Richards repaired pole #20903 | High Pressure Sodium | 38.90762144000 | -77.06910533000
8/27/09 | 753974 | 1117 | NEW HAMPSHIRE AVE | NW | 8/28/09 | 23864 | 2G713 | (Light out) | 8-28-09 I.Paraway---repaired (sc) | High Pressure Sodium | 38.90423833000 | -77.04840189000
8/27/09 | 753955 | 0 | L ST | SE | 8/27/09 | 67701 | 6A438 | (Light out) | DA 8-27-09 @ 1100pm T. Richards repaired pole #67701 - reset master Photocell @ pole #67698 | High Pressure Sodium | 38.87758258000 | -77.00088038000
8/27/09 | 753950 | 0 | NEW HAMPSHIRE AVE | NW | 8/28/09 | 26879 | 2M146 | (Light out) | DA 8-27-09 @ 1151pm T. Richards repaired pole #26879 | High Pressure Sodium | 38.91121020000 | -77.04186432000
8/27/09 | 752954 | 3300 | O ST | NW | 8/27/09 | 21101 | 2G163 | (Light out) | DA 8-27-09 @ 1249am T. Richards repaired pole #21101 | High Pressure Sodium | 38.90782116000 | -77.06762886000
8/24/09 | 749604 | 0 | 24TH ST | NW | 8/24/09 | 24804 | 2G664 | (Light out) | DA 8-24-09 @ 1109pm T. Richards repaired pole #24804 | High Pressure Sodium | 38.90272824000 | -77.05133683000
8/23/09 | 749537 | 0 | BENNING RD | NE | 8/23/09 | 59599 | 5M220 | (Light out) | DA 8-23-09 @ 1057pm K. Simmons pole #59599 N/C underground - pole has already been referred to ddot comments Construction company on site has area torn up due to construction. refer to wo #733633 | High Pressure Sodium | 38.89996191000 | -76.98156127000
8/23/09 | 749535 | 900 | NEW JERSEY AVE | SE | 8/23/09 | 67472 | 6A060 | (Light out) | DA 8-23-09 @ 1032pm K. Dunton pole #67472 N/C underground (Streetlight pole is inside JPI construction area. ) pole #67472 has already been refered over to ddot refer to wo #691654 | High Pressure Sodium | 38.87881747000 | -77.00509329000
8/21/09 | 748820 | 821 | VIRGINIA AVE | SE | 8/21/09 | 67622 | 6L982 | (Light out) | DA 8-21-09 @ 147am T. Richards repaired pole #67622 | High Pressure Sodium | 38.87828971000 | -76.99484473000
8/21/09 | 748086 | 60 | FLORIDA AVE | NE | 8/21/09 | 56991 | 5M143 | (Light out) | DA 8-21-09 @ 1213am K. Simmons repaired pole #56991 | High Pressure Sodium | 38.90995698000 | -77.00685274000
8/19/09 | 747228 | 919 | L ST | NW | 8/20/09 | 29202 | 2L562 | (Light off/on) | DA 8-20-09 @ 302am V .Cooke repaired pole #29202 | High Pressure Sodium | 38.90411036000 | -77.02503736000
8/18/09 | 746516 | 3267 | P ST | NW | 8/20/09 | 21017 | 2G142 | (Light out) | DA 8-20-09 @ 324am V. Cooke repaired pole #21017 DA 8-19-09 @ 410am K. Duntion request for map | High Pressure Sodium | 38.90886358000 | -77.06536598000
8/18/09 | 746505 | 1720 | 18TH ST | NW | 8/19/09 | 26897 | 2M125 | (Light out) | DA 8-18-09 @ 1200am K. Dunton repaired pole #26897 | High Pressure Sodium | 38.91329133000 | -77.04170854000
8/17/09 | 747206 | 2 | MASSACHUSETTS AVE | NE | 11/20/09 | 60928 | 6U602 | (Light out) | DA 8-20-09 @ 120am T. Richards repaired pole #60928 POLE # 60928 THANKS MERRIT DRUCKER - G 11-19-09 S.Manning---pole tag was removed/no longer serviced by d-dot (sc) | High Pressure Sodium | 38.89801466000 | -77.00755371000
8/17/09 | 745624 | 1701 | 18TH ST | NW | 8/18/09 | 26754 | 2M132 | (Light out) | DA 8-18-09 @ 1200am V. Cooke repaired pole #26754 | High Pressure Sodium | 38.91269470000 | -77.04159836000
8/13/09 | 744016 | 1400 | BRENTWOOD PKY | NE |  | 52559 | 5M037 | (Light out) | DA 8-14-09 @ 129am R. Warren pole #52559 N/C underground | High Pressure Sodium | 38.91138782000 | -76.99222307000
8/13/09 | 744013 | 0 | NEW YORK AVE | NE |  | 56790 | 5M031 | (Light out) | DA 8-14-09 @ 141am R. Warren pole #56790 N/C underground | High Pressure Sodium | 38.91355367000 | -76.99280870000
8/13/09 | 744011 | 0 | NEW YORK AVE | NE | 9/15/09 | 56832 | 5M053 | (Light out) | DA 8-14-09 @ 119am R. Warren pole #56832 N/C underground | High Pressure Sodium | 38.91324438000 | -76.99169504000
8/13/09 | 744008 | 0 | MOUNT OLIVET RD | NE | 9/15/09 | 54272 | 5M044 | (Light out) | DA 8-13+-09 @ 1152pm R. Warren pole #54272 N/C underground | High Pressure Sodium | 38.91240042000 | -76.99153361000
8/13/09 | 744006 | 1300 | 1ST ST | NE |  | 61247 | 6A279 | (Light out) | DA 8-14-09 @ 108am T. Richards repaired pole #61247 - needs tree trimmed | High Pressure Sodium | 38.90758804000 | -77.00596758000
8/13/09 | 744004 | 0 | 9TH ST | NE | 9/15/09 | 52561 | 5M036 | (Light out) | DA 8-13-09 @ 1139pm R. Warren pole #52561 N/C underground | High Pressure Sodium | 38.91169939000 | -76.99207526000
8/13/09 | 744003 | 0 | 9TH ST | NE | 9/15/09 | 52561 | 5M036 | (Light out) | DA 8-14-09 @ 100am R. Warren pole #52561 N/C underground | High Pressure Sodium | 38.91169939000 | -76.99207526000
8/13/09 | 744002 | 1222 | 1ST ST | NE | 8/14/09 | 61244 | 6A275 | (Light out) | DA 8-14-09 @ 116am T. Richards repaired pole #61244 - repaired loose photocell | High Pressure Sodium | 38.90676525000 | -77.00596728000
8/13/09 | 744001 | 2 | L ST | NE | 8/14/09 | 61201 | 6A240 | (Light out) | DA 8-14-09 @ 108am T. Richards pole #61201 N/C with surface cut refer to open wo #725113 | High Pressure Sodium | 38.90378899000 | -77.00858856000
8/13/09 | 743996 | 457 | MASSACHUSETTS AVE | NW | 8/14/09 | 60481 | 6A195 | (Light out) | DA 8-14-09 @ 116am T. Richards pole #60481 has been refered to ddot refer to open wo #628005 | High Pressure Sodium | 38.90073307000 | -77.01753805000
8/13/09 | 743993 | 0 | INTERSTATE 695 | SE | 8/13/09 | 695-001W-9 | 695W613 | (Overhead guide sign light out) |  | High Pressure Sodium | 38.88110666000 | -77.00656804000
8/13/09 | 743954 | 1600 | OATES ST | NE | 8/13/09 | 52808 | 5B259 | (Light out) | DA 8-13-09 @ 409am R. Warren repaired pole #52808 | High Pressure Sodium | 38.90288129000 | -76.98206430000
8/12/09 | 743350 | 800 | 4TH ST | SW | 8/13/09 | 66751 | 6S043 | (Light out) | DA 8-13-09 @ 204am T. Richards rpaired pole #66751 | High Pressure Sodium | 38.87942157000 | -77.01744296000
8/12/09 | 743342 | 0 | 3RD ST | NW | 8/14/09 | 67896 | 68448 | (Light out) | DA 8-14-09 @ 116am T. Richards all lights in area are on and working DA 8-13-09 @ 240am T. Richards pole #67896 can not locate - Bad address request for map | High Pressure Sodium | 38.90052914000 | -77.01507220000
8/11/09 | 742560 | 911 | T ST | NW | 8/13/09 | 13452 | 1L371 | (Light out) | DA 8-13-09 @ 125am K. Dunton repaired pole #13452 - street light is out | High Pressure Sodium | 38.91552640000 | -77.02455445000
8/10/09 | 742578 | 0 | 3RD ST | NW | 8/13/09 | 59991 | 5A184 | (Light out) | DA 8-13-09 @ 135am R, Warren repaired pole #59991 CORNER - | High Pressure Sodium | 38.91407956000 | -77.01569433000
8/10/09 | 741735 | 0 | 13TH ST | NW | 8/11/09 | 4K429 | 4U143 | (Light out) | DA 8-11-09 @ 356am R. Warren repaired pole #4k429 | High Pressure Sodium | 38.94382247000 | -77.02962404000
8/10/09 | 741761 | 741 | 51ST ST | SE | 8/12/09 | 75475 | 75475DC | (Light out) | DA8-12-09 @ 111am T. Richards repaired pole #75475 ALLEY - Alleylight is out on wooden pole.This happened very often. Light was repaired just last week /request # 2211953 | Incandescent | 38.87911825000 | -76.93033276000
8/10/09 | 741697 | 2010 | 48TH ST | NW | 8/10/09 | 35371DC | 3E028 | (Light out) | DA 8-10-09 @ 317am K, Dunton repaired pole #35371dc | Incandescent | 38.91732328000 | -77.09428336000
8/7/09 | 740228 | 1702 | SHEPHERD ST | NW | 8/18/09 | 4F232DC | 4F231DC | (Light out) | DA 8-13-09 @ 209am R. Warren pole #4f232dc - NEEDS A LADDER - can not access with van DA 8-11-09 @ 423am R. Warren pole #4f232dc Needs ladder DA 8-10-09 K. Dunton request for map | High Pressure Sodium | 38.93971259000 | -77.03814519000
8/6/09 | 740178 | 1901 | 18TH ST | NW | 8/7/09 | 26748 | 2M097 | (Light out) | BCM 8-7-09 V. COOKE REPAIRED POLE | High Pressure Sodium | 38.91567759000 | -77.04157059000
8/6/09 | 740143 | 226 | RHODE ISLAND AVE | NW | 8/6/09 | 59994 | 5A186 | (Light out) | DA 8-6-09 @ 408am K. Simmons repaired pole #59994 | Incandescent | 38.91452540000 | -77.01525438000
8/6/09 | 740104 | 2702 | WISCONSIN AVE | NW | 8/6/09 | 30175 | 3G030 | (Light out) | DA 8-6-09 @ 130am K. Dunton repaired pole #30175 | High Pressure Sodium | 38.92501826000 | -77.07307257000
8/5/09 | 739404 | 2473 | 18TH ST | NW | 8/6/09 | 11406 | 1G478 | (Light out) | DA 8-6-09 @ 220am V. Cooke repaired pole #11406 | High Pressure Sodium | 38.92224805000 | -77.04243267000
8/5/09 | 739392 | 5656 | 3RD ST | NE |  | 4P473DC | 4U162 | (Light out) | DA 8-6-09 @ 1219am R. Warren repaired pole #4p473dc - needs tree trimmed | High Pressure Sodium | 38.95791886000 | -77.00307597000
8/4/09 | 738487 | 0 | 18TH ST | NW | 8/5/09 | 26770 | 2M164 | (Light out) | DA 8-4-09 @ 1145pm V Cooke repaired pole #26770 | High Pressure Sodium | 38.91009872000 | -77.04173924000
8/4/09 | 738504 | 741 | 51ST ST | SE | 8/5/09 | 75475 | 75475DC | (Light out) | (8-5-09 D Dixon 295 inc lamp) ALLEY - alleylight is out,please inspect and repair | Incandescent | 38.87911825000 | -76.93033276000
8/4/09 | 738425 | 2101 | WISCONSIN AVE | NW | 2/10/12 | 29803 | 3G117 | (Light out) | (8-4-09 MB REFER to DDOT traffic pole) DA 8-4-09 @ 358am V. Cooke repaired pole #29803 - needs 4 ears | High Pressure Sodium | 38.91692553000 | -77.06883584000
8/4/09 | 738424 | 1901 | 9TH ST | NE | 8/4/09 | 51319DC | 5M023 | (Light out) | DA 8-4-09 @ 410am K. Simmons repaired pole #51319dc | High Pressure Sodium | 38.91566226000 | -76.99357657000
8/4/09 | 738419 | 1400 | PARK RD | NW | 8/4/09 | 12701 | 1G378 | (Light out) | DA 8-4-09 @ 200am V. Cooke repaired pole #12701 | High Pressure Sodium | 38.93092482000 | -77.03443295000
8/3/09 | 737617 | 107 | WASHINGTON CIR | NW | 8/5/09 | 24655 | 2G671 | (Light out) | DA 8-5-09 @ 225am V. Cooke repaired pole #24655 - street light on metal pole is on and off | High Pressure Sodium | 38.90310962000 | -77.05038859000
8/3/09 | 737575 | 0 | EAST CAPITOL ST | NE | 2/10/12 | 74205DC | 7A063DC | (Light out) | DA 8-4-09 @ 1239am T. Richards pole # is 74205dc - Correct address is east capital street and benning road NW corner NE ward 7 Traffic pole - N/C underground (islims updated) | High Pressure Sodium | 38.89216210000 | -76.94254713000
8/3/09 | 739489 | 900 | UPSHUR ST | NW | 8/6/09 | 4R782 | 4R790 | (Light out) | ALLEY - 8-6-09 D.Dixon---repaired (sc) | High Pressure Sodium | 38.94192259000 | -77.02846969000
8/2/09 | 737412 | 1400 | S ST | NW | 8/4/09 | 26184 | 2A080 | (Light off/on) | DA 8-4-09 @ 1230am V. Cooke repaired - rewired pole (rubber tape, electrical tape) | High Pressure Sodium | 38.91415171000 | -77.03212341000
7/31/09 | 736845 | 1500 | ECKINGTON PL | NE | 8/3/09 | 57178 | 5M137 | (Light out) | DA 8-2-09 @ 1050pm V. Cooke reattached T Base door - pole 5778 need a tee base repair | High Pressure Sodium | 38.90954093000 | -77.00511944000
7/31/09 | 736784 | 2434 | WISCONSIN AVE | NW | 7/31/09 | 30167 | 3G062 | (Light out) | DA 7-31-09 @ 137am K. Dunton repaired pole #30167 | High Pressure Sodium | 38.92197361000 | -77.07243532000
7/29/09 | 735463 | 2218 | WISCONSIN AVE | NW | 7/31/09 | 30152 | 3G085 | (Light out) | DA 7-31-09 @ 119am K. Dunton repaired pole #30152 | High Pressure Sodium | 38.91965393000 | -77.07114553000
7/29/09 | 735455 | 0000 | H ST | NE | 2/6/12 | 68256DC | 68256 | (Light out) | DA 7-30-09 @ 150am K. Dunton pole #68256dc temp traffic pole - N/Current - refer to ddot | High Pressure Sodium | 38.90037511000 | -77.00632229000
7/29/09 | 735451 | 0 | MARTIN LUTHER KING JR AVE | SE | 7/30/09 | 81018 | 8L855 | (Light out) | DA 7-30-09 @ 1206am R. Warren pole #81018 N/C underground | High Pressure Sodium | 38.86833152000 | -76.98830912000
7/29/09 | 735435 | 0 | 3RD ST | NW | 7/31/09 | 67896 | 68448 | (Light out) | DA 7-31-09 @ 151am T. Richards all lights in area are on and working | High Pressure Sodium | 38.90052914000 | -77.01507220000
7/29/09 | 735431 | 0 | EAST CAPITOL ST | NE | 7/30/09 | 74205DC | 7A063DC | (Light out) | DA 7-30-09 @ 120am T. Richards repaired pole #74205dc | High Pressure Sodium | 38.89216210000 | -76.94254713000
7/29/09 | 735419 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 3/10/11 | 71270 | 71270DC | (Light out) | DA 7-30-09 @ 305am T. Richards pole #71270 stlii N/C underground | High Pressure Sodium | 38.89827347000 | -76.92679095000
7/29/09 | 735481 | 741 | 51ST ST | SE | 7/31/09 | 75475 | 75475DC | (Light out) | DA 7-30-09 @ 1143pm T. Richards repaired pole #75475 REAR - alley lght is out | Incandescent | 38.87911825000 | -76.93033276000
7/29/09 | 735336 | 1125 | 11TH ST | NW | 7/29/09 | 25263 | 2M226 | (Light out) | DA 7-29-09 @ 1240am V. Cooke repaired pole #25263 | High Pressure Sodium | 38.90526694000 | -77.02692404000
7/28/09 | 734619 | 300 | EASTERN AVE | NE | 7/29/09 | 70026 | 72855 | (Light out) | DA 7-29-09 @ 430am T. Richards repaired pole #70026 | High Pressure Sodium | 38.89394625000 | -76.91101330000
7/28/09 | 734608 | 4500 | SHERIDAN RD | SE | 7/30/09 | 81359DC | 8U644 | (Light out) | DA 7-29-09 @ 203am R. Warren pole #81359dc N/C to overhead neds triplex pulled from pole 81359dc to 81358dc | High Pressure Sodium | 38.85817131000 | -76.99317521000
7/28/09 | 734580 | 2811 | PENNSYLVANIA AVE | SE | 7/28/09 | 78570DC | 7E083DC | (Light out) | DA7-28-09 @ 1100pm T. Richards repaired pole #78570dc - tightened split bolt | High Pressure Sodium | 38.87218747000 | -76.96768794000
7/28/09 | 734520 | 2201 | WISCONSIN AVE | NW | 7/28/09 | 30160 | 3G090 | (Light out) | DA 7-28-09 @ 250am V. Cooke repaired pole #30160 | High Pressure Sodium | 38.91927198000 | -77.07055935000
7/27/09 | 733746 | 0 | L ST | SE | 2/6/12 | 67701 | 6A438 | (Light out) | DA 7-28-09 @ 350am T. Richards pole #67701 N/C underground | High Pressure Sodium | 38.87758258000 | -77.00088038000
7/27/09 | 733772 | 0 | GARFIELD ST | NW | 7/28/09 | 35100 | 3A377 | (Light out) | (7-28-09 M Brewer inst 150w hps lamp) INTERSECTION ON 27TH ST NW - street light out on a metal pole. | High Pressure Sodium | 38.92674181000 | -77.05525746000
| 733795 | 1126 | 11TH ST | NW | 7/29/09 | 25276 | 2M262 | (Light out) | DA 7-29-09 @ 105am V. Cooke repaired pole #25276 FRONT - Metal pole burnt out bulb. | High Pressure Sodium | 38.90502429000 | -77.02715562000
7/26/09 | 733637 | 1950 | BENNING RD | NE | 7/27/09 | 59612DC | 5M317 | (Light out) | DA 7-27-09 @ 940am T. Richards repaired pole #59612dc | High Pressure Sodium | 38.89868854000 | -76.97411295000
7/26/09 | 733634 | 0 | BENNING RD | NE | 7/27/09 | 59598 | 5M225 | (Light out) | DA 7-27-09 @ 1015pm T. Richards pole #59598 N/C underground - open wo #668067 - Hansen #208239 | High Pressure Sodium | 38.90009642000 | -76.98233922000
7/26/09 | 733633 | 0 | BENNING RD | NE | 2/6/12 | 59599 | 5M220 | (Light out) | DA 7-27-09 @ 1010pm T. Richards pole #59599 N/C underground - Traffic pole / seperate conduit | High Pressure Sodium | 38.89996191000 | -76.98156127000
7/26/09 | 733632 | 4500 | EAST CAPITOL ST | SE | 3/21/10 | 70052 | 7A035 | (Light out) | DA 7-27-09 @ 1259am T. Richards pole #70052 N/C underground - open wo #723160 | High Pressure Sodium | 38.88960932000 | -76.93729068000
7/24/09 | 732862 | 2636 | FIRTH STERLING AVE | SE | 7/27/09 | 81580DC | 8A054 | (Light out) | DA 7-26-09 @ 1144pm T. Richards repaired pole #81580dc FRONT - caller request that a streetlight be repaired in front of address on two wooden poles one pole facing Eaton Rd | High Pressure Sodium | 38.86102892000 | -77.00057006000
7/24/09 | 732124 | 2619 | WISCONSIN AVE | NW | 7/24/09 | 30141 | 3G039 | (Light out) | DA 7-24-09 @ 1226am K. Dunton repaied pole #30141 | High Pressure Sodium | 38.92412603000 | -77.07330492000
7/23/09 | 732114 | 623 | KENNEDY ST | NW | 7/24/09 | 4M069 | 4M069DC | (Light out) | DA 7-24-09 @ 224am R. Warren repaired pole #4m069 | High Pressure Sodium | 38.95646426000 | -77.02185855000
7/23/09 | 732105 | 4521 | 13TH ST | NW | 7/24/09 | 4K421 | 4U130 | (Light out) | DA 7-24-09 @ 313am R. Warren repaired pole #4k421 | High Pressure Sodium | 38.94589765000 | -77.02962270000
7/23/09 | 731399 | 4520 | HOBAN RD | NW | 7/23/09 | 35820DC | 35820 | (Light out) | DA 7-23-09 @ 1230am V. Cooke repaired pole #35820dc | Incandescent | 38.91406815000 | -77.08570450000
7/22/09 | 731316 | 0 | MARYLAND AVE | NE | 7/22/09 | 59539 | 5M243 | (Light out) | DA 7-22-09 @ 1031pm K. Simmons repaired pole #59539 | High Pressure Sodium | 38.90096397000 | -76.98165776000
7/22/09 | 731315 | 0 | MORSE ST | NE | 7/22/09 | 52757 | 5M268 | (Light out) | DA 7-22-09 @ 1016pm K. Simmons repaired pole #52757 | High Pressure Sodium | 38.90089466000 | -76.98323986000
7/22/09 | 731310 | 0 | MOUNT OLIVET RD | NE | 9/15/09 | 54272 | 5M044 | (Light out) | DA 7-23-09 @ 330am K. Simmons pole #54272 N/C underground | High Pressure Sodium | 38.91240042000 | -76.99153361000
7/22/09 | 731306 | 0 | 9TH ST | NE |  | 52561 | 5M036 | (Light out) | DA 7-23-09 @ 314an . Simmons pole #52561 N/C underground | High Pressure Sodium | 38.91169939000 | -76.99207526000
7/22/09 | 731305 | 0 | 9TH ST | NE |  | 52562 | 5M035 | (Light out) | DA 7-23-09 @ 325am K. Simmons pole #52562 N/C underground | High Pressure Sodium | 38.91202820000 | -76.99202987000
7/22/09 | 731304 | 1400 | BRENTWOOD PKY | NE |  | 52559 | 5M037 | (Light out) | DA 7-23-09 @ 318am K. Simmons pole #52559 N/C underground | High Pressure Sodium | 38.91138782000 | -76.99222307000
7/22/09 | 731286 | 1300 | BRYANT ST | NE |  | 51336DC | 5A254 | (Light out) | DA 7-23-09 @ 214am K. simmons pole #51336dc refer to ddot defective teardrop fixture | High Pressure Sodium | 38.92097735000 | -76.98895164000
7/22/09 | 731284 | 0 | NEW YORK AVE | NE | 7/23/09 | 56831 | 5M054 | (Light out) | DA 7-23-09 @ 243am K. Simmons repaired pole #56831 | High Pressure Sodium | 38.91332392000 | -76.99146591000
7/21/09 | 730444 | 1411 | H ST | NE | 7/22/09 | 62355 | 6M711 | (Light out) | DA 7-21-09 @ 1004pm T./ Ri9chards repaired pole #62355 - Needs Ears 7-22-09 M.Brewer---drill & tapped 2 holes/install 2 ee's (sc) | High Pressure Sodium | 38.90010969000 | -76.98500705000
7/21/09 | 730066 | 1918 | 18TH ST | NW | 7/21/09 | 26783 | 2M092 | (Light out) | DA 7-21-09 @ 315am V. Cooke repaired pole #26783 | High Pressure Sodium | 38.91621491000 | -77.04174256000
7/21/09 | 729293 | 1300 | MONROE ST | NW | 7/21/09 | 13676 | 1G086 | (Light out) | DA 7-21-09 @ 1215am K. Simmons repaired pole #13676 | High Pressure Sodium | 38.93146550000 | -77.03246204000
7/20/09 | 728887 | 777 | 6TH ST | NE |  | 68454 | 6S588 | (Light out) | DA 7-20-09 @ 341am T. Richards pole #68454 N/C underground @ fixture no access to base | High Pressure Sodium | 38.89954137000 | -77.01979685000
7/20/09 | 729313 | 0 | NEW YORK AVE | NE | 7/22/09 | 50005 | 5A039 | (Light out) | (7-22-09 D Smith/Dixon repaired pole 1-400w hps lMp & TLPC) DA 7-21-09 @ 1010pm K. Simmons only one light found out pole #50005 - Needs Big Boom NEAR THE WASHINGTON TIMES BLDG - all street lights are out//on both sides of the street | High Pressure Sodium | 38.91734425000 | -76.96859446000
7/19/09 | 728847 | 0 | CONNECTICUT AVE | NW | 7/19/09 | 38617 | 3L467 | (Light out) | DA D7-19-09 @ 1108pm K. Dunton repaired pole #38617 | High Pressure Sodium | 38.94688419000 | -77.06495794000
7/17/09 | 728074 | 3328 | 14TH ST | NW | 7/17/09 | 13814 | 1G070 | (Light out) | DA 7-16-09 @ 410am V. Cooke Repaired pole #13814 | High Pressure Sodium | 38.93115209000 | -77.03279719000
7/16/09 | 727353 | 1553 | BENNING RD | NE |  | 63609 | 6M758 | (Light out) | DA 7-16-09 @ 1151pm T. Richards pole #63609 N/C underground - rooad construction in area | High Pressure Sodium | 38.89983358000 | -76.98244187000
7/16/09 | 727429 | 1900 | 37TH ST | NW | 7/23/09 | 36891 | 30482 | (Light out) | DA 7-20-09 @ 240am K. Dunton repaired pole tag missing SW CORNER - one wooden pole light is out 7-22-09 S.Kennedy---install tag (sc) | High Pressure Sodium | 38.91672906000 | -77.07292654000
7/15/09 | 728138 | 0 | M ST | NW | 7/20/09 | 23739 | 2G718 | (Light out) | DA 7-20-9 @ 240am V. Cooke pole #23739 light found on and working NEC - | High Pressure Sodium | 38.90513126000 | -77.04778068000
7/15/09 | 726792 | 0 | NEW YORK AVE | NE | 7/15/09 | 50005 | 5A039 | (Light out) | DA 7-15-069 @ 423am T. Richards repaired pole #50005 | High Pressure Sodium | 38.91734425000 | -76.96859446000
7/15/09 | 726791 | 0 | NEW YORK AVE | NE | 7/15/09 | 50011 | 5A045 | (Light out) | DA 7-15-09 @ 316am T. Richards repaired pole #50011 | High Pressure Sodium | 38.91707776000 | -76.96424700000
7/15/09 | 726778 | 600 | MICHIGAN AVE | NE | 7/15/09 | 53646DC | 5U708 | (Light out) | DA 7-15-09 @ 245am K. Simmons repaired pole #53646dc | High Pressure Sodium | 38.93303755000 | -76.99623620000
7/14/09 | 725990 | 0 | FLORIDA AVE | NW | 7/15/09 | 11432 | 1A124 | (Light out) | DA 7-15-09 @ 1255am K. Dunton pole #11432 light found on and woking | High Pressure Sodium | 38.91785023000 | -77.04029018000
7/14/09 | 725988 | 0 | CALIFORNIA ST | NW | 7/15/09 | 11159 | 1A102 | (Light out) | DA 7-15-09 @ 1255am K. Dunton pole #11159 light found on and woking | High Pressure Sodium | 38.91772320000 | -77.04056351000
7/14/09 | 725838 | 410 | 7TH ST | NW | 7/14/09 | 60647 | 6M616 | (Light out) | DA 7-14-09 @ 1246am T. Richards adjusted photocell pole #60647 | High Pressure Sodium | 38.89512871000 | -77.02201224000
7/14/09 | 725837 | 410 | 7TH ST | NW | 7/14/09 | 60647 | 6M616 | (Light out) | DA7-14-09 @ 1246am T. Richards repaired shortage in wire pole #60647 | High Pressure Sodium | 38.89512871000 | -77.02201224000
7/13/09 | 725113 | 2 | L ST | NE | 9/3/09 | 61201 | 6A240 | (Light out) | DA 7-13-09 @ 1124pm T. Richards pole #61201 N/C undergound and needs T Base Door | High Pressure Sodium | 38.90378899000 | -77.00858856000
7/13/09 | 725062 | 777 | 6TH ST | NE | 7/13/09 | 68454 | 6S588 | (Light out) | DA 7-13-09 @ 415am V. Cooke pole #68454 N/C underground | High Pressure Sodium | 38.89954137000 | -77.01979685000
7/13/09 | 725054 | 1125 | 11TH ST | NW | 7/13/09 | 25263 | 2M226 | (Light out) | DA 7-13-09 @ 353am V. Cooke repaired pole #52563 | High Pressure Sodium | 38.90526694000 | -77.02692404000
7/13/09 | 725053 | 1111 | 11TH ST | NW | 7/13/09 | 25266 | 2M224 | (Light out) | DA 7-13-09 @ 346am V. Cooke pole #25266 N/C underground | High Pressure Sodium | 38.90495600000 | -77.02692559000
7/13/09 | 725030 | 2200 | WISCONSIN AVE | NW | 7/13/09 | 30153 | 3G089 | (Light out) | DA 7-13-09 @ 220am K. Dunton repaired pole #30153 | High Pressure Sodium | 38.91934954000 | -77.07088992000
7/12/09 | 724975 | 5516 | NANNIE HELEN BURROUGHS AVE | NE | 7/13/09 | 72651 | 7A184 | (Light out) | DA 7-13-09 @ 214am T. Richards pole #72651 N/C undergound - refer to wo #722256 | High Pressure Sodium | 38.89830423000 | -76.92065348000
7/12/09 | 724973 | 5408 | NANNIE HELEN BURROUGHS AVE | NE | 7/13/09 | 72639DC | 7A190 | (Light out) | DA 7-13-09 @ 329am T. Richards repaired pole #72639dc | High Pressure Sodium | 38.89843971000 | -76.92240956000
7/12/09 | 724972 | 5403 | NANNIE HELEN BURROUGHS AVE | NE | 7/13/09 | 72648 | 7A191 | (Light out) | DA 7-13-09 @ 214am T. Richards pole #72648 N/C underground | High Pressure Sodium | 38.89829839000 | -76.92250388000
7/12/09 | 724971 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 7/13/09 | 71269 | 7A201 | (Light out) | DA 7-13-09 @ 214am T. Richards pole #71269 N/ C underground - lights are still N/C | High Pressure Sodium | 38.89826963000 | -76.92624974000
7/12/09 | 724970 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 7/13/09 | 71270 | 71270DC | (Light out) | DA 7-13-09 @ 214am T. Richards pole #71270 N/C underground - earlier wo closed but lights are still out | High Pressure Sodium | 38.89827347000 | -76.92679095000
7/12/09 | 724969 | 5338 | NANNIE HELEN BURROUGHS AVE | NE | 7/13/09 | 72647 | 7A196 | (Light out) | DA 7-13-09 @ 214am T. Richards pole #72647 N/C underground - open wo #721375 | High Pressure Sodium | 38.89828319000 | -76.92411425000
7/12/09 | 724968 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 7/13/09 | 72645 | 7S073 | (Light out) | DA 7-13-09 @ 214am T. Richards pole #72645 N/C underground | High Pressure Sodium | 38.89826452000 | -76.92554310000
7/10/09 | 724021 | 0 | 14TH ST | NW | 7/10/09 | 12074 | 1G562 | (Light out) | DA 7-10-09 @ 200am V.Cooke repaired pol #12074 | High Pressure Sodium | 38.92050364000 | -77.03173722000
7/9/09 | 723160 | 4500 | EAST CAPITOL ST | SE | 2/6/11 | 70052 | 7A035 | (Light out) | DA 7-10-09 @ 1235am T. Richards pole #70052 N/C underground (traffic pole ) | High Pressure Sodium | 38.88960932000 | -76.93729068000
7/8/09 | 722256 | 5516 | NANNIE HELEN BURROUGHS AVE | NE | 7/13/09 | 72651 | 7A184 | (Light out) | DA 7-8-09 @ 1120pm T. Richards pole #72651 N/C underground | High Pressure Sodium | 38.89830423000 | -76.92065348000
7/8/09 | 722233 | 4215 | NANNIE HELEN BURROUGHS AVE | NE | 7/9/09 | 71321DC | 7A254 | (Light out) | DA 7-8-069 @ 1053pm T. Richards repaired pole #71321dc | High Pressure Sodium | 38.90185248000 | -76.94213833000
7/8/09 | 722229 | 0 | MARTIN LUTHER KING JR AVE | SE | 7/13/09 | 81018 | 8L855 | (Light out) | DA 7-8-09 @ 1022pm K. Simmons pole #81018 N/C underground | High Pressure Sodium | 38.86833152000 | -76.98830912000
7/7/09 | 721375 | 5338 | NANNIE HELEN BURROUGHS AVE | NE | 3/10/11 | 72647 | 7A196 | (Light out) | - (7-13-09 GE no problem found) DA 7-8-09 @ 1109pm T. Richards pole #72647 - N/C underground - Needs T base door installed / and tbase needs repaired ACROSS STREET FROM ADDRESS - streetlight has been out since grass was cut and wire was cut off las | High Pressure Sodium | 38.89828319000 | -76.92411425000
7/7/09 | 721370 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 3/10/11 | 72649 | 7A189 | (Light out) | DA 7-809 @ 1115pm T. Richards pole #72649 N/Cunderground BETWEEN 55TH & 58TH STREETS ON NANNIE HELEN BURROUGHS AVE, NE - | High Pressure Sodium | 38.89825683000 | -76.92196339000
7/7/09 | 721341 | 0 | RIGGS RD | NE | 7/22/09 | 4P772DC | 4P772 | (Light out) | DA 7-8-09 @ 1200am R. Warren repaired pole #4p772dc- Need tree trimmed | High Pressure Sodium | 38.95714199000 | -77.00204139000
7/7/09 | 721367 | 3224 | G ST | SE | 7/9/09 | 76723DC | 7S039 | (Light out) | DA 7-9-09 @ 1255am T. Richards repaired pole #76723dc ALLEY - Light is out on wooden pole | Incandescent | 38.88056165000 | -76.95979610000
7/7/09 | 721159 | 18 | 3RD ST | SE | 7/7/09 | 6A003 | 6A003 | (Light out) | DA 7-7-09 @ 352am T. Richards repaired pole #6a003 | Incandescent | 38.87723028000 | -77.00452085000
7/6/09 | 720400 | 1826 | CALVERT ST | NW | 7/13/09 | 11197 | 1A003 | (Light out) | DA 7-7-09 @ 1019pm K. Simmons pole #11197 N/C underground | High Pressure Sodium | 38.92316276000 | -77.04378689000
7/6/09 | 720399 | 1826 | CALVERT ST | NW | 7/13/09 | 10729 | 1A013 | (Light out) | DA 7-7-09 @ 1024pm K. Simmons pole #10729 N/C underground | High Pressure Sodium | 38.92339148000 | -77.04377813000
7/2/09 | 719526 | 1457 | PARK RD | NW | 2/6/12 | 12702 | 1G375 | (Light out) | DA 7-7-09 @ 255am K. Simmoms pole #12702 N/C underground | High Pressure Sodium | 38.93096473000 | -77.03479369000
7/2/09 | 719524 | 0 | 14TH ST | NW | 7/7/09 | 12074 | 1G562 | (Light out) | DA 7-7-09 @ 308am K. Simmons repaired pole #12074 | High Pressure Sodium | 38.92050364000 | -77.03173722000
6/30/09 | 717695 | 1300 | BRYANT ST | NE | 7/5/09 | 51336DC | 5A254 | (Light out) | DA 7-02-09 @ 329am K. Simmons can npt reach light due to construction - these lights are being converted by a 3rd party contractor | High Pressure Sodium | 38.92097735000 | -76.98895164000
6/30/09 | 717672 | 1435 | NEWTON ST | NW | 7/1/09 | 13913 | 1G072 | (Light out) | DA 7-01-09 @ 1210am K. Dunton repaired pole #13913 | High Pressure Sodium | 38.93143118000 | -77.03279918000
6/26/09 | 716139 | 700 | 1ST ST | NE | 6/29/09 | 68284 | 6U596 | (Light out) | DA 6-28-09 @ 1045pm K. dunton base of light found in good condition pole #68284 - requesting to have the base of street light pole # 68284 at this location replaced.. | High Pressure Sodium | 38.89900607000 | -77.00720264000
6/26/09 | 715355 | 0 | K ST | NW | 6/26/09 | 22402 | 6A100 | (Light out) | CP - 6/26 - D Smith DA 6-26-09 @ 1200am T. Richards pole #22402 No Current Underground | High Pressure Sodium | 38.90245268000 | -77.01971021000
6/25/09 | 715345 | 5338 | NANNIE HELEN BURROUGHS AVE | NE | 3/10/11 | 72647 | 7A196 | (Light out) | DA 6+25-09 @ 1145pm K. Simmons pole #72647 / No Current underground | High Pressure Sodium | 38.89828319000 | -76.92411425000
6/24/09 | 714558 | 1401 | 17TH ST | NW | 2/8/12 | 26710 | 2M005 | (Light out) | 6-29-09 G Smith Traffic pole REFER to DDOT) DA 6-25-09 @ 221am R. Warren Repaired pole #26710 - Need T Base Repaired rusted and has hole in base | High Pressure Sodium | 38.90803650000 | -77.03840680000
6/24/09 | 714557 | 0 | NEW YORK AVE | NW | 6/25/09 | 22914 | 2L029 | (Light out) | DA 6-24-09 @ 1140pm R. Warren repaired east fixture pole #22914 | High Pressure Sodium | 38.90105629000 | -77.02684066000
6/24/09 | 714554 | 0 | 1ST ST | NE | 7/22/09 | 61239 | 6A264 | (Light out) | DA 6-24-09 @ 1019pm T. Richards repaired pole #61239 - Needs tree trimmed | High Pressure Sodium | 38.90515476000 | -77.00581203000
6/24/09 | 714551 | 410 | 7TH ST | NW | 6/26/09 | 60647 | 6M616 | (Light out) | DA 6-26-09 @ 338am T. Richards repaired pole #60647 DA 6-24-09 @1044pm T. Richards could not access light due to heavy traffic | High Pressure Sodium | 38.89512871000 | -77.02201224000
6/24/09 | 714550 | 0 | NEW YORK AVE | NW | 6/25/09 | 22947 | 2L030 | (Light out) | DA 6-25-09 @ 1211am R. Warren repaired pole #22947 | High Pressure Sodium | 38.90115976000 | -77.02723326000
6/24/09 | 714548 | 4202 | BENNING RD | NE | 6/25/09 | 73867DC | 73867 | (Light out) | DA 6-25-09 @ 417am T. Richards repaird pole #73867dc | High Pressure Sodium | 38.89298310000 | -76.94251439000
6/23/09 | 713806 | 1815 | 18TH ST | NW | 6/30/09 | 26750 | 2M107 | (Light out) | DA 6-25-09 @ 212am R. Warren repaired pole #26750 - T Base Door needs repaired \ STREET - street light on metal pole is out , 6-30-09 M.Craig---secured t-base door (sconnor) | High Pressure Sodium | 38.91477052000 | -77.04159278000
6/22/09 | 712875 | 2311 | 18TH ST | NW | 6/22/09 | 11409 | 1G496 | (Light off/on) | DA 6-22-09 @ 1030pm V. cooke repaired pole #11409 | High Pressure Sodium | 38.92009844000 | -77.04170982000
6/22/09 | 712842 | 2108 | 18TH ST | NW | 6/24/09 | 11413 | 1G506 | (Bridge light out) | DA 6-24-09 @ 1256am R. Warren pole #11413 light found on and working | High Pressure Sodium | 38.91831567000 | -77.04154601000
6/22/09 | 712815 | 900 | 3RD ST | SE | 7/22/09 | 67528 | 6A460 | (Light out) | DA 6-23-09 @ 311am T. richards repaired pole #67528 - needs tree trimmed | High Pressure Sodium | 38.87868199000 | -77.00198085000
6/22/09 | 712812 | 1952 | INDEPENDENCE AVE | SE | 6/22/09 | 63657 | 6M841 | (Light out) | DA 6-22-09 @ 1054pm T. Richards repaired pole #63657 | High Pressure Sodium | 38.88767159000 | -76.97678155000
6/22/09 | 712808 | 1063 | 3RD ST | NE | 6/24/09 | 61352 | 6S416 | (Light out) | DA 6-23-09 @ 113am T. richards pole #61352 N/C underground due to construction Paradigm constrution co. - phone #703-527-7500 | High Pressure Sodium | 38.90320663000 | -77.00197013000
6/22/09 | 712760 | 2108 | 18TH ST | NW | 6/23/09 | 11413 | 1G506 | (Light out) | DA 6-23-09 @ 120am V. Cooke repaired pole #11413 IN THE 2100 BLOCK 18TH ST NW | High Pressure Sodium | 38.91831567000 | -77.04154601000
6/18/09 | 711337 | 0 | WISCONSIN AVE | NW | 6/22/09 | 30145 | 3G056 | (Light out) | DA 622-09 @ 150am V. Cooke pole #30145 light found on and working SOUTHWEST CORNER OF INTERSECTION - | High Pressure Sodium | 38.92250517000 | -77.07302857000
6/18/09 | 711336 | 2336 | WISCONSIN AVE | NW | 6/22/09 | 30149 | 3G073 | (Light out) | DA 6-22-09 @ 145am V. Cooke pole #30149 light found on and working IMMEDIATELY NORTH OF 2323 WISCONSIN AVENUE NW - | High Pressure Sodium | 38.92085423000 | -77.07199482000
6/17/09 | 710521 | 709 | H ST | NW | 6/18/09 | 22630 | 2M424 | (Light out) | DA 6-17-09 @ 1141pm T. Richards repaired pole #22630 | High Pressure Sodium | 38.89990397000 | -77.02240296000
6/17/09 | 710627 | 100 | STODDERT PL | SE | 6/19/09 | 70028 | 74231 | (Light out) | DA 6-18-09 @ 1007pm T. richards pole #70028 - N/C underground FRONT - Light is out on metal pole | High Pressure Sodium | 38.88967004000 | -76.94839956000
6/16/09 | 708968 | 3000 | PENNSYLVANIA AVE | SE | 6/16/09 | 78561DC | 7E093DC | (Light out) | DA 6-15-09 @ 1139pm T. RRichards repaired pole #78561dc | High Pressure Sodium | 38.87074474000 | -76.96412983000
6/15/09 | 708945 | 3724 | GEORGIA AVE | NW | 6/16/09 | 4J357 | 4G248 | (Light out) | DA 6-16-09 @ 1050pm R. Warren repaired pole #4J357 DA 6-15-09 @ 1130pm R. Warren pole #4j357 Needs 400 powerdoor and TLP | High Pressure Sodium | 38.93749586000 | -77.02460026000
6/13/09 | 708700 | 711 | D ST | NW | 6/16/09 | 60088 | 2M325 | (Light out) | DA 6-1609 @ 1009pm T. Richards repaired pole #60088 - streetlight out on metal pole, would like to have it repaired. | High Pressure Sodium | 38.89485723000 | -77.02246234000
6/12/09 | 708070 | 1222 | 1ST ST | NE | 6/15/09 | 61244 | 6A275 | (Light out) | DA 6-15-09 @ 415am T. Richards pol #61244 light found on and working - POLE # 61244 IS NO LONGER FLUSH | High Pressure Sodium | 38.90676525000 | -77.00596728000
6/11/09 | 707288 | 0 | KENNEDY ST | NW | 6/14/09 | 4M081 | 4M081DC | (Light out) | DA 6-12-09 @ 121am R. WArren pole #4m081 N/C underground | High Pressure Sodium | 38.95634883000 | -77.02585493000
6/11/09 | 707230 | 715 | ANACOSTIA AVE | NE | 6/12/09 | 72359DC | 7A482 | (Light out) | DA 6-12-09 @ 337am T. Richards pole #72359dc power restored al on and working | High Pressure Sodium | 38.90218502000 | -76.95030078000
6/9/09 | 705653 | 0 | 23RD ST | NW | 6/11/09 | 28344 | 2M283 | (Light out) | DA 6-11-09 @ 118am K. Simmons repaired pole #28344 | High Pressure Sodium | 38.90148874000 | -77.05001185000
6/9/09 | 705644 | 711 | D ST | NW | 6/12/09 | 60088 | 2M325 | (Light out) | DA 6-11-09 @ 329am T. Richards pole #60088 light is on but has bad neturial underground refer to fault crew | High Pressure Sodium | 38.89485723000 | -77.02246234000
6/9/09 | 705643 | 410 | 7TH ST | NW | 6/11/09 | 60647 | 6M616 | (Light out) | DA 6-11-09 @ 319am T. Richards repaired pole #60647 | High Pressure Sodium | 38.89512871000 | -77.02201224000
6/9/09 | 705536 | 0000 | H ST | NE | 6/16/11 | 68252DC | 68252 | (Light out) |  | High Pressure Sodium | 38.90032915000 | -77.00287599000
6/9/09 | 705512 | 0000 | OVERLOOK AVE | SE | 2/2/12 | 81806 | 85793 | (Light out) | DA 6-9-09 @ 1011pm K. Simmons pole #81806 Defective teardrop fixture refer to ddot | High Pressure Sodium | 38.82907587000 | -77.01730772000
6/8/09 | 704697 | 2606 | BOWEN RD | SE | 6/9/09 | 81380DC | 8M044 | (Light out) | DA 6-9-09 @ 156am K Simmons repaired pole #81380dc | High Pressure Sodium | 38.85914186000 | -76.99291332000
6/8/09 | 704769 | 0 | FLORIDA AVE | NE | 6/25/09 | 54443 | 5M132 | (Light out) | - (6-25-09 G Edwards No problem found 100% complete) DA 6-11-09 @ 257am T. Richards light is on and working - Needs T base repaired 25 FEET AWAY FROM CORNER OF - pole # 54443, corroded base | High Pressure Sodium | 38.90877588000 | -77.00407804000
6/8/09 | 704768 | 100 | NEW YORK AVE | NE | 2/8/12 | 56753 | 5M130 | (Light out) | Pole is a Traffic Pole DA 6-11-09 @ 257am T. richards light is on and working - Needs T base repaired SW CORNER OF INTERSECTION - caller reports a streetlight with a corroded base | High Pressure Sodium | 38.90888813000 | -77.00500782000
6/6/09 | 704493 | 1231 | U ST | NW | 6/7/09 | 12573 | 1G531 | (Light out) | DA 6-7-09 @ 1055pm V. Cooke repaired ole #12573 FRONT - Street light out pole #12573 | High Pressure Sodium | 38.91709688000 | -77.02906097000
6/4/09 | 703153 | 301 | 4TH ST | SW | 6/5/09 | 21580 | 6L636 | (Light out) | DA 6-5-09 @ 340am R. Warren repaired pole #21580 | High Pressure Sodium | 38.88593815000 | -77.01743975000
6/4/09 | 703152 | 300 | D ST | SW | 6/5/09 | 21630 | 6L642 | (Light off/on) | DA 6-5-09 @ 330am R. Warren repaired pole #21630 | High Pressure Sodium | 38.88513805000 | -77.01701858000
6/4/09 | 703151 | 0 | 7TH ST | NW | 6/5/09 | 25651 | 6A827 | (Light out) | DA 6-5-09 @ 140am R. Warren repaired pole #25651 | High Pressure Sodium | 38.91214028000 | -77.02202436000
6/4/09 | 703148 | 525 | 9TH ST | NW | 6/5/09 | 22525 | 22522 | (Light out) | DA 6-5-09 @ 210am R. Warren repaired pole #22525 | High Pressure Sodium | 38.89645150000 | -77.02387620000
6/4/09 | 703148 | 525 | 9TH ST | NW | 6/5/09 | 22525 | 2L079 | (Light out) | DA 6-5-09 @ 210am R. Warren repaired pole #22525 | High Pressure Sodium | 38.89677792000 | -77.02387631000
6/4/09 | 703002 | 3310 | 15TH ST | NE | 6/4/09 | 51221DC | 5A117DC | (Light out) | DA 6-409 2 250am K. Simmons repaired pole #51221dc | Incandescent | 38.93137950000 | -76.98438250000
6/3/09 | 702300 | 0 | WISCONSIN AVE | NW | 6/8/09 | 30142 | 3G043 | (Light out) | DA 6-8-09 @ 100am V. Cooke repaired pole #30142 | High Pressure Sodium | 38.92372594000 | -77.07329890000
6/3/09 | 702291 | 1245 | H ST | NE | 6/4/09 | 62349 | 6S118 | (Light out) | DA 6-4-09 @ 422am T. Richards repaired pole #62349 | High Pressure Sodium | 38.90011568000 | -76.98878114000
6/3/09 | 702280 | 410 | 8TH ST | NW | 6/4/09 | 60659 | 2M372 | (Light out) | DA 6-4-09 @ 257am T. Richards repaired pole #60659 | High Pressure Sodium | 38.89515333000 | -77.02306415000
6/3/09 | 702279 | 601 | D ST | NW | 6/5/09 | 60094 | 6S600 | (Light out) | (vw 6-5-09 LR secured hanging pc) DA 6-4-09 @ 244am T. Richards repaired pole #60094 Needs hole drilled for photocell | High Pressure Sodium | 38.89486033000 | -77.02070899000
6/3/09 | 702278 | 775 | H ST | NE | 6/5/09 | 61991 | 6S197 | (Light out) | DA 6-4-09 @ 410am T. richards pole #61991 N/C underground | High Pressure Sodium | 38.90030060000 | -76.99586046000
6/3/09 | 702276 | 0 | H ST | NE | 6/5/09 | 62327 | 6S140 | (Light off/on) | DA 6-5-09 @ 1240am T. Richards pole #62327 light is on and working - checked pole last night and was also on - pole has new fixture and wiring may have gone out due to heavy rains, but light is on | High Pressure Sodium | 38.90029795000 | -76.98565875000
6/2/09 | 701518 | 3028 | BLADENSBURG RD | NE | 6/3/09 | 51232DC | 5A128DC | (Light out) | DA 6-03-09 @ 222am K. Simmons repaired pole #51232dc | High Pressure Sodium | 38.92838717000 | -76.96142018000
6/1/09 | 700661 | 3224 | 16TH ST | NW | 6/2/09 | 10115 | 1G359 | (Light out) | DA 6-02-09 @ 1240am K. Simmons repaired pole #10115 | High Pressure Sodium | 38.93159581000 | -77.03656398000
6/1/09 | 700660 | 1400 | PARK RD | NW | 6/2/09 | 12701 | 1G378 | (Light out) | DA 6-01-09 @ 1150pm K. Simmons pole #12701 N/C underground | High Pressure Sodium | 38.93092482000 | -77.03443295000
6/1/09 | 700659 | 1457 | PARK RD | NW | 6/2/09 | 12702 | 1G375 | (Light out) | DA 6-02-09 @ 1200am K. Simmons repaired pole #12702 | High Pressure Sodium | 38.93096473000 | -77.03479369000
6/1/09 | 700658 | 0 | IRVING ST | NW | 6/2/09 | 12738 | 1G044 | (Light out) | DA 6-02-09 @ 1220am K. Simmons pole #12738 light found on and working | High Pressure Sodium | 38.92871205000 | -77.03568647000
6/1/09 | 700691 | 0 | CHILLUM PL | NE | 6/2/09 | 4P514DC | 4U171 | (Light out) | DA 6-02-09 @ 1123pm R. Warren repaired pole #4p514dc - wooden pole 799409-3195 | High Pressure Sodium | 38.95916838000 | -77.00214355000
6/1/09 | 700570 | 1370 | H ST | NE | 6/1/09 | 62353 | 6S133 | (Light out) | DA 6-01-09 @ 1000pm T. Richards repaired pole #62353 | High Pressure Sodium | 38.90011788000 | -76.98594986000
6/1/09 | 700569 | 800 | 4TH ST | NW | 6/2/09 | 60448 | 6S459 | (Light off/on) | DA 6-02-09 @ 1221am T. Richards repaired pole #60448 | High Pressure Sodium | 38.90032749000 | -77.01608012000
6/1/09 | 700534 | 0 | IRVING ST | NW | 6/1/09 | 12738 | 1G044 | (Light out) | DA 5-31-09 @ 1147pm K. Soimmons repaired pole#12738 | High Pressure Sodium | 38.92871205000 | -77.03568647000
5/30/09 | 700433 | 2348 | WISCONSIN AVE | NW | 6/1/09 | 30165 | 3G072 | (Light out) | DA 5-31-09 @ 1050pm V. Cooke pole #30165 light found on and working 15 FEET NORTH OF THIS ADDRESS - | High Pressure Sodium | 38.92100387000 | -77.07184696000
5/29/09 | 699843 | 5516 | NANNIE HELEN BURROUGHS AVE | NE | 6/3/09 | 72651 | 7A184 | (Light out) | DA 6-01-09 @ 203am T. Richards pole #72651 N/C underground - street light on a metal pole is out | High Pressure Sodium | 38.89830423000 | -76.92065348000
5/29/09 | 699143 | 1135 | NEW JERSEY AVE | NW | 5/31/09 | 60744 | 6S259 | (Light out) | DA 5-31-09 @ 1050pm T. Richardsrepaired pole #60744 | High Pressure Sodium | 38.90457894000 | -77.01436787000
5/28/09 | 699847 | 0 | CAMDEN ST | SE | 6/1/09 | 74756DC | 7A070DC | (Light out) | DA 6-01-09 @ 237am T. Richards repaired pole #74756dc IT'S THE STREETLIGHT CLOSEST TO THE ALLEY. - BRANCH | High Pressure Sodium | 38.85947622000 | -76.95961031000
5/28/09 | 699093 | 0 | SOUTH DAKOTA AVE | NE | 6/1/09 | 50052DC | 50047 | (Light out) | DA 6-1-09 @ 1225am K. simmons repaired pole #50052dc | High Pressure Sodium | 38.95620340000 | -77.00164178000
5/28/09 | 699076 | 625 | D ST | SW | 2/2/12 | 21623 | 6A334 | (Light out) | (vw 5-29-09 I Paraway - REFER to Fault Crew No Current - pole in construction zone) | High Pressure Sodium | 38.88477726000 | -77.02020126000
5/28/09 | 699066 | 3327 | O ST | NW | 5/29/09 | 21103 | 2G165 | (Light out) | DA 5-28-09 @ 1105pm V. Cooke repaired pole #21103 - reconnected neturial | High Pressure Sodium | 38.90782993000 | -77.06720414000
5/28/09 | 699061 | 0 | WASHINGTON CIR | NW | 5/29/09 | 28509 | 2M286 | (Light out) | DA 5-29-09 @ 320am R. Warren repaired pole #28509 | High Pressure Sodium | 38.90199338000 | -77.04975164000
5/28/09 | 699042 | 1919 | 18TH ST | NW | 5/29/09 | 26747 | 2M093 | (Light out) | DA 5-29-09 @ 140am R. Warren repaired pole #26747 | High Pressure Sodium | 38.91616351000 | -77.04156419000
5/28/09 | 699040 | 1826 | 18TH ST | NW | 6/1/09 | 26780 | 2M106 | (Light off/on) | DA 6-01-09 @ 205am R. Warren repaired pole #26780 DA 5-29-09 @ 130am R. Warren installed 400 hps lamp and powerdoor pole #26780 - Needs wire ran (unable to complete due to weather) | High Pressure Sodium | 38.91492300000 | -77.04174945000
5/28/09 | 699039 | 1742 | 18TH ST | NW | 5/29/09 | 26778 | 2M116 | (Light out) | DA 5-28-09 @ 1141pm R. Warren repaired pole #26778 | High Pressure Sodium | 38.91399493000 | -77.04172986000
5/28/09 | 699021 | 0 | NEW YORK AVE | NW | 5/29/09 | 22947 | 2L030 | (Light out) | DA 5-29-09 @ 240am T. Richards repaired pole #22947 - tightened connections | High Pressure Sodium | 38.90115976000 | -77.02723326000
5/28/09 | 699018 | 0 | 7TH ST | NW | 5/29/09 | 22455 | 6M667 | (Light out) | DA 5-29-09 @ 400am T. Richards repasired pol #22455 | High Pressure Sodium | 38.90101301000 | -77.02181903000
5/28/09 | 699122 | 1200 | 18TH ST | NW | 6/1/09 | 24761 | 2U532 | (Light out) | DA 6-01-09 @ 323am R. Warren repaired pole #24761 ACF 1200 18TH STREET WESTSIDE OF LONGFELLOW PARK - | High Pressure Sodium | 38.90579457000 | -77.04160331000
5/28/09 | 698242 | 1370 | H ST | NE | 5/28/09 | 62353 | 6S133 | (Light out) | DA 5-28-09 @ 1224am T. Richards repaired pole #62353 | High Pressure Sodium | 38.90011788000 | -76.98594986000
5/28/09 | 699112 | 0 | WILTBERGER ST | NW | 5/31/09 | 29509 | 1M010 | (Light out) | DA 5-31-09 @ 1105pm T. Richards pole #29509 light found on and working FRONT - street light is out it's a metal pole | High Pressure Sodium | 38.91554664000 | -77.02082826000
5/27/09 | 698179 | 1309 | 11TH ST | NW | 5/28/09 | 25258 | 2M239 | (Light out) | DA 5-27-09 @ 1106pm T. Richards repaired pole #25258 THE 1300 BLOCK 11TH STREET N.W. | High Pressure Sodium | 38.90777791000 | -77.02692516000
5/27/09 | 697448 | 410 | 7TH ST | NW | 5/27/09 | 60647 | 6M616 | (Light out) | PC installed 5/27 - L Roberto DA 5-26-09 @ 1149pm T. Richards repaired pole #60647 Needs hole drilled for photocell | High Pressure Sodium | 38.89512871000 | -77.02201224000
5/27/09 | 697446 | 711 | D ST | NW | 5/26/09 | 60088 | 2M325 | (Light out) | DA 526-09 @ 1125pm T. Richards repaired loose photocell wire pole #60088 | High Pressure Sodium | 38.89485723000 | -77.02246234000
5/26/09 | 697424 | 400 | RHODE ISLAND AVE | NW | 5/27/09 | 59987 | 5A178 | (Light out) | DA 5-27-09 @ 150pm K. Simmons repaired pole #59987(checked 59986) | High Pressure Sodium | 38.91400893000 | -77.01743154000
5/21/09 | 695874 | 1702 | SHEPHERD ST | NW | 5/29/09 | 4F232DC | 4F231DC | (Light out) | (vw 5-28-09 L Roberto TLP & 250w hps lamp) DA 5-27-09 @ 345am Pole #4F232dc needs ladder | High Pressure Sodium | 38.93971259000 | -77.03814519000
5/21/09 | 695814 | 901 | 9TH ST | NW | 5/21/09 | 22987 | 2G988 | (Light out) | DA 5-21-09 @ 355am H. Darden repaired pole #22987 | High Pressure Sodium | 38.90092176000 | -77.02415354000
5/20/09 | 695082 | 800 | 8TH ST | NW | 5/21/09 | 22969 | 2M383 | (Light out) | DA 5-21-09 @ 1210am H. Darden repaired pole #22969 | High Pressure Sodium | 38.90023907000 | -77.02300991000
5/20/09 | 694459 | 3310 | 15TH ST | NE | 5/20/09 | 51221DC | 5A117DC | (Light out) | DA 5-20-09 @ 111am K, Simmons repaired pole #51221dc | Incandescent | 38.93137950000 | -76.98438250000
5/19/09 | 694209 | 1520 | ALABAMA AVE | SE | 5/21/09 | 81749 | 88026 | (Light out) | DA 5-21-09 @ 336am K. Simmons pole #81749 light found on and in working condition BETWEEN 445 AND 449 MELLON ST. SE - There is a street lights burnt out on a metal pole. | High Pressure Sodium | 38.84689369000 | -76.98188151000
5/18/09 | 693166 | 1808 | HOBAN RD | NW | 5/18/09 | 35823DC | 35823 | (Light out) | DA 5-18-09 @ 210am V. Cooke repaired pole #35823dc | Incandescent | 38.91448031000 | -77.08497341000
5/18/09 | 693164 | 4520 | HOBAN RD | NW | 5/18/09 | 35822DC | 35822 | (Light out) | DA 5-18-09 @ 205am V. Cooke repaired pole #35822dc | Incandescent | 38.91433459000 | -77.08526855000
5/18/09 | 693125 | 812 | 7TH ST | NW | 5/18/09 | 22419 | 6M668 | (Light out) | DA 5-18-09 @ 1230am H. Darden repaired pole #22419 | High Pressure Sodium | 38.90058335000 | -77.02201480000
5/17/09 | 693081 | 1525 | TUBMAN RD | SE | 5/19/09 | 81743 | 88020 | (Light out) | DA 5-19-09 @ 1258am K. Simmons repaired pole #81743 | High Pressure Sodium | 38.84806394000 | -76.98142985000
5/15/09 | 691679 | 1404 | H ST | NE | 5/15/09 | 62326 | 6S139 | (Light out) | DA 5-15-09 @ 132am T. richards repaired pole #62336 | High Pressure Sodium | 38.90029477000 | -76.98535817000
5/15/09 | 691678 | 1370 | H ST | NE | 5/15/09 | 62353 | 6S133 | (Light out) | DA 5-15-09 @ 123am T. richards repaired pole #62353 | High Pressure Sodium | 38.90011788000 | -76.98594986000
5/14/09 | 691654 | 900 | NEW JERSEY AVE | SE | 2/6/12 | 67472 | 6A060 | (Light out) | DA 5-14-09 @ 1125pm T. Richards pole #67472 N/ C underground | High Pressure Sodium | 38.87881747000 | -77.00509329000
5/14/09 | 691844 | 3222 | O ST | NW | 5/17/09 | 21111 | 2G180 | (Light out) | DA 5-17-09 @ 1040pm H. Darden repaired pole #21111 IN THE FRONT OF 3226 O ST., NW - STREET LIGHT ON METAL POLE NEED REPLACING | High Pressure Sodium | 38.90779366000 | -77.06456455000
5/14/09 | 691612 | 509 | 7TH ST | NW | 5/15/09 | 22431 | 6M628 | (Light out) | DA 5-14-09 @ 1130pm H. Darden repaired pole #22431 | High Pressure Sodium | 38.89648966000 | -77.02200839000
5/14/09 | 691597 | 1447 | LAWRENCE ST | NE | 5/14/09 | 52489DC | 5A160DC | (Light out) | DA 5-14-09 @ 424am K. simmons repaired pole #52489dc | High Pressure Sodium | 38.93181874000 | -76.98481663000
5/14/09 | 690988 | 2 | WESTMORELAND CIR | NW |  | 34380 | 3M038 | (Light out) | Refer to DC 5-14-09 Defective MV fixture. K. Greenfield completed on 5-15-09 Made splices in the t-base and manhole. DA 5-14-09 @ 1247am V. Cooke poles 34380 nad 3F247 - N/C underground | Mercury Vapor | 38.94941039000 | -77.10097492000
5/14/09 | 690949 | 2001 | 37TH ST | SE | 5/14/09 | 74793DC | 7A082DC | (Light out) | DA 5-13-09 @ 1108pm T. Richards repaired pole #74793dc - reattached split bolt working phase | High Pressure Sodium | 38.86459154000 | -76.95373421000
5/13/09 | 690939 | 0 | FLORIDA AVE | NE | 5/13/09 | 62313 | 5M114 | (Light out) | DA 5-13-09 @ 1044pm k. Simmons repaired pole #62313 | High Pressure Sodium | 38.90860897000 | -77.00417478000
5/13/09 | 690937 | 1400 | FLORIDA AVE | NE | 5/15/09 | 54410 | 5M289 | (Light out) | DA 2-13-09 @ 1000pm K. Simmons pole #54410 N/C underground | High Pressure Sodium | 38.90051673000 | -76.98498235000
5/13/09 | 690976 | 1312 | W ST | NW | 5/14/09 | 11807 | 1G575 | (Light out) | DA 5-14-09 @ 1030pm H. Darden repaired pole #11807 STREET SIDE - | High Pressure Sodium | 38.91924506000 | -77.03039147000
5/13/09 | 690974 | 5109 | NANNIE HELEN BURROUGHS AVE | NE |  | 71270 | 71270DC | (Light out) | DA 6-8-09 @ 1100pm T. Richards lights in 5500 block are on,but poles 71270, 71269, 2 poles 72657 (same id) are still N/C Nannie hellen Burroughs and division street are still N/C DA 5-14-09 @ 1020pm T. Richards poles 71270, 71269, 72657, 79661,79660, 7 | High Pressure Sodium | 38.89827347000 | -76.92679095000
5/13/09 | 690967 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 6/3/09 | 71270 | 71270DC | (Light out) | DA 5-14-09 @ 1020pm T. Richards poles 71270, 71269, 72657, 79661,79660, 72651, 72650, 72649, and 72648 N/C underground- streetlights' bulbs are needed, it is very dark at night dangerous situation. Apparently problem was called in but not resolved | High Pressure Sodium | 38.89827347000 | -76.92679095000
5/13/09 | 690969 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 6/3/09 | 71270 | 71270DC | (Light out) | DA 5-14-09 @ 1020pm T. Richards poles 71270, 71269, 72657, 79661,79660, 72651, 72650, 72649, and 72648 N/C underground ' 58 STR. AND 55 ST. NE - THERE IS A SEVERAL STREET IS OUT. NEE TO BE FIX IT 5500.00 BLOCK UP TO 5800.00 ENTIRE BLOCK | High Pressure Sodium | 38.89827347000 | -76.92679095000
5/12/09 | 690040 | 0 | LANG PL | NE | 5/12/09 | 59561 | 5B255 | (Light out) | DA 5-12-09 @ 1008pm K. Simmons repaired pole #59561 | High Pressure Sodium | 38.90433596000 | -76.98020495000
5/11/09 | 689063 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 5/15/09 | 71269 | 7A201 | (Light out) | DA 5-11-09 @ 1011pm T. Richards pole #71269 N/C underground | High Pressure Sodium | 38.89826963000 | -76.92624974000
5/11/09 | 689062 | 5109 | NANNIE HELEN BURROUGHS AVE | NE | 5/15/09 | 71270 | 71270DC | (Light out) | DA 5-11-09 @ 1011pm T. Richards pole #71270 N/C underground | High Pressure Sodium | 38.89827347000 | -76.92679095000
5/11/09 | 689037 | 1701 | M ST | NW | 5/12/09 | 26411 | 2U750 | (Light off/on) | DA 5-12-09 @ 245am H. Darden repaired pole #26411 | High Pressure Sodium | 38.90572284000 | -77.03887684000
5/11/09 | 689032 | 1262 | NEW HAMPSHIRE AVE | NW | 5/16/09 | 23852 | 2G757 | (Light out) | DA 5-12-09 @ 310am H. Darden pole #23852 N/C underground | High Pressure Sodium | 38.90669938000 | -77.04633627000
5/9/09 | 688894 | 2838 | BLADENSBURG RD | NE | 5/12/09 | 50096 | 5A082 | (Light out) | DA 5-12-09 @ 159am K. Simmons repaired pole #50096 IN THE REAR OF 5180 EASTERN AVE., NE - Light on metal pole need replacing asap | High Pressure Sodium | 38.92653880000 | -76.96331853000
5/8/09 | 688145 | 5600 | 3RD ST | NE | 5/11/09 | 4P471DC | 4U158 | (Light out) | (vw 5-11-09 Paraway/Barclay repaired pole) | High Pressure Sodium | 38.95858464000 | -77.00292664000
5/7/09 | 687322 | 601 | D ST | NW | 5/11/09 | 60501 | 6S591 | (Light out) | DA 5-10-09 @ 1134pm T. richards repaired pole #60501 | High Pressure Sodium | 38.89511910000 | -77.02001367000
5/7/09 | 687321 | 1101 | 14TH ST | NW | 5/8/09 | 27351 | 2M419 | (Light out) | DA 5-08-09 @ 240am H. Darden repaired pole #27351 | High Pressure Sodium | 38.90399643000 | -77.03208460000
5/7/09 | 687318 | 1231 | 11TH ST | NW | 5/8/09 | 25260 | 2M233 | (Light out) | DA 5-08-09 @ 250am H. Darden repaired pole #25260 | High Pressure Sodium | 38.90681635000 | -77.02692053000
5/7/09 | 687316 | 0 | I ST | NW | 5/8/09 | 22487 | 2G985 | (Light out) | DA 5-08-9 @ 320am H. Darden repaired pole #22487 | High Pressure Sodium | 38.90081220000 | -77.02379981000
5/7/09 | 687315 | 900 | 7TH ST | NW | 5/8/09 | 22462 | 6A084 | (Light out) | DA 5-08-09 @ 330am H. Darden repaired pole #22462 | High Pressure Sodium | 38.90225041000 | -77.02177737000
5/6/09 | 686572 | 100 | FLORIDA AVE | NE | 5/8/09 | 56988 | 5M138 | (Light out) | DA 5-08-09 @ 105am K. Simmons repaired pole #56988 THE STREET LIGHT IS SITUATED ON THE CORNER BESIDE 1500 ECKINGTON PLACE ACROSS FROM WENDYS. - | High Pressure Sodium | 38.90936280000 | -77.00549051000
5/6/09 | 686460 | 0 | 23RD ST | NW | 5/6/09 | 28344 | 2M283 | (Light out) | DA 5-06-09 @ 440am H. Darden repaired pole #28344 | High Pressure Sodium | 38.90148874000 | -77.05001185000
5/5/09 | 685623 | 0 | C ST | SW | 5/5/09 | 21787 | 6A355 | (Light out) | DA 5-05-09 @ 345am H. Darden repaired pole #21787 | High Pressure Sodium | 38.88598751000 | -77.01461550000
5/5/09 | 685607 | 400 | VIRGINIA AVE | SW | 5/5/09 | 21626 | 6L715 | (Light out) | DA 5-05-09 @ 200am H. Darden repaired pole #21628 | High Pressure Sodium | 38.88471591000 | -77.01896800000
5/5/09 | 685603 | 1524 | 18TH ST | NW | 5/5/09 | 26336 | 2M161 | (Light out) | DA 5-04-09 2 1115pm H. Darden repaired pole #26336 | High Pressure Sodium | 38.91030730000 | -77.04160728000
5/4/09 | 684832 | 0 | SOUTH CAPITOL ST | SE | 5/5/09 | 82046 | 8M063 | (Light out) | DA 5-04-09 @ 1156pm T. Richards repaired pole #82046 | High Pressure Sodium | 38.86082577000 | -77.00320587000
5/4/09 | 684824 | 0 | ANACOSTIA FWY | SE | 5/4/09 | 79491 | 7A160 | (Light out) | DA 5-04-09 @ 1051pm T. Richards repaired pole #79491 | High Pressure Sodium | 38.88928656000 | -76.95990942000
5/4/09 | 684804 | 0 | MARTIN LUTHER KING JR AVE | SE | 5/5/09 | 81015 | 8L861 | (Light out) | DA 5-04-09 @ 1131pm T. richards pole #81015 N/C underground - Bad voltage | High Pressure Sodium | 38.86901189000 | -76.98845490000
5/3/09 | 684732 | 600 | MICHIGAN AVE | NE | 5/3/09 | 53649DC | 5U721 | (Light out) | DA 5-03-09 @ 1115pm K. Simmons repaired pole #53649dc | High Pressure Sodium | 38.93248081000 | -76.99750323000
5/3/09 | 684727 | 3861 | PENNSYLVANIA AVE | SE | 5/3/09 | 78581DC | 7E009 | (Light out) | DA 5-03-09 @ 1012pm k. Simmons repaired pole #78581dc | High Pressure Sodium | 38.86516778000 | -76.95003984000
4/30/09 | 683051 | 3128 | SHERMAN AVE | NW | 5/1/09 | 12867 | 1L264 | (Light out) | DA 4-30-09 @ 1010pm H. darden repaired pole #12867 | High Pressure Sodium | 38.92970603000 | -77.02645797000
4/29/09 | 683222 | 0 | 7TH ST | NW | 5/1/09 | 25703 | 6A818 | (Light out) | FRONT - street lights are out one side is flashing and one side are out they are metal pole 5-1-09 D.Smith---repaired(sconnor) | High Pressure Sodium | 38.91121698000 | -77.02181678000
4/29/09 | 682358 | 1826 | CALVERT ST | NW | 2/7/12 | 10729 | 1A013 | (Light out) | DA 4-30-09 @ 330am V. Cooke pole #10729(traffic pole) N/C underground | High Pressure Sodium | 38.92339148000 | -77.04377813000
4/29/09 | 682357 | 1826 | CALVERT ST | NW | 2/7/12 | 11197 | 1A003 | (Light out) | DA 4-30-09 @ 335am V. Cooke pole #11197(traffic pole ) N/C underground | High Pressure Sodium | 38.92316276000 | -77.04378689000
4/29/09 | 682339 | 3400 | SHERMAN AVE | NW | 4/29/09 | 13072 | 1L293 | (Light out) | DA 4-29-09 @ 355am V. Cooke repaired pole #13072 | High Pressure Sodium | 38.93200019000 | -77.02660138000
4/28/09 | 681625 | 0 | CHILLUM PL | NE | 4/30/09 | 4P469DC | 4U154 | (Light out) | DA 4-30-09 @ 155am R. Warren pole #4p469dc light found on and working | High Pressure Sodium | 38.95926271000 | -77.00275729000
4/27/09 | 680892 | 3901 | PENNSYLVANIA AVE | SE | 4/27/09 | 78522DC | 7E143 | (Light out) | DA 4-27-09 @ 1038pm K. simmons repaired pole #78522dc | High Pressure Sodium | 38.86491145000 | -76.94983912000
4/27/09 | 680885 | 0 | 24TH ST | NW | 4/30/09 | 24804 | 2G664 | (Light off/on) | DA 4-30-09 @ 250am H. Darden repaired pole #24804 | High Pressure Sodium | 38.90272824000 | -77.05133683000
4/27/09 | 680871 | 418 | 7TH ST | NW | 4/28/09 | 60648 | 6M622 | (Light out) | (VW 4-28-09 M Craig reinstalled NWP in their proper hole) DA 4-28-09 @ 104am T. Richards repaired pole #60648 - Needs hole drilled for photocell | High Pressure Sodium | 38.89553430000 | -77.02201303000
4/27/09 | 680870 | 420 | 7TH ST | NW | 4/28/09 | 60640 | 6M627 | (Light off/on) | DA 4-28-09 @ 112am T. Richards repaired pole #60640 | High Pressure Sodium | 38.89567249000 | -77.02181889000
4/27/09 | 680856 | 2 | L ST | NE | 5/1/09 | 61201 | 6A240 | (Light out) | DA 4-28-09 @ 210am T. Richards pole #61201 N/C underground - Traffic pole | High Pressure Sodium | 38.90378899000 | -77.00858856000
4/27/09 | 680853 | 0 | FLORIDA AVE | NE | 4/28/09 | 62313 | 5M114 | (Light out) | DA 4-28-09 @ 229am T. Richards repaired loose connection in powerdoor - pole #62313 | High Pressure Sodium | 38.90860897000 | -77.00417478000
4/27/09 | 680839 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 4/27/09 | 71294DC | 7A226 | (No Current to Over Head) | (VW 4-27-09 K Greenfield inst 400ft #6 triplex cable on poles# 71294, 71293 & 71291) | High Pressure Sodium | 38.89882951000 | -76.93342319000
4/27/09 | 680829 | 400 | VIRGINIA AVE | SW | 4/29/09 | 21626 | 6L715 | (Light out) | DA 4-29-09 @ 335am H. Darden repaired pole #21626 | High Pressure Sodium | 38.88471591000 | -77.01896800000
4/26/09 | 680770 | 1701 | M ST | NW | 4/28/09 | 26411 | 2U750 | (Light out) | DA 4-27-09 @ 1115pm H. Darden repaired pole #26411 | High Pressure Sodium | 38.90572284000 | -77.03887684000
4/26/09 | 680760 | 0 | O ST | NW | 4/29/09 | 24475 | 2G771 | (Light out) | DA 4-29-09 @ 1225am H. Darden repaired pole #24475 | High Pressure Sodium | 38.90841495000 | -77.04472917000
4/24/09 | 679917 | 3430 | PENNSYLVANIA AVE | SE | 4/24/09 | 78534DC | 7E125DC | (Light out) | DA 4-24-09 @ 345am R. Warren repaired pole #78534dc | High Pressure Sodium | 38.86695624000 | -76.95485118000
4/24/09 | 679916 | 3400 | PENNSYLVANIA AVE | SE | 4/24/09 | 78537DC | 7E122DC | (Light out) | DA -24-09 @ 345am R. Warren repaired pole #78537dc | High Pressure Sodium | 38.86734823000 | -76.95581654000
4/24/09 | 679901 | 3211 | PENNSYLVANIA AVE | SE | 4/24/09 | 78548DC | 7E108 | (Light out) | DA 4-24-09 @ 130am R. Warren repaired pole #78548dc | High Pressure Sodium | 38.86886291000 | -76.95955716000
4/24/09 | 679666 | 327 | 7TH ST | SE | 4/24/09 | 64333 | 6A401 | (Light out) | DA 4-24-09 @ 104am T. Richards repaired pole #64333 | High Pressure Sodium | 38.88539659000 | -76.99624971000
4/22/09 | 678253 | 0 | H ST | NE | 4/22/09 | 62345 | 6S103 | (Light out) | DA 4-22-09 T. Richards repaired pole #62345 | High Pressure Sodium | 38.90012051000 | -76.99138683000
4/22/09 | 678239 | 0 | LOUGHBORO RD | NW | 4/24/09 | 34481 | 3M001 | (Light out) | DA 4-24-09 @ 220am V. Cooke pole #34481 light found on and working | High Pressure Sodium | 38.93586277000 | -77.10634398000
4/22/09 | 678237 | 3144 | PENNSYLVANIA AVE | SE | 4/22/09 | 78554DC | 7E101DC | (Light out) | DA 4-22-09 @ 425am R. Warren repaired pole #78554dc | High Pressure Sodium | 38.86981292000 | -76.96183892000
4/21/09 | 677404 | 600 | E ST | NW | 4/27/09 | 60186 | 2M339 | (Light out) | DA 4-21-09 @ 1045pm H. Darden repaired pole tag missing - needs screws in globe 4-22-09 M.Brewer---secured globe/already had screws they just needed to be tighten(sconnor) 4-24-09 S.Manning---install tag#60186 & re-gps pole for x,y coordinates(sconnor | High Pressure Sodium | 38.89605294000 | -77.02062808000
4/21/09 | 677368 | 0 | DALECARLIA PKY | NW | 4/24/09 | 34480 | 3M002 | (Light out) | DA 4-22-09 @ 1125pm V. Cooke pole #34480 broken neturial underground refer to fault crew | High Pressure Sodium | 38.93606261000 | -77.10611312000
4/21/09 | 677367 | 2 | WESTMORELAND CIR | NW | 4/22/09 | 34380 | 3M038 | (Light out) | DA 4-22-09 @ 330am V. Cooke repaired pole #34380 | Mercury Vapor | 38.94941039000 | -77.10097492000
4/21/09 | 677425 | 1112 | Q ST | NW | 4/22/09 | 29306DC | 2U047DC | (Light out) | DA 4-22-09 @ 1048pm H. Darden repaired pole #29306dc ALLEY - wooden pole alley light out 1 week, req imm repair | Incandescent | 38.91083084000 | -77.02756095000
4/21/09 | 677282 | 3817 | GEORGIA AVE | NW | 4/21/09 | 4J341 | 4G253 | (Light out) | DA 4-21-09 @ 125am R. Warren repaired pole #4J341 | High Pressure Sodium | 38.93827040000 | -77.02448591000
4/20/09 | 676676 | 214 | L ST | NE | 4/21/09 | 61364 | 6B081 | (Light out) | DA 4-21-09 @ 252am K. Simmons repaired pole #61364 | High Pressure Sodium | 38.90368595000 | -77.00276993000
4/20/09 | 676673 | 443 | I ST | NW | 4/24/09 | 61060DC | 6A739 | (Light out) | DA 4-20-09 @ 1141pm K. Simmons pole #61060dc no neturial underground | High Pressure Sodium | 38.90185387000 | -77.01800134000
4/20/09 | 676672 | 902 | 4TH ST | NW | 4/21/09 | 60425 | 6S494 | (Light out) | (vw 4-21-09 M Craig repaired pole) DA -4-20-09 @ 1133pm K. Simmons repaired pole #60425 -- Needs (1) elephant ear | High Pressure Sodium | 38.90179606000 | -77.01624923000
4/20/09 | 676671 | 504 | K ST | NW | 4/20/09 | 60470 | 6A104 | (Light out) | DA 4-20-09 @ 1055pm K. Simmons repaired pole #60470 | High Pressure Sodium | 38.90245334000 | -77.01925493000
4/20/09 | 676608 | 0 | 14TH ST | NW | 4/20/09 | 12758 | 1G065 | (Light out) | DA 4-20-09 @ 155am K./ Simmons repaired pole #12758 and repaired wire in powerdoor | High Pressure Sodium | 38.93048194000 | -77.03261694000
4/19/09 | 676569 | 3128 | SHERMAN AVE | NW | 4/19/09 | 12867 | 1L264 | (Light out) | DA 4-19-09 @ 1058pm K. Simmons repaired pole #12867 | High Pressure Sodium | 38.92970603000 | -77.02645797000
4/19/09 | 676547 | 2445 | 18TH ST | NW | 4/20/09 | 11407 | 1G482 | (Light out) | DA 4-20-09 @ 1242am K. Simmons repaired pole #11407 | High Pressure Sodium | 38.92173293000 | -77.04225784000
4/17/09 | 675508 | 0 | NAYLOR RD | SE | 5/4/09 | 79134DC | 7S070DC | (Light out) | DA 4-20-09 @ 1242am T. Richards poles 79134dc, 83431dc, 83432dc,83433dc, and 83434dc N/ C to overhead INTERSECTION - all lights at this intersection are out | High Pressure Sodium | 38.85198614000 | -76.96224489000
4/17/09 | 675503 | 1242 | 13TH ST | SE | 4/30/09 | 64460 | 64460DC | (Light out) | (vw 4-29-09 G Edwards 2- 5-A-Alley pole/w100hps fix 1-70hps fix 70'#10 cbl on both poles# 64460 &64456) DA 4-20-09 @ 251am T. Richards 2 poles have been hit and damaged pole #64460 and 64456 light is on and working but poles are damaged ALLEY - me | High Pressure Sodium | 38.88645072000 | -76.98879959000
4/15/09 | 674777 | 0 | ANACOSTIA FWY | SE | 4/17/09 | 79482 | 7A151 | (Light out) | DA 4-16-09 @ 1118pm T. Richards pole #79482 light found on and working | High Pressure Sodium | 38.88927741000 | -76.95876088000
4/15/09 | 674710 | 1400 | 17TH ST | NW | 4/16/09 | 26729 | 2M081 | (Light out) | DA 4-16-09 @ 1245am H. Darden repaired pole #26729 | High Pressure Sodium | 38.90872626000 | -77.03858078000
4/15/09 | 674708 | 206 | RHODE ISLAND AVE | NW | 4/15/09 | 59996 | 5A188 | (Light out) | DA 4-15-09 @ 424am K. Simmons repaired pole #59996 | Incandescent | 38.91473859000 | -77.01463730000
4/14/09 | 673965 | 4121 | 9TH ST | NW | 4/15/09 | 4J792 | 4G328 | (Light out) | DA 4-15-09 @ 131am R. Warren repaired pole #4J792 | High Pressure Sodium | 38.94134498000 | -77.02510288000
4/13/09 | 673136 | 3901 | PENNSYLVANIA AVE | SE | 4/13/09 | 78525DC | 7E135DC | (Light out) | DA 4-13-09 @ 1003pm K. Simmons repaired pole #78525dc | High Pressure Sodium | 38.86569632000 | -76.95176682000
4/12/09 | 672978 | 0 | L ST | NE | 4/15/09 | 61206 | 6S237 | (Light out) | 4-13-09 D.Dixon---under construction by B.Frank Joy Inc.(sconnor) | High Pressure Sodium | 38.90378817000 | -77.00651378000
4/10/09 | 672281 | 0 | K ST | SE | 4/15/09 | 67657 | 6B470 | (Light out) | (vw 4-15-09 M Craig repaired pole) DA 4-13-09 @ 402am T. Richards light is on and worrking pole tag missing -- needs T Base door FRONT INTERSECTION - Caller reporting streetlight out on metal pole. The base of the streetllight has no door. | High Pressure Sodium | 38.87835831000 | -77.00020892000
4/10/09 | 672202 | 0 | DALECARLIA PKY | NW | 4/13/09 | 34480 | 3M002 | (Light out) | DA 4-10-09 @ 1235am V. Cooke pole #34480 N/C underground | High Pressure Sodium | 38.93606261000 | -77.10611312000
4/9/09 | 671549 | 1121 | 1ST ST | NW |  | 60856 | 6S269 | (Light out) | DA 4-13-09 @ 319am T. Richards pole #60856 N/C underground - due to construction in area Forester Construction co, No phone # avalible 1100 BLOCK OF FIRST STREET NW - caller request a streetlight is out | High Pressure Sodium | 38.90455577000 | -77.01223195000
4/9/09 | 670700 | 3848 | SOUTH CAPITOL ST | SE | 4/10/09 | 85647 | 8M006 | (Light off/on) | DA 4-9-09 @ 1131pm T. Richards repaired pole #85647 | High Pressure Sodium | 38.83413920000 | -77.00815861000
4/8/09 | 670597 | 650 | MASSACHUSETTS AVE | NW | 4/8/09 | 22465 | 6A979 | (Light out) | DA 4-8-09 @ 300am H. Darden repaired pole #22465 | High Pressure Sodium | 38.90204075000 | -77.02130668000
4/8/09 | 670585 | 0 | MARTIN LUTHER KING JR AVE | SE | 4/21/09 | 81015 | 8L861 | (Light out) | DA 4-10-09 @ 350am T. Richards request for MOT DA 4-9-09 @ 1240am H. Darden - Request for Map 4-13-09 D.Dixon---No current at base(sconnor) | High Pressure Sodium | 38.86901189000 | -76.98845490000
4/8/09 | 669858 | 1400 | 17TH ST | NW | 4/8/09 | 26729 | 2M081 | (Light out) | DA -7-09 @ 1120pm H. Darden repaired pole #26729 | High Pressure Sodium | 38.90872626000 | -77.03858078000
4/7/09 | 669762 | 0 | KANSAS AVE | NW | 4/8/09 | 4K568 | 4G321 | (Light out) | DA 4-8-09 @ 155am R. Warren repaired pole #4k568 -- adjusted photocell | High Pressure Sodium | 38.94326049000 | -77.02502562000
4/7/09 | 669735 | 1735 | 17TH ST | NW | 4/7/09 | 26701 | 2M036 | (Light out) | DA 4-7-09 @ 220am H. Darden repaired pole #26701 | High Pressure Sodium | 38.91375043000 | -77.03840149000
4/6/09 | 668896 | 3458 | PENNSYLVANIA AVE | SE | 4/7/09 | 78531DC | 7E128DC | (Light out) | DA 4-7-09 @ 419am T. Richards repaired pole #78531dc | High Pressure Sodium | 38.86657755000 | -76.95392452000
4/6/09 | 668918 | 1735 | 17TH ST | NW | 4/7/09 | 26701 | 2M036 | (Light out) | DA 4-7-09 @ 1055pm H. Darden pole #26701 previously repaired on 4-6-09 using 250 hps kit and watchmen photocell refer to wo #669735 FRONT - caller req to have streetlight repaired #26701 | High Pressure Sodium | 38.91375043000 | -77.03840149000
4/6/09 | 668895 | 2811 | PENNSYLVANIA AVE | SE | 4/6/09 | 78570DC | 7E083DC | (Light out) | DA 4-6-09 @ 1115pm T. richards repaired pole #78570dc | High Pressure Sodium | 38.87218747000 | -76.96768794000
4/6/09 | 668884 | 623 | KENNEDY ST | NW | 4/7/09 | 4M069 | 4M069DC | (Light out) | DA 4-7-09 @ 106am R. Warren repaired pole #4m069 | High Pressure Sodium | 38.95646426000 | -77.02185855000
4/6/09 | 668849 | 410 | 7TH ST | NW | 4/6/09 | 60647 | 6M616 | (Light out) | DA 4-6-09 @ 200am H. Darden repaired pole #60647 | High Pressure Sodium | 38.89512871000 | -77.02201224000
4/5/09 | 668834 | 0 | ALLISON ST | NW | 4/7/09 | 4K101DC | 4U136DC | (Light off/on) | DA 4-6-09 @ 1115pm R. Warren repaired pole #4k101dc | High Pressure Sodium | 38.94511734000 | -77.02981962000
4/3/09 | 668082 | 1111 | NORTH CAPITOL ST | NW | 4/6/09 | 60045 | 6A237 | (Light out) | DA 4-5-09 @ 1115pm H. Darden repaired pole #60045 POLE IS LOCATED ON THE ODD SIDE OF THE STREET. - | High Pressure Sodium | 38.90432536000 | -77.00893358000
4/3/09 | 668077 | 100 | FLORIDA AVE | NE | 4/5/09 | 56989 | 5M139 | (Light out) | DA 4-5-09 @ 1048pm K. Simmons repaired pole #56989 -- poles 56988 and 56990 (ok )POLE IS LOCATED ON THE EVEN SIDE OF FLORIDA AVE NE. - 1ST | High Pressure Sodium | 38.90947523000 | -77.00574268000
4/3/09 | 668075 | 2 | L ST | NE | 4/10/09 | 61201 | 6A240 | (Light out) | (VW 4-10-09 L Roberto repaired pole) DA 4-5-09 @ 1050pm H. Darden pole #61201 is missing arm and fixture AT THE SEC, ON COMBINATION POLE 61201. - | High Pressure Sodium | 38.90378899000 | -77.00858856000
4/3/09 | 668067 | 0 | BENNING RD | NE |  | 59598 | 5M225 | (Light out) | DA 4-5-09 @ 952pm K. simmons pole #59598 N/C underground - metal pole,,,light out | High Pressure Sodium | 38.90009642000 | -76.98233922000
4/2/09 | 667360 | 2 | L ST | NE | 4/10/09 | 61201 | 6A240 | (Light out) | (VW 4-10-09 L Roberto repaired pole) DA 4-5-09 @ 1050pm H. Darden pole #61201 missing arm and fixture - A street light is missing both the glob and arm,pls repair | High Pressure Sodium | 38.90378899000 | -77.00858856000
4/2/09 | 667312 | 620 | T ST | NW | 4/2/09 | 14310 | 1M008 | (Light out) | DA 4-02-09 @ 1122pm K./ simmons repaired pole #14310 -- poles 29509 and 19514 (ok) | High Pressure Sodium | 38.91552837000 | -77.02104441000
4/2/09 | 667294 | 3211 | PENNSYLVANIA AVE | SE | 3/10/11 | 78548DC | 7E108 | (Light out) | (VW 4-3-09 G Edwards REFER to PEPCO popco pole#(813774407) DA 4-3-09 # 104am T. Richards repaired pole #78548dc and installed bird flap - pole is damaged and needs to be checked | High Pressure Sodium | 38.86886291000 | -76.95955716000
4/2/09 | 667289 | 3536 | MINNESOTA AVE | SE | 4/3/09 | 76384DC | 7S263 | (Light off/on) | DA 4-3-09 @ 230am T. Richards repaired pole #76384dc | High Pressure Sodium | 38.88718063000 | -76.95487395000
4/2/09 | 667217 | 0 | 9TH ST | NW | 4/2/09 | 25437 | 2L558 | (Light out) | DA 4-02-09 @ 430am H. Darden repaired pole #25437 | High Pressure Sodium | 38.90380790000 | -77.02408338000
4/2/09 | 667213 | 0 | RHODE ISLAND AVE | NW | 4/3/09 | 25214 | 2U043 | (Light out) | DA 4-3-09 @ 1255am H. Darden repaired pole #25214 | High Pressure Sodium | 38.91062739000 | -77.02719923000
4/2/09 | 667175 | 2 | L ST | NE | 4/3/09 | 61201 | 6A240 | (Light out) | DA 4-02-09 @ 101am T. Richards pole #61201 N/C underground | High Pressure Sodium | 38.90378899000 | -77.00858856000
4/1/09 | 666573 | 1435 | NEWTON ST | NW | 4/2/09 | 13913 | 1G072 | (Light out) | DA 4-02-09 @ 1220am H. Darden repaired pole #13913 | High Pressure Sodium | 38.93143118000 | -77.03279918000
4/1/09 | 666532 | 2655 | FIRTH STERLING AVE | SE | 4/1/09 | 81552DC | 8M071 | (Light out) | DA 4-01-09 @ 437am K. simmons repaired pole #81552dc | High Pressure Sodium | 38.86092272000 | -77.00172883000
3/31/09 | 665787 | 3408 | SHERMAN AVE | NW | 4/1/09 | 13073 | 1L294 | (Light out) | DA 4-01-09 @ 1210am H. Darden repaired pole #13073 -- needs 3 elephant ears 4-1-09 L.Roberto---replace 3 ee,s(sconnor) | High Pressure Sodium | 38.93221585000 | -77.02683398000
3/31/09 | 665708 | 0 | VIRGINIA AVE | SE | 4/1/09 | 68047 | 6L987 | (Light out) | DA 4-01-09 @ 1119pm T. Richards repaired pole #68047 | High Pressure Sodium | 38.87807147000 | -76.99363313000
3/31/09 | 665696 | 0 | ALLISON ST | NW | 3/31/09 | 4K101DC | 4U136DC | (Light out) | DA 3-31-09 @ 323am R, Warren repaired pole #4k101dc | High Pressure Sodium | 38.94511734000 | -77.02981962000
3/31/09 | 665688 | 5403 | NANNIE HELEN BURROUGHS AVE | NE | 3/31/09 | 72648 | 7A191 | (Light out) | DA 3-31-09 @ 248am K, Simmons repaired pole #72648 | High Pressure Sodium | 38.89829839000 | -76.92250388000
3/31/09 | 665685 | 4910 | NANNIE HELEN BURROUGHS AVE | NE | 3/31/09 | 71284DC | 7A217 | (Light out) | DA 3-31-09 @ 203am K. Simmons repaired pole #71284dc | High Pressure Sodium | 38.89864693000 | -76.93127544000
3/31/09 | 664935 | 2801 | PENNSYLVANIA AVE | SE | 3/31/09 | 78588 | 7E064 | (Light out) | DA 3-31-09 @ 1217am T. Richards repaired pole #78588 | High Pressure Sodium | 38.87221490000 | -76.96732472000
3/30/09 | 664918 | 0 | H ST | NW | 4/1/09 | 22739 | 2G965 | (No current) |  | High Pressure Sodium | 38.89969019000 | -77.02607864000
3/30/09 | 664980 | 1000 | 3RD ST | SE | 5/14/09 | 68141 | 6A470 | (Light out) | DA 4-01-09 @ 312am T. Richards pole #68141 N/C underground '' NORTH WEST CORNER - medal pole streetlight is out///very dark | High Pressure Sodium | 38.87763332000 | -77.00211232000
3/30/09 | 664911 | 715 | H ST | NW | 4/1/09 | 22567 | 2M435 | (Light out) | DA 3-31-09 @ 1030pm H. Darden pole #22567 previously repaired refer to wo #664705 | High Pressure Sodium | 38.89973194000 | -77.02259727000
3/30/09 | 664708 | 0 | PIERCE ST | NE | 3/30/09 | 61236 | 6A258 | (Light out) | DA 3-30-09 @ 410am K. Simmons repaired pole #61236 | High Pressure Sodium | 38.90445580000 | -77.00596738000
3/30/09 | 664705 | 715 | H ST | NW | 3/30/09 | 22567 | 2M435 | (Light out) | DA 3-30-09 @ 345am H. Darden repaired pole #22567 | High Pressure Sodium | 38.89973194000 | -77.02259727000
3/30/09 | 664690 | 0 | NEW YORK AVE | NE | 3/30/09 | 50006 | 5A040 | (Light out) | DA 3-30-09 @ 250am T. Richards repaired pole #50006 | High Pressure Sodium | 38.91731218000 | -76.96789154000
3/30/09 | 664685 | 1100 | 2ND ST | SW | 3/30/09 | 68133 | 6A413 | (Light out) | DA 3-30-09 @ 301am K. Simmons repaired pole #68133 | Incandescent | 38.87749103000 | -77.00282119000
3/29/09 | 664615 | 216 | RHODE ISLAND AVE | NW | 3/30/09 | 59995 | 5A187 | (Light out) | DA 3-30-09 @ 1249am K. Simmons repaired pole #59995 (there are two poles @ this location with the same pole tag #59995) | High Pressure Sodium | 38.91463757000 | -77.01493167000
3/27/09 | 663819 | 0 | ANACOSTIA FWY | SE | 3/27/09 | 79473 | 7A137 | (Light out) | DA 3-27-09 @ 200am R. Waren repaired pole #79473 | High Pressure Sodium | 38.88109425000 | -76.96448919000
3/27/09 | 663265 | 0 | ANACOSTIA FWY | SE | 3/27/09 | 79491 | 7A160 | (Light out) | DA 3-26-09 @ 1034pm T. Richards repaired pole #79491 -- reinstalled short cap | High Pressure Sodium | 38.88928656000 | -76.95990942000
3/26/09 | 663186 | 3408 | SHERMAN AVE | NW | 3/27/09 | 13073 | 1L294 | (Light out) | DA 3-27-09 @ 135am V. Cooke repaired pole #13073 | High Pressure Sodium | 38.93221585000 | -77.02683398000
3/26/09 | 663921 | 216 | RHODE ISLAND AVE | NW | 3/29/09 | 59995 | 5A187 | (Light out) | DA 3-29-09 @ 1039pm K. Simmons repaired pole #59995 ALLEY PARRALLEL TO KEARNEY ST IN THE MIDDLE OF THE BLOCK - 15TH | High Pressure Sodium | 38.91463757000 | -77.01493167000
3/26/09 | 663094 | 1500 | PENNSYLVANIA AVE | SE | 3/26/09 | 65364 | 6U668 | (Light out) | DA 3-26-09 @ 312am T. Richards repaired pole #65364 | High Pressure Sodium | 38.87910251000 | -76.98200727000
3/26/09 | 663092 | 2 | L ST | NE | 3/26/09 | 61201 | 6A240 | (Light out) | DA 3-26-09 @ 334am T. Richards repaired pole #61201 | High Pressure Sodium | 38.90378899000 | -77.00858856000
3/26/09 | 663039 | 1005 | 1ST ST | NE | 3/26/09 | 61231 | 6S439 | (Light out) | DA 3-26-09 @ 148am T. Richards repaired pole #61231 | High Pressure Sodium | 38.90311217000 | -77.00596908000
3/25/09 | 662324 | 0 | KANSAS AVE | NW | 3/25/09 | 4K568 | 4G321 | (Light out) | DA 3-25-09 @ 1053pm R. Warren repaired pole #4k568 | High Pressure Sodium | 38.94326049000 | -77.02502562000
3/25/09 | 662318 | 0 | IRVING ST | NW | 3/26/09 | 12738 | 1G044 | (Light out) | DA 3-6-09 @ 1230am H. Darden repaired pole #12738 | High Pressure Sodium | 38.92871205000 | -77.03568647000
3/25/09 | 662278 | 0 | 9TH ST | NW | 3/25/09 | 4K015 | 4G322 | (Light out) | DA 3-25-09 @ 1046pm R. Warren repaired pole #4k015 | High Pressure Sodium | 38.94305820000 | -77.02519022000
3/25/09 | 662220 | 4469 | WISCONSIN AVE | NW | 3/25/09 | 30131 | 3L465 | (Light out) | DA 3-25-09 @ 325am V. Cooke pole #30131 N/C underground | High Pressure Sodium | 38.94724720000 | -77.06516811000
3/25/09 | 662170 | 0 | 18TH ST | NE | 3/25/09 | 59471 | 5M326 | (Light out) | DA 3-25-09 @ 129am K. Simmons repaired pole #59471 | High Pressure Sodium | 38.89920000000 | -76.97735548000
3/24/09 | 662182 | 309 | H ST | NE | 3/26/09 | 61520 | 6S048 | (Light out) | DA 3-26-09 @ 1218am T. Richards light found on nd working pole #61520 FRONT - the door of base cover door off | High Pressure Sodium | 38.90012250000 | -77.00160714000
3/23/09 | 660673 | 1001 | 14TH ST | NW | 3/24/09 | 27356 | 2M404 | (Light out) | DA 3-24-09 @ 1220am H. Darden repaired pole #27356 -- checked poles 27354 and 27355 (ok) | High Pressure Sodium | 38.90297282000 | -77.03182495000
3/23/09 | 660666 | 1211 | CONNECTICUT AVE | NW | 3/24/09 | 27222 | 2U526 | (Light out) | DA 3-24-09 @ 230am H. Darden repaired pole #27222 | High Pressure Sodium | 38.90611590000 | -77.04122309000
3/23/09 | 660662 | 0 | N ST | NW | 3/25/09 | 23793 | 2G761 | (Light out) | DA 3-25-09 @ 330am H. Darden repaired pole #23793 | High Pressure Sodium | 38.90730541000 | -77.04583361000
3/23/09 | 660653 | 1625 | MASSACHUSETTS AVE | NW | 2/9/12 | 27102 | 2M003 | (Light off/on) | DA 3-25-09 @ 400am H. Darden repaired pole #27102 -- needs @ ears | High Pressure Sodium | 38.90778988000 | -77.03832443000
3/22/09 | 660528 | 3845 | PENNSYLVANIA AVE | SE | 3/23/09 | 77879DC | 7E013 | (Light out) | DA 3-22-09 @ 1131pm T. Richards repaird pole #77879dc -- checked poles 78881dc and 77880dc (ok) | High Pressure Sodium | 38.86555413000 | -76.95089797000
3/22/09 | 660525 | 1633 | FORT DUPONT ST | SE | 3/22/09 | 78170DC | 7A341DC | (Light out) | DA 3-22-09 @ 1105pm T. Richards repaired pole #78170dc - reset photocell | High Pressure Sodium | 38.86620718000 | -76.94625361000
3/22/09 | 660506 | 2200 | 18TH ST | NW | 4/14/09 | 11537 | 1G503 | (Light out) | DA 3-23-09 @ 120am H. Darden repaired pole #11537 -- needs tree trimmed | High Pressure Sodium | 38.91888453000 | -77.04173093000
3/20/09 | 660418 | 1735 | 17TH ST | NW | 3/23/09 | 26701 | 2M036 | (Light out) | DA 3-23-09 @ 155am H. Darden pole #26701 -previously repaired using 400 hps lamp refer to wo #658428 metal pole streetlight is out | High Pressure Sodium | 38.91375043000 | -77.03840149000
3/19/09 | 659148 | 2200 | H ST | NW | 3/20/09 | 27997 | 2A216 | (Light out) | DA 3-20-09 @ 1215am H. Darden repaired pole #27997-- checked poles 27996 nad 27998 (ok) | High Pressure Sodium | 38.89963632000 | -77.04973980000
3/19/09 | 659125 | 1454 | IRVING ST | NW | 3/24/09 | 12741 | 1G036 | (Light off/on) | DA 3-23-09 @ 1000pm H. Darden repaired pole #12741 respliced hot and neturial @ base Da 3-20-09 @ 250am K. simmons pole #12741 Needs 400 hps fixture | High Pressure Sodium | 38.92872574000 | -77.03484302000
3/19/09 | 659058 | 0 | L ST | NW | 3/19/09 | 61098 | 6S254 | (Light out) | DA 3-19-09 @ 109am T. Richars repaired pole #61098 | High Pressure Sodium | 38.90367060000 | -77.01389371000
3/18/09 | 658423 | 1735 | 17TH ST | NW | 3/18/09 | 26701 | 2M036 | (Light out) | DA 3-18-09 @ 1101pm H. Darden repaired pole #26701 - checked poles 26741 (needs TB door) 26700 (ok) | High Pressure Sodium | 38.91375043000 | -77.03840149000
3/18/09 | 658416 | 815 | V ST | NW | 3/19/09 | 14235 | 1U030 | (Light out) | (VW 3-20-09 Ripp - Resplaced 189 inc lamp) DA 3-19-09 @ 120am K. Simmons refer to day crew cars blocking alley | High Pressure Sodium | 38.91785954000 | -77.02338967000
3/17/09 | 657680 | 3408 | SHERMAN AVE | NW | 3/18/09 | 13073 | 1L294 | (Light off/on) | DA 3-17-09 @ 1135pm H. Darden repaired pole #13073 | High Pressure Sodium | 38.93221585000 | -77.02683398000
3/17/09 | 657631 | 0 | K ST | NW | 3/17/09 | 24658 | 2G677 | (Light out) | DA 3-17-09 @ 300am H. Darden repaired pole #24658 | High Pressure Sodium | 38.90256507000 | -77.04931783000
3/17/09 | 657602 | 2611 | POMEROY RD | SE | 3/17/09 | 81350DC | 8U661 | (Light out) | DA 3-17-09 @ 118am K. Simmons repaired pole #81350dc | High Pressure Sodium | 38.85565774000 | -76.99249822000
3/16/09 | 657023 | 0 | KENNEDY ST | NW | 3/18/09 | 4M070 | 4M070DC | (Light out) | DA 3-17-09 @ 1100pm V. Cooke pole #4M070 N/C underground CROSS - 3 street light on metal pole is out , | High Pressure Sodium | 38.95645469000 | -77.02220865000
3/15/09 | 656883 | 2721 | PENNSYLVANIA AVE | SE | 3/17/09 | 78571DC | 7E082 | (Light off/on) | DA 3-17-09 @ 403am T. Richards repaired pole #78571dc | High Pressure Sodium | 38.87220266000 | -76.96783710000
3/15/09 | 656863 | 509 | 51ST ST | SE | 3/10/11 | 75380DC | 7B001DC | (Light out) | (VW 3-17-09 G Edwards - 250w hps fixture & 8'arm needs to be removed from 60'wood pole - REFER to PEPCO (Pepco pole) DA 3-17-09 @ 154am T. Richards repaired pole #75380dc - pole has been hit and damaged - pole craked | High Pressure Sodium | 38.88130308000 | -76.92927806000
3/12/09 | 655499 | 0 | INTERSTATE 295 | SE | 3/17/09 | 86516 | 8L776 | (Light out) |  | High Pressure Sodium | 38.86724779000 | -76.99038506000
3/12/09 | 655482 | 0 | INTERSTATE 295 | SE | 3/13/09 | 86510 | 8L768 | (Light out) | DA 3-13-09 @ 225am K. Simmons repaired pole #86510 | High Pressure Sodium | 38.86566546000 | -76.99168893000
3/12/09 | 655517 | 1421 | 33RD ST | NW | 3/15/09 | 20732 | 2G181 | (Light out) | DA 3-15-09 @ 1030pm H. Darden pole #20732 light found on and working previously repaired using 150 lamp, kit and WMP refer to wo #653805 BETWEEN 1421 AND 1433 - request to have light bulb repaired, it is on the NE side....Light is on metal pole....ple | High Pressure Sodium | 38.90853673000 | -77.06614097000
3/12/09 | 655466 | 750 | I ST | NW | 3/13/09 | 22481 | 2M183 | (Light off/on) | DA 3-12-09 @ 1150pm H. Darden repaired pole #22481 | High Pressure Sodium | 38.90094560000 | -77.02237583000
3/12/09 | 655357 | 37 | L ST | SE | 3/13/09 | 67680 | 6B105 | (Light out) | DA 3-13-09 @ 1228am T. richards repaired pole #67680 | High Pressure Sodium | 38.87758882000 | -77.00809103000
3/11/09 | 654603 | 1421 | MARYLAND AVE | NE | 3/11/09 | 63605 | 6M735 | (Light out) | DA 3-11-09 @ 212am T. Richards repaired pole #63605 | High Pressure Sodium | 38.89948779000 | -76.98477250000
3/10/09 | 653805 | 1421 | 33RD ST | NW | 3/10/09 | 20732 | 2G181 | (Light out) | DA 3-10-09 @ 335am H. Darden repaired pole #20732 | High Pressure Sodium | 38.90853673000 | -77.06614097000
3/10/09 | 653786 | 7051 | SPRING PL | NW | 3/10/09 | 4H523DC | 4H523 | (Light out) | DA 3-10-09 @ 211am R. Warren repaired pole #4h523dc | Incandescent | 38.97594098000 | -77.01865986000
3/9/09 | 653148 | 3601 | GEORGIA AVE | NW | 3/9/09 | 12968 | 1G214 | (Light out) | DA 3-9-09 @ 1045pm H. Darden repaired pole #12968 | High Pressure Sodium | 38.93445504000 | -77.02413636000
3/9/09 | 653146 | 3884 | PENNSYLVANIA AVE | SE | 3/9/09 | 77877DC | 7E015 | (Light out) | DA 3-9-09 @ 1044pm T. Richards repaired pole #77877dc | High Pressure Sodium | 38.86571914000 | -76.95138037000
3/9/09 | 653901 | 1421 | 33RD ST | NW | 3/15/09 | 20732 | 2G181 | (Light out) | DA 3-15-09 @ 1030pm H. Darden pole #20732 light found on and working previously repaired using 150 lamp, kit and WMP refer to wo #653805 ODD SIDE - | High Pressure Sodium | 38.90853673000 | -77.06614097000
3/9/09 | 652866 | 1000 | 3RD ST | SE |  | 68141 | 6A470 | (Light out) | CP - 4/14/09 - J Lancaster DA 3-10-09 @ 1215am T. Richards pole #68141 N/C underground | High Pressure Sodium | 38.87763332000 | -77.00211232000
3/9/09 | 652789 | 720 | RHODE ISLAND AVE | NE | 3/9/09 | 56389DC | 5M343 | (Light out) | DA 3-9-09 @ 1225am K. Simmons repaired pole #56389dc | High Pressure Sodium | 38.92154000000 | -76.99495411000
3/8/09 | 652815 | 64 | NEW YORK AVE | NE | 3/10/09 | 56752 | 5M127 | (Light out) | DA 3-10-09@ 1237am K. Simmons repaired pole #56752 - street light on metal pole #56752 ia on and off | High Pressure Sodium | 38.90868561000 | -77.00559893000
3/6/09 | 652064 | 1826 | CALVERT ST | NW | 2/7/12 | 11197 | 1A003 | (Light out) | DA 3-6-09 @ 4200am V. Cooke pole #1197 N/C underground | High Pressure Sodium | 38.92316276000 | -77.04378689000
3/6/09 | 652063 | 1826 | CALVERT ST | NW | 2/7/12 | 10729 | 1A013 | (Light out) | DA 3-6-09 @ 415am V. Cooke pole #10729 N/C underground | High Pressure Sodium | 38.92339148000 | -77.04377813000
3/6/09 | 652056 | 0 | H ST | NE | 3/6/09 | 62350 | 6S120 | (Light out) | DA 3-6-09 @ 333am T. Richards repaired pole #62350 | High Pressure Sodium | 38.90011633000 | -76.98846372000
3/5/09 | 651331 | 3209 | ALABAMA AVE | SE | 3/9/09 | 74836DC | 7A100DC | (Light out) | DA 3-8-09 @ 1008pm T. Richards Verizon pole, Verizon has been notified DA 3-8-09 @ 1131pm T. Richards pole #74836dc pole is leaning but light is on ALLEY (BETWEEN 32ND ST AND 33RD S, SE) - alleylight wooden pole is cracked and is leaning toward neigh | High Pressure Sodium | 38.86132638000 | -76.96088830000
3/5/09 | 651253 | 0 | INTERSTATE 395 | SW | 3/24/09 | 28688 | 6A579 | (No current) | Al Young completed on 3-24-09 Made splices in the base of the SL pole. | High Pressure Sodium | 38.88293251000 | -77.01275060000
3/5/09 | 650542 | 1101 | L ST | NW | 3/5/09 | 25942 | 2M218 | (Light out) | DA 3-4-09 @ 1130pm H. Darden repaired pole #25942 | High Pressure Sodium | 38.90408908000 | -77.02717553000
3/4/09 | 650525 | 0 | INTERSTATE 395 | SW | 3/5/09 | 28716 | 28638 | (Light dim) | DA 3-5-09 B. Black repaired | High Pressure Sodium | 38.87963390000 | -77.03245609000
3/4/09 | 650498 | 1807 | MARTIN LUTHER KING JR AVE | SE | 3/5/09 | 81019 | 8L851 | (Light out) | DA 3-5-09 @ 1235am V. Cooke repaired pole #81019 | High Pressure Sodium | 38.86789068000 | -76.98847973000
3/4/09 | 650487 | 900 | UPSHUR ST | NW | 3/24/09 | 4J744 | 4G330 | (Light out) | DA 3-24-09 @ 1031pm R. Warren pole #4J744 light found okay on and working DA 3-4-09 @ 1047pm R. Warren repaired pole #4j744 - Needs QC follow up | High Pressure Sodium | 38.94182164000 | -77.02494834000
3/4/09 | 650475 | 1000 | NEW YORK AVE | NW | 3/4/09 | 22948 | 2L032 | (Light out) | DA 3-4-09 @ 435am H. Darden repaired pole #22948 | High Pressure Sodium | 38.90132896000 | -77.02684244000
3/4/09 | 650474 | 0 | 11TH ST | NW | 3/4/09 | 23376 | 2L019 | (Light out) | DA 3-4-09 @ 420am H. Darden repaired pole #23376 | High Pressure Sodium | 38.90082404000 | -77.02675794000
3/4/09 | 650469 | 4239 | 9TH ST | NW | 3/4/09 | 4K016 | 4G323 | (Light out) | DA 3-4-09 @ 405am R. Warren repaired pole #4k016 | High Pressure Sodium | 38.94283513000 | -77.02505211000
2/25/09 | 647242 | 301 | MASSACHUSETTS AVE | NW | 4/2/09 | 60399 | 6A198 | (Light out) | CP - 3/26 - J Lancaster Keith Greenfield on 3-3-09 Needs surface cut. DA 2-25-09 @ 1127pm T. Richards pole #60399 N/C underground - open neturial | High Pressure Sodium | 38.90029659000 | -77.01558775000
2/24/09 | 646580 | 900 | UPSHUR ST | NW | 2/26/09 | 4J744 | 4G330 | (Light out) | DA 2-25-09 @ 1045pm R. Warren pole #4j744 light found okay SOUTHEAST CORNER - Please repair the street light | High Pressure Sodium | 38.94182164000 | -77.02494834000
2/23/09 | 645740 | 3225 | PENNSYLVANIA AVE | SE | 2/23/09 | 78589 | 7E044 | (Light out) | DA 2-23-09 @ 1121pm T. Richards repaired pole #78589 | High Pressure Sodium | 38.86945735000 | -76.96055314000
2/23/09 | 645779 | 300 | 34TH PL | NE | 2/25/09 | 74813DC | 7A088DC | (Light out) | DA 2-25-09 @ 1215am K. Simmons repaird pole #74813dc LIGHT IS ON THE CORNER - | High Pressure Sodium | 38.85998206000 | -76.95477112000
2/22/09 | 645689 | 0 | U ST | NW | 2/22/09 | 13283 | 1G528 | (Light out) | DA 2-22-09 @ 1015pm H. Darden repaired pole #13283 | High Pressure Sodium | 38.91691876000 | -77.02945599000
2/21/09 | 645591 | 3700 | NEW HAMPSHIRE AVE | NW | 2/24/09 | 4J333 | 4G235 | (Light out) | AT BUS STOP ON GEORGIA AVENUE SIDE - | High Pressure Sodium | 38.93668536000 | -77.02424031000
2/21/09 | 645567 | 4878 | NANNIE HELEN BURROUGHS AVE | NE | 2/24/09 | 71291DC | 7A221DC | (Light out) | DA 2-23-09 @ 104am T. Richards pole #71291dc - N/C to overhead | High Pressure Sodium | 38.89881397000 | -76.93206898000
2/21/09 | 645566 | 4832 | NANNIE HELEN BURROUGHS AVE | NE | 2/24/09 | 71292DC | 7A222DC | (Light out) | DA 2-23-09 @ 104am T. Richards pole #71292dc - N/C to overhead | High Pressure Sodium | 38.89861491000 | -76.93235329000
2/21/09 | 645565 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 2/24/09 | 71294DC | 7A226 | (Light out) | DA 2-23-09 @ 104am T. Richards pole #71294dc - N/C to overhead | High Pressure Sodium | 38.89882951000 | -76.93342319000
2/21/09 | 645557 | 1105 | STEVENS RD | SE | 2/25/09 | 81584DC | 8A048 | (Light out) | DA 2-25-09 @ 1230am V. Cooke repaired pole #81584dc | High Pressure Sodium | 38.86023686000 | -77.00228963000
2/20/09 | 644925 | 301 | MASSACHUSETTS AVE | NW | 2/22/09 | 60399 | 6A198 | (Light out) | DA 2-22-09 @ 1041pm T. Richards repaired pole #60399 IN FRONT OF "TUNNEL LIQUOR" STORE. - 4TH WE HAVE HAD A NUMBER OF PURSE SNATCHES AND ROBBERIES ON THIS BLOCK IN THE PAST TWO WEEKS. IT WOULD HELP IF WE HAD OUR LIGHTING BACK. H STREET, BWT 3RD AND 4 | High Pressure Sodium | 38.90029659000 | -77.01558775000
2/20/09 | 644821 | 1001 | NEW HAMPSHIRE AVE | NW | 2/20/09 | 23862 | 2G674 | (Light out) | DA 2-20-09 @ 1235am H. Darden repaired pole #23862 and trimmed tree | High Pressure Sodium | 38.90308383000 | -77.04974132000
2/19/09 | 644141 | 0 | INTERSTATE 295 | SE | 2/20/09 | 86510 | 8L768 | (Light out) | DA 2-19-09 @ 1134pm B. Black repaired pole #86510 | High Pressure Sodium | 38.86566546000 | -76.99168893000
2/19/09 | 644060 | 0 | H ST | NE | 2/20/09 | 62340 | 6S187 | (Light out) | DA 2-20-09 @ 126am K. Simmons repaired pole #62340 | High Pressure Sodium | 38.90029917000 | -76.99390863000
2/18/09 | 643456 | 0 | 22ND ST | NE | 2/24/09 | 63632 | 6M793 | (Light out) | DA 2-19-09 @ 1131pm K. Simmons pole #63632 N/C underground DA 2-19-09 K. Simmons request for map | High Pressure Sodium | 38.89028237000 | -76.97436503000
2/18/09 | 643477 | 232 | CARROLL ST | NW | 2/23/09 | 4H568DC | 4H568 | (Light out) | DA 2-23-09@ 257am R. Warren repaired pole #4h568dc ALLEY LIGHTS - caller request that the whole alley is very dark and the alley light need to be repair asap | High Pressure Sodium | 38.97499707000 | -77.01542228000
2/18/09 | 643437 | 7051 | SPRING PL | NW | 2/19/09 | 4H523DC | 4H523 | (Light out) | DA 2-19-09 @ 322am R. Warren repaired pole #4H523dc | Incandescent | 38.97594098000 | -77.01865986000
2/18/09 | 643427 | 459 | CLAY ST | NE | 2/19/09 | 74829DC | 7A093DC | (Light out) | DA 2-19-09 @ 440am V. Cooke repaired pole #74829dc | High Pressure Sodium | 38.86054953000 | -76.95960200000
2/18/09 | 643426 | 300 | 34TH PL | NE | 2/19/09 | 74813DC | 7A088DC | (Light out) | DA 2-19-09 @ 230am V .Cooke repaired pole #74813dc installed t base door | High Pressure Sodium | 38.85998206000 | -76.95477112000
2/18/09 | 643414 | 200 | L ST | SE | 2/18/09 | 67695 | 6A414 | (Light out) | DA 2-18-09 @ 1051pm K. Simmons repaired pole #67695 | Incandescent | 38.87766628000 | -77.00287950000
2/18/09 | 643407 | 711 | D ST | NW | 2/19/09 | 60088 | 2M325 | (Light out) | DA 2-19-09 @ 113am K. Simmons repaired pole #60088 | High Pressure Sodium | 38.89485723000 | -77.02246234000
2/18/09 | 643335 | 401 | 4TH ST | NE | 2/22/09 | 61630 | 6S054 | (Light out) | DA 2-18-09 @ 350am K. Simmons pole #61630 N/C undergound | High Pressure Sodium | 38.90012025000 | -77.00042007000
2/17/09 | 642600 | 3601 | GEORGIA AVE | NW | 2/17/09 | 12968 | 1G214 | (Light out) | DA 2-17-09 @ 1105pm H. Darden pole #12968 light found on and working - 400 hps bulb was replaced on 2-2-09 refer to wo #635838 | High Pressure Sodium | 38.93445504000 | -77.02413636000
2/17/09 | 642584 | 717 | H ST | NE | 2/18/09 | 61992 | 6S083 | (Light out) | DA 2-18-09 @ 332am K. Simmons repaired pole #61992 | High Pressure Sodium | 38.90011980000 | -76.99537874000
2/17/09 | 642582 | 0 | K ST | SE | 2/18/09 | 67658 | 6A445 | (Light out) | DA 2-17-09 @ 1137pm K. Simmons pole #67658 N/C underground | High Pressure Sodium | 38.87835686000 | -77.00087371000
2/17/09 | 642581 | 1000 | 3RD ST | SE | 2/18/09 | 68141 | 6A470 | (Light out) | DA 2-18-09 @ 152am K. Simmons repaired pole #68141 DA 2-18-09 K. Simmons - request for map | High Pressure Sodium | 38.87763332000 | -77.00211232000
2/17/09 | 642579 | 301 | MASSACHUSETTS AVE | NW | 2/18/09 | 60399 | 6A198 | (Light out) | DA 2-18-09 @ 306am K. Simmons installed 400 hps lamp and TLP - pole #60399 | High Pressure Sodium | 38.90029659000 | -77.01558775000
2/16/09 | 642502 | 3033 | BLADENSBURG RD | NE | 2/16/09 | 58720DC | 5A172DC | (Light out) | mistake | Incandescent | 38.92960546000 | -76.95868010000
2/16/09 | 642497 | 4520 | HOBAN RD | NW | 2/16/09 | 35822DC | 35822 | (Light out) | DA 2-16-09 @ 1240am T. Richards repaired pole #35822dc | Incandescent | 38.91433459000 | -77.08526855000
2/15/09 | 642474 | 4878 | NANNIE HELEN BURROUGHS AVE | NE | 2/16/09 | 71291DC | 7A221DC | (Light out) | DA 2-15-09 @ 1050pm V. Cooke repaired pole #71291dc - respliced overhead line | High Pressure Sodium | 38.89881397000 | -76.93206898000
2/15/09 | 642473 | 4832 | NANNIE HELEN BURROUGHS AVE | NE | 2/18/09 | 71292DC | 7A222DC | (Light out) | DA 2-15-09 @ 1105pm V. Cooke pole #71292dc N/C to overhead - phase going to pole has no voltage - 2nd phase 120 volts | High Pressure Sodium | 38.89861491000 | -76.93235329000
2/15/09 | 642472 | 4832 | NANNIE HELEN BURROUGHS AVE | NE | 2/18/09 | 71293DC | 7A223DC | (Light out) | DA 2-15-09 @ 1110pm V. Cooke pole #71293dc N/C to overhead - phase to light no voltage - 2nd phase 120 volts | High Pressure Sodium | 38.89895905000 | -76.93289413000
2/13/09 | 641811 | 623 | KENNEDY ST | NW | 2/19/09 | 4M069 | 4M069DC | (Light off/on) | DA 2-19-09 @ 1210am R. Warren repaired pole #4M069 | High Pressure Sodium | 38.95646426000 | -77.02185855000
2/13/09 | 641754 | 44 | H ST | NW | 2/13/09 | 60397 | 68450 | (Light out) | DA 2-13-09 @ 150am T. Richards pole #60397 N/C underground | High Pressure Sodium | 38.90030196000 | -77.01493317000
2/12/09 | 641864 | 1421 | 33RD ST | NW | 2/16/09 | 20732 | 2G181 | (Light out) | DA 2-16-09 @ 225am H. Darden repaired pole #20732 ODD SIDE - | High Pressure Sodium | 38.90853673000 | -77.06614097000
2/12/09 | 641131 | 300 | 34TH PL | NE | 2/12/09 | 74813DC | 7A088DC | (Light out) | DA 2-12-09 @ 132pm T. Richards repaired pole #74813dc | High Pressure Sodium | 38.85998206000 | -76.95477112000
2/12/09 | 641127 | 0 | MARTIN LUTHER KING JR AVE | SE | 2/13/09 | 81018 | 8L855 | (Light out) | DA 2-12-09 @ 1025pm V. Cooke repaired pole #81018 | High Pressure Sodium | 38.86833152000 | -76.98830912000
2/12/09 | 641167 | 3301 | SHERMAN AVE | NW | 2/16/09 | 12874 | 1L279 | (Light out) | DA 2-16-09 @ 145am H. Darden repaired pole #12874 - street light on a metal pole out | High Pressure Sodium | 38.93089776000 | -77.02642978000
2/12/09 | 641120 | 2100 | M ST | NW | 2/12/09 | 23738 | 2G753 | (Light off/on) | DA 2-12-09 @ 1121pm H. Darden repaired pole #23738 | High Pressure Sodium | 38.90623409000 | -77.04677309000
2/12/09 | 641118 | 1272 | NEW HAMPSHIRE AVE | NW | 2/13/09 | 23851 | 2G759 | (Light off/on) | (VW 2-13-09 T Pitt Found ok) DA 2-12-09 @ 1109pm H. Darden repaired pole #23851 - part of T Base Door is missing | High Pressure Sodium | 38.90689340000 | -77.04614952000
2/12/09 | 641051 | 0 | PENNSYLVANIA AVE | NW | 2/13/09 | 28040 | 2M289 | (Light out) | DA 2-13-09 @ 125am H, Daren repaired pole #28040 | High Pressure Sodium | 38.90206835000 | -77.04914862000
2/12/09 | 641049 | 711 | D ST | NW | 2/13/09 | 60088 | 2M325 | (Light out) | DA 2-13-09 @ 1251am T. Richards repaired pole #60088 | High Pressure Sodium | 38.89485723000 | -77.02246234000
2/12/09 | 641048 | 717 | D ST | NW | 2/13/09 | 60651 | 2M361 | (Light out) | DA 2-13-09 @ 112am T. Richards repaired pole #60651 | High Pressure Sodium | 38.89496625000 | -77.02287031000
2/12/09 | 641046 | 301 | MASSACHUSETTS AVE | NW | 2/13/09 | 60399 | 6A198 | (Light out) | DA 2-13-09 @ 204am T. Richards repaired pole #60399 | High Pressure Sodium | 38.90029659000 | -77.01558775000
2/11/09 | 640491 | 3429 | 14TH ST | NW | 2/12/09 | 13804 | 1G082 | (Light out) | DA 2-12-09 H. Darden request for map 2-12-09 T.Pitt---found ok(sconnor) | High Pressure Sodium | 38.93260036000 | -77.03283470000
2/11/09 | 640484 | 3033 | BLADENSBURG RD | NE | 2/16/09 | 58720DC | 5A172DC | (Light out) | DA 2-16-09 @ 245am K. Simmons repaired pole #58720dc DA 2-13-09 @ 235am R. Warren pole #58720dc - car blocking alley can't acess light | Incandescent | 38.92960546000 | -76.95868010000
2/11/09 | 640482 | 807 | V ST | NW | 2/11/09 | 14237DC | 1U041 | (Light out) | DA 2-11-09 @ 420am H. Darden repaired pole #14237dc | Incandescent | 38.91856611000 | -77.02346139000
2/11/09 | 640479 | 0 | 8TH ST | NW | 2/11/09 | 25501 | 2M196 | (Light out) | DA 2-11-09 @ 410am H. Darden repaired pole #25501 | High Pressure Sodium | 38.91218874000 | -77.02287935000
2/11/09 | 640466 | 800 | 8TH ST | NW | 2/11/09 | 22969 | 2M383 | (Light out) | DA 2-11-09 @ 315am H. Darden repaired pole #22969 | High Pressure Sodium | 38.90023907000 | -77.02300991000
2/11/09 | 640447 | 1601 | 18TH ST | NW | 2/17/09 | 26756 | 2M150 | (Light out) | DA 2-11-09 @ 110am H. Darden pole #26756 N/C underground | High Pressure Sodium | 38.91120712000 | -77.04160249000
2/10/09 | 639820 | 1105 | STEVENS RD | SE | 2/13/09 | 81584DC | 8A048 | (Light out) | DA 2-12-09 @ 1250am H. Darden pole #81584dc - N/C to Overhead | High Pressure Sodium | 38.86023686000 | -77.00228963000
2/10/09 | 639731 | 0 | INTERSTATE 295 | SE | 6/16/11 | 86510 | 8L768 | (Light out) |  | High Pressure Sodium | 38.86566546000 | -76.99168893000
2/10/09 | 639709 | 0 | L ST | SE | 2/12/09 | 67701 | 6A438 | (Light out) | DA 2-12-09 @ 309am T. Richards repaired pole #67701 | High Pressure Sodium | 38.87758258000 | -77.00088038000
2/10/09 | 639689 | 1601 | 18TH ST | NW | 2/10/09 | 26756 | 2M150 | (Light out) | DA 2-10-09 @ 420am H. Darden repaired pole #26756 - adjusted photocell | High Pressure Sodium | 38.91120712000 | -77.04160249000
2/10/09 | 639665 | 3321 | IDAHO AVE | NW | 6/26/09 | 38888DC | 3U416 | (Light out) | DA 2-10-09 @ 1235am V. Cooke pole #38888dc refer to ddot defective 250 MV fixture | Mercury Vapor | 38.93408385000 | -77.07471732000
2/9/09 | 639081 | 200 | W ST | NW | 2/9/09 | 13760 | 1U188 | (Light out) | DA 2-9-09 @ 955pm H. Darden repaired pole #13760 | High Pressure Sodium | 38.91949574000 | -77.01713787000
2/9/09 | 639107 | 711 | D ST | NW | 2/13/09 | 60088 | 2M325 | (Light out) | DA 2-13-09 @ 1251am T. Richards repaired pole #60088 using 40 hps powerdoor and TLP refer to wo #641049 BLOCK - one metal pole light is out | High Pressure Sodium | 38.89485723000 | -77.02246234000
2/9/09 | 639100 | 301 | MASSACHUSETTS AVE | NW | 2/13/09 | 60399 | 6A198 | (Light out) | DA 2-13-09 @ 204am T. Richards repaired pole #60399 using 400 hps bulb refer to wo #641046 IN FRONT OF "TUNNEL LIQUOR" STORE. - 4TH **SRCB** Is the pole metal or wood? - Metal What is the problem with the light (light is out, light is always on, | High Pressure Sodium | 38.90029659000 | -77.01558775000
2/9/09 | 639005 | 3033 | BLADENSBURG RD | NE | 2/9/09 | 58720DC | 5A172DC | (Light out) | DA 2-9-09 @ 242am K. Simmons repaired pole #58720dc | Incandescent | 38.92960546000 | -76.95868010000
2/8/09 | 638971 | 600 | MICHIGAN AVE | NE | 2/9/09 | 53649DC | 5U721 | (Light out) | DA 2-8-09 @ 1139pm K. Simmons repaired pole #53649dc | High Pressure Sodium | 38.93248081000 | -76.99750323000
2/6/09 | 638411 | 0 | GEORGIA AVE | NW | 2/10/09 | 4J349 | 4G292 | (Light out) | DA 2-10-09 @ 157am R. Warren repaired pole #4j349 | High Pressure Sodium | 38.94177305000 | -77.02558101000
2/6/09 | 638407 | 4235 | 9TH ST | NW | 2/11/09 | 4K017 | 4G319 | (Light out) | DA 2-10-09 @ 220am R. Warren pole #4k017 - ran 75 ft wire , 2 splices - N/C underground / needs neturial pulled - pole #4K017 | High Pressure Sodium | 38.94272297000 | -77.02520204000
2/6/09 | 638369 | 3400 | PENNSYLVANIA AVE | SE | 2/6/09 | 78537DC | 7E122DC | (Light out) | DA 2-6-09 @ 411am R. Warren repaired pole #78537dc | High Pressure Sodium | 38.86734823000 | -76.95581654000
2/6/09 | 638352 | 5350 | CALL PL | SE | 2/6/09 | 75597 | 75597DC | (Light out) | DA 2-6-09 @ 225am R. Warren repaired pole #75597 | Incandescent | 38.88403430000 | -76.92511243000
2/6/09 | 638351 | 5350 | C ST | SE | 2/6/09 | 75596 | 75596DC | (Light out) | DA 2-6-09 @ 225am R. Warren repaired pole #75596 | Incandescent | 38.88422223000 | -76.92507148000
2/6/09 | 638342 | 1211 | 7TH ST | NW | 2/6/09 | 25661 | 6A790 | (Light out) | DA 2-609 @ 230am H. Darden repaired pole #25661 | High Pressure Sodium | 38.90712952000 | -77.02201691000
2/5/09 | 637867 | 4100 | GEORGIA AVE | NW | 2/10/09 | 4J350 | 4J025 | (Light out) | DA 2-10-09 @ 205am R. Warren repaired pole #4J350 | High Pressure Sodium | 38.94087801000 | -77.02540931000
2/5/09 | 637863 | 300 | I ST | SE | 2/6/09 | 67652 | 6A428 | (Light off/on) | DA 2-6-09 @ 304am T. Richards redirected photocell pole #67652 | High Pressure Sodium | 38.87923404000 | -77.00083843000
2/5/09 | 637856 | 401 | 4TH ST | NE | 2/9/09 | 61630 | 6S054 | (Light out) | DA 2-5-09 @ 1057pm T. Richards pole #61630 N/C underground - refer to fault crew | High Pressure Sodium | 38.90012025000 | -77.00042007000
2/5/09 | 637898 | 418 | 7TH ST | NW | 2/10/09 | 60648 | 6M622 | (Light out) | DA 2-10-09 @ 347am T. Richards repaired pole #60648 POLE IS ADJACENT TO 101 CONSTITUTION AVE NW, ON 2ND STREET NW, ACROSS THE STREET FROM THE US DEPARTMENT OF LABOR. - **SRCB** Is the pole metal or wood? - Metal What is the problem with the light | High Pressure Sodium | 38.89553430000 | -77.02201303000
2/5/09 | 637884 | 623 | KENNEDY ST | NW | 2/9/09 | 4M069 | 4M069DC | (Light out) | DA 2-9-09 @ 1104pm R. Warren repaired pole #4m069 NOTH SIDE SIDEWALK METAL POLE WITH DC POLE NO 4M069DCL227T WEST 07 ALLEY ENTRANCE 600 BLOCK OF KENNEDY ST NW - | High Pressure Sodium | 38.95646426000 | -77.02185855000
2/5/09 | 637752 | 800 | 8TH ST | NW | 2/5/09 | 22969 | 2M383 | (Light out) | DA 2-5-09 @ 420am H. Darden repaired pole #22969 | High Pressure Sodium | 38.90023907000 | -77.02300991000
2/4/09 | 637148 | 4604 | IOWA AVE | NW | 2/4/09 | 4K465DC | 4U133 | (Light out) | DA 2-4-09 @ 401am R. Warren repaired pole #4k465dc | High Pressure Sodium | 38.94554728000 | -77.02962114000
2/3/09 | 636645 | 0 | 17TH ST | NW | 2/4/09 | 26734 | 2M067 | (Light out) | DA 2-3-09 @ 1135pm H. Darden repaired pole #26734 | High Pressure Sodium | 38.91104247000 | -77.03857643000
2/3/09 | 636643 | 1601 | 18TH ST | NW | 2/3/09 | 26756 | 2M150 | (Light out) | DA 2-3-09 @ 1110pm H. Darden repaired pole #26756 | High Pressure Sodium | 38.91120712000 | -77.04160249000
2/3/09 | 636633 | 2400 | 37TH ST | NW | 2/4/09 | 30170 | 3G050 | (Light off/on) | DA 2-3-09 @ 1100pm V. Cooke repaired pole #30170 | High Pressure Sodium | 38.92292626000 | -77.07297784000
2/3/09 | 636625 | 2450 | 37TH ST | NW | 2/4/09 | 36869 | 3G057 | (Light off/on) | DA 2-3-09 @ 1050pm V. Cooke repaired pole #36869 | High Pressure Sodium | 38.92247432000 | -77.07310675000
2/3/09 | 636569 | 650 | MASSACHUSETTS AVE | NW | 2/3/09 | 22466 | 2L131 | (Light out) | DA 2-3-09 @ 405am H. Darden repaired pole #22466 | High Pressure Sodium | 38.90183469000 | -77.02118586000
2/3/09 | 636543 | 1005 | 1ST ST | NE | 2/4/09 | 61231 | 6S439 | (Light out) | DA 2-3-09 @ 241am T. Richards pole #61231 N/C underground | High Pressure Sodium | 38.90311217000 | -77.00596908000
2/1/09 | 635846 | 4612 | 12TH ST | NE | 2/2/09 | 51256DC | 5A150DC | (Light out) | DA 2-2-09 @ 1221am K. Simmons repaired pole #51256dc | High Pressure Sodium | 38.94542966000 | -76.99072288000
2/1/09 | 635838 | 3601 | GEORGIA AVE | NW | 2/2/09 | 12968 | 1G214 | (Light out) | DA 2-2-09 @ 1030pm H Darden repaired pole #12968 | High Pressure Sodium | 38.93445504000 | -77.02413636000
2/1/09 | 635830 | 0 | 8TH ST | NW | 2/2/09 | 4M075 | 4M075DC | (Light out) | DA 2-2-09 @ 158am R. Warren repaired pole #4M075 | High Pressure Sodium | 38.95640844000 | -77.02396296000
2/1/09 | 635812 | 325 | 7TH ST | NW | 3/2/09 | 60642 | 6M609 | (Light out) | DA 2-2-09 @ 109am T. Richards repaired pole #60642 - needs major tree trim | High Pressure Sodium | 38.89443475000 | -77.02181706000
2/1/09 | 635811 | 509 | 7TH ST | NW | 2/2/09 | 22431 | 6M628 | (Light out) | DA 2-2-09 @ 1130pm H. Darden pole #22431 light on and working - new 400 hps bulb | High Pressure Sodium | 38.89648966000 | -77.02200839000
1/30/09 | 635158 | 3601 | GEORGIA AVE | NW | 2/2/09 | 12968 | 1G214 | (Light out) | DA 2-2-09 @ 1030pm H. Darden repaired pole #12965 using 400 hps bulb refer to wo #635838 | High Pressure Sodium | 38.93445504000 | -77.02413636000
1/30/09 | 635118 | 0 | GRANT ST | NE | 2/2/09 | 72339DC | 7A216 | (Light out) | DA 1-30-09 @ 110am T. Richards pole #723339dc N/C to overhead | High Pressure Sodium | 38.89843429000 | -76.93131145000
1/29/09 | 634257 | 1826 | CALVERT ST | NW | 3/5/09 | 10729 | 1A013 | (Light out) | BM 3-4-09 - S. Parker found lights on and working DA 2-2-09 @ 320am H. Darden pole #10729 N/C underground SW CORNER OF INTERSECTION - | High Pressure Sodium | 38.92339148000 | -77.04377813000
1/29/09 | 634196 | 800 | 44TH ST | NE | 1/30/09 | 71311DC | 7A245 | (Light off/on) | DA 1-30-09 @ 1239am T. Richards repaired pole #71311dc | High Pressure Sodium | 38.90055492000 | -76.93897667000
1/29/09 | 634165 | 5345 | ASTOR PL | SE | 1/29/09 | 75574 | 75574DC | (Light out) | 1-29-09 T.Pitt---repaired(sconnor) | High Pressure Sodium | 38.88660798000 | -76.92411890000
1/28/09 | 634270 | 0 | M ST | NW | 2/7/12 | 23729 | 2U531 | (Light out) | DA 2-3-09 @ 1210am H. Darden pole #23729 Teardrop fixture refer to Ddot need wire ran fron top of pole to T base - not yet connected THE STREETLIGHT IS AT THE SOUTHWEST CORNER OF CONNECTICUT AVENUE AND M STREET, N.W. - | High Pressure Sodium | 38.90574984000 | -77.04138732000
1/27/09 | 633791 | 580 | 23RD PL | NE | 1/30/09 | 74315 | 7E159 | (Light out) | DA 1-30-09 @ 402am T. Richards repaired pole #74315 ALLEY - alley light is out in the rear of this location request for the light to be fixed | High Pressure Sodium | 38.89816568000 | -76.97316755000
1/26/09 | 633186 | 0 | 13TH PL | NW | 1/27/09 | 4J740 | 4U153 | (Light out) | DA 1-26-09 @ 1124pm R. Warren repaired pole #4J740 | High Pressure Sodium | 38.94182450000 | -77.02958631000
1/26/09 | 633185 | 4200 | 13TH ST | NW | 1/27/09 | 4J609 | 4U151 | (Light out) | DA 1-26-09 @ 1115pm R. Warren repaired pole #4J609 | High Pressure Sodium | 38.94196034000 | -77.02962652000
1/26/09 | 633180 | 3123 | SHERMAN AVE | NW | 1/29/09 | 12851 | 1L261 | (Light out) | Hudson Lancaster completed on 1-29-09 DA 1-26-09 @ 1020pm H. Darden - pole #12851 has new wire, fixture and t base installed - reading 120 from hot to fixture - BB would like fault crew to check underground wiring | High Pressure Sodium | 38.92946499000 | -77.02622282000
1/26/09 | 633152 | 711 | D ST | NW | 1/26/09 | 60088 | 2M325 | (Light out) | DA 1-26-09 @ 230am H. Dardin repaired pole #60088 | High Pressure Sodium | 38.89485723000 | -77.02246234000
1/25/09 | 633128 | 2010 | 48TH ST | NW | 1/25/09 | 35370DC | 3E030 | (Light out) | DA 1-25-09 @ 1030pm V. Cooke repaired pole #35370dc | Incandescent | 38.91704622000 | -77.09453331000
1/23/09 | 632485 | 301 | MASSACHUSETTS AVE | NW | 1/26/09 | 60399 | 6A198 | (Light out) | DA 1-26-09 @ 419am T. Richards repaired pole #60399 IN FRONT OF "TUNNEL LIQUOR" STORE. - 4TH | High Pressure Sodium | 38.90029659000 | -77.01558775000
1/23/09 | 632465 | 815 | KENNEDY ST | NW | 1/26/09 | 4M078 | 4M078DC | (Light out) | DA 1-25-09 @ 1154pm R. Warren repaired pole #4m078 FRONT - | High Pressure Sodium | 38.95637067000 | -77.02492280000
1/22/09 | 631724 | 2420 | WISCONSIN AVE | NW | 1/22/09 | 30147 | 3G067 | (Light out) | DA 1-22-09 @ 1225am V. Cooke repaired pole #30147 | High Pressure Sodium | 38.92145383000 | -77.07236458000
1/21/09 | 631199 | 2487 | MINNESOTA AVE | SE | 1/21/09 | 80100 | 78575 | (Light out) | (VW) 1-21-09 FC inst 400hps lamp | High Pressure Sodium | 38.87343340000 | -76.97095551000
1/19/09 | 631042 | 0 | EAST CAPITOL ST | NE | 1/22/09 | 74205DC | 7A063DC | (No current) |  | High Pressure Sodium | 38.89216210000 | -76.94254713000
1/16/09 | 630626 | 3123 | SHERMAN AVE | NW | 1/23/09 | 12851 | 1L261 | (Light out) | K.Greenfield needs a surface cut. IN FRONT OF - the street is very dark | High Pressure Sodium | 38.92946499000 | -77.02622282000
1/16/09 | 630616 | 60 | M ST | SE | 1/17/09 | 67424 | 6L599 | (Light out) | nw man pc adn 400 hps lamp--1-17-09 | High Pressure Sodium | 38.87659105000 | -77.00715580000
1/16/09 | 630531 | 900 | NEW JERSEY AVE | SE | 1/17/09 | 67472 | 6A060 | (Light out) | DA 1-16-09 @ 338am T. Richards pole #67472 N/C underground | High Pressure Sodium | 38.87881747000 | -77.00509329000
1/16/09 | 630523 | 100 | FLORIDA AVE | NE | 1/16/09 | 56754 | 5M134 | (Light out) | DA 1-16-09 @ 119am T. Richards repaired pole #56754 | High Pressure Sodium | 38.90903901000 | -77.00458905000
1/15/09 | 630031 | 4121 | 9TH ST | NW | 1/20/09 | 4J792 | 4G328 | (Light off/on) | M.Tomlin found ok | High Pressure Sodium | 38.94134498000 | -77.02510288000
1/15/09 | 630030 | 4235 | 9TH ST | NW | 1/19/09 | 4K017 | 4G319 | (Light out) | Lorenzo Robert completed 1-19-9 | High Pressure Sodium | 38.94272297000 | -77.02520204000
1/15/09 | 629956 | 900 | 2ND ST | SW | 1/15/09 | 68129 | 6A416 | (Light out) |  | High Pressure Sodium | 38.87878241000 | -77.00287862000
1/15/09 | 629956 | 900 | 2ND ST | SW | 1/15/09 | 68129 | 68621 | (Light out) |  | High Pressure Sodium | 38.90623996000 | -77.01082515000
1/14/09 | 629482 | 4612 | 12TH ST | NE | 1/15/09 | 51256DC | 5A150DC | (Light out) | DA 1-14-09 @ 1210am K. Simmons repaired pole #51256dc | High Pressure Sodium | 38.94542966000 | -76.99072288000
1/14/09 | 629408 | 400 | RHODE ISLAND AVE | NW | 1/15/09 | 59988 | 5A180 | (Light out) | DA 1-15-09 @ 525am K. Simmons pole #59988 previously repaired refer to wo #628645 | High Pressure Sodium | 38.91371248000 | -77.01761756000
1/14/09 | 628835 | 3901 | ALABAMA AVE | SE | 1/15/09 | 78524DC | 7E137 | (Light out) | DA 1-15-09 @ 358am T. Richards repaired pole #78524dc | High Pressure Sodium | 38.86548351000 | -76.95124229000
1/14/09 | 628834 | 3901 | PENNSYLVANIA AVE | SE | 1/15/09 | 78528DC | 7E131DC | (Light out) | DA 1-15-09 @ 412am T. Richards repaired pole #78528dc | High Pressure Sodium | 38.86609981000 | -76.95276035000
1/13/09 | 628801 | 2313 | MARTIN LUTHER KING JR AVE | SE | 1/13/09 | 82042DC | 82042 | (Light out) | DA 1-13-09 @ 1021pm T. Richards repaired pole #82042dc | High Pressure Sodium | 38.86321311000 | -76.99157505000
1/13/09 | 628798 | 509 | 51ST ST | SE | 1/14/09 | 75380DC | 7B001DC | (Light off/on) | 1-14-09 Tom O. & Pitt----repaired(sconnor) | High Pressure Sodium | 38.88130308000 | -76.92927806000
1/13/09 | 628699 | 1125 | 11TH ST | NW |  | 25263 | 2M226 | (Light out) | DA 1-14-09 @ 240am R. Warren can not access pole due to street construction - no consrtuction information avaliable (VW) 1-13-09 R Rippean Shut down due to construction REFER to DDOT 2nd pole south of M St on the East side of 11th St | High Pressure Sodium | 38.90526694000 | -77.02692404000
1/13/09 | 628694 | 1125 | 11TH ST | NW |  | 25263 | 2M226 | (Light out) | DA 1-14-09 @ 230am R. Warren can not access pole due to street construction - no consrtuction information avaliable (VW) 1-14-09 R Rippean shut down due to construction REFER to DDOT 1st pole south of M St on the east side of 11th St. | High Pressure Sodium | 38.90526694000 | -77.02692404000
1/13/09 | 628658 | 1815 | 18TH ST | NW | 1/15/09 | 26750 | 2M107 | (Light out) | DA 1-15-09 @ 240am V. Cooke repaired pole #26750 - repaired wires | High Pressure Sodium | 38.91477052000 | -77.04159278000
1/13/09 | 628645 | 400 | RHODE ISLAND AVE | NW | 1/14/09 | 59988 | 5A180 | (Light out) | DA 1-14-09 @ 555am K. Simmons repaired pole #59988 | High Pressure Sodium | 38.91371248000 | -77.01761756000
1/13/09 | 628643 | 1270 | NEW HAMPSHIRE AVE | NW | 1/14/09 | 23873 | 2G758 | (Light out) | (VW) 1-14-09 R Ripp inst 400hps lamp, fixture TLPC | High Pressure Sodium | 38.90672638000 | -77.04606427000
1/13/09 | 628641 | 611 | 22ND ST | NW | 2/22/09 | 28290 | 2M437 | (Light out) | DA 1-15-09 @ 1200am R. Warren pole #28290 N/C underground | High Pressure Sodium | 38.89769965000 | -77.04891041000
1/13/09 | 628640 | 1016 | 22ND ST | NW | 1/15/09 | 23901 | 2G782 | (Light out) | DA 1-15-09 @ 1240am R. Warren repaired pole #23901 | High Pressure Sodium | 38.90364037000 | -77.04888304000
1/13/09 | 628636 | 0 | INTERSTATE 695 | SE | 1/13/09 | 67934 | 6L986 | (Light out) | DA 1-13-09 @ 335am B. Black repaired pole #67934 | High Pressure Sodium | 38.87818161000 | -76.99406246000
1/13/09 | 628206 | 0 | INTERSTATE 295 | SE | 1/13/09 | 68024 | 6U011 | (Light out) | DA 1-13-09 @ 1255am B. Black repaired pole #68024 | High Pressure Sodium | 38.87721979000 | -76.98955066000
1/12/09 | 628127 | 0 | ANACOSTIA FWY | SE | 1/13/09 | 79465 | 7A129 | (Light out) | DA 1-12-09 @ 1015pm B. Black repaired pole #79465 | High Pressure Sodium | 38.88861563000 | -76.96080132000
1/12/09 | 628126 | 0 | KENILWORTH AVE | NE | 1/13/09 | 79462 | 7A126 | (Light out) | DA 1-12-09 @ 1000pm B. Black repaired pole #79462 | High Pressure Sodium | 38.89001850000 | -76.95803705000
1/12/09 | 628203 | 2712 | WISCONSIN AVE | NW | 1/14/09 | 30139 | 3G029 | (Light out) | DA 1-14-09 @ 225am V. Cooke repaired pole #30139dc- street light on metal is out , | High Pressure Sodium | 38.92532015000 | -77.07330634000
1/12/09 | 628112 | 810 | NEW HAMPSHIRE AVE | NW | 1/13/09 | 28356 | 2G658 | (Light out) |  | High Pressure Sodium | 38.89994754000 | -77.05265975000
1/12/09 | 628111 | 810 | NEW HAMPSHIRE AVE | NW | 1/13/09 | 28356 | 2G658 | (Light out) |  | High Pressure Sodium | 38.89994754000 | -77.05265975000
1/12/09 | 628110 | 810 | NEW HAMPSHIRE AVE | NW | 1/13/09 | 28356 | 2G658 | (Light out) |  | High Pressure Sodium | 38.89994754000 | -77.05265975000
1/12/09 | 628109 | 810 | NEW HAMPSHIRE AVE | NW | 1/15/09 | 28356 | 2G658 | (Light out) | DA 1-14-09 @ 1045pm V. Cooke repaired pole #28356 | High Pressure Sodium | 38.89994754000 | -77.05265975000
1/12/09 | 628193 | 3700 | NEW HAMPSHIRE AVE | NW | 1/14/09 | 4J333 | 4G235 | (Light out) | DA 1-14-09 @ 425am B. Black repaired pole #4j333 FRONT OF 3716 AND - TWO STREET LIGHTS ARE OUT, METAL POLE, PLEASE REPAIR. | High Pressure Sodium | 38.93668536000 | -77.02424031000
1/12/09 | 628186 | 1200 | 1ST ST | NE | 1/15/09 | 61243 | 6A273 | (Light out) | DA 1-14-09 @ 1117pm T. Richards repaired pole #61243 1200 FIRST STREET NE, WASHINGTON, DC IFO 1200 FIRST STREET NE, ABOUT MID BLOCK. - | High Pressure Sodium | 38.90637775000 | -77.00597499000
1/12/09 | 628029 | 0 | FLORIDA AVE | NE | 1/13/09 | 62313 | 5M114 | (Light out) | DA 1-13-09 @ 405am T. Richards repired pole #62313 | High Pressure Sodium | 38.90860897000 | -77.00417478000
1/12/09 | 628025 | 900 | 2ND ST | SW | 1/13/09 | 68129 | 6A416 | (Light out) | DeVon Smith bad address DA 1-13-09 @ 340am T. Richards poles 68129 and 68130 N/C underground | High Pressure Sodium | 38.87878241000 | -77.00287862000
1/12/09 | 628025 | 900 | 2ND ST | SW | 1/13/09 | 68129 | 68621 | (Light out) | DeVon Smith bad address DA 1-13-09 @ 340am T. Richards poles 68129 and 68130 N/C underground | High Pressure Sodium | 38.90623996000 | -77.01082515000
1/12/09 | 628016 | 2712 | WISCONSIN AVE | NW | 1/14/09 | 30139 | 3G029 | (Light out) | DA 1-13-09 @ 1120pm V. Cooke repaired pole #30139 | High Pressure Sodium | 38.92532015000 | -77.07330634000
1/12/09 | 628007 | 0 | SHERMAN AVE | NW | 1/12/09 | 14219 | 1G462 | (Light out) | DA 1-12-09 @ 1043pm K. Simmons repaired pole #14219 | High Pressure Sodium | 38.92198110000 | -77.02520587000
1/12/09 | 628005 | 457 | MASSACHUSETTS AVE | NW | 2/7/12 | 60481 | 6A195 | (Light out) | DA 1-13-09 @ 303am T. Richards pole #60481 N/C underground - has been refered to ddot wo #461351 | High Pressure Sodium | 38.90073307000 | -77.01753805000
1/9/09 | 627472 | 0 | C ST | SW | 3/12/09 | 21748 | 6A386 | (Light out) | RR, 3-12-09, Pepco completed connection and AVA Qced after. Light is energized. DA 1-12-09 @ 1107pm R. Warren pole #21748 N/C underground DA 1-12-09 @ 620am R. Warren installed 400mv bulb pole #21748 still needs 1 more 400 mv bulb | High Pressure Sodium | 38.88607059000 | -77.01250580000
1/9/09 | 627464 | 1457 | PARK RD | NW | 1/12/09 | 12702 | 1G375 | (Light out) | DA 1-11-09 @ 1155pm V. Cooke repaired pole #12702 | High Pressure Sodium | 38.93096473000 | -77.03479369000
1/8/09 | 626928 | 3901 | PENNSYLVANIA AVE | SE | 1/9/09 | 78528DC | 7E131DC | (Light out) | DA 1-9-09 @ 321am T. Richards pole #78528dc previously repaired using 400 hps bulb, TLP and tree trim refer to wo #625304 | High Pressure Sodium | 38.86609981000 | -76.95276035000
1/8/09 | 626926 | 3144 | PENNSYLVANIA AVE | SE | 1/9/09 | 78554DC | 7E101DC | (Light out) | DA 1-9-09 @ 221am T. Richards repaired pole #78554dc | High Pressure Sodium | 38.86981292000 | -76.96183892000
1/8/09 | 626923 | 0 | KENILWORTH AVE | SE | 1/13/09 | 79496 | 7A149 | (Light out) | DA 1-9-09 @ 535am T. Richards request for map wblack-1/13-repaired | High Pressure Sodium | 38.88522570000 | -76.96311007000
1/8/09 | 626919 | 4878 | NANNIE HELEN BURROUGHS AVE | NE | 1/12/09 | 71291DC | 7A221DC | (Light out) | DA 1-12-09 @ 139am T. Richards repaired pole #71291dc - attached plastic bird flap | High Pressure Sodium | 38.89881397000 | -76.93206898000
1/8/09 | 626802 | 2 | WESTMORELAND CIR | NW | 1/8/09 | 34380 | 3M038 | (Light out) | DA 1-7-09 @ 1040pm V. Cooke repaired pole #34380 | Mercury Vapor | 38.94941039000 | -77.10097492000
1/7/09 | 626391 | 0 | 7TH ST | NW | 1/7/09 | 22455 | 6M667 | (Light out) | DA 1-7-09 @ 1100pm R. Warren repaired pole #22455 | High Pressure Sodium | 38.90101301000 | -77.02181903000
1/7/09 | 626385 | 1500 | 18TH ST | NW | 1/8/09 | 26772 | 2M152 | (Light out) | DA 1-8-09 @ 423am R. Warren repaired pole #26772 | High Pressure Sodium | 38.91102666000 | -77.04173758000
1/7/09 | 626383 | 1301 | U ST | NW | 1/9/09 | 11721 | 1G521 | (Light out) | DA 1-9-09 @ 240am V. Cooke repaired pole #11721 | High Pressure Sodium | 38.91709342000 | -77.03069626000
1/7/09 | 626300 | 2730 | WISCONSIN AVE | NW | 1/12/09 | 30177 | 3G020 | (Light out) | DA 1-12-09 @ 240am V. Cooke repaired pole #30177 | High Pressure Sodium | 38.92608314000 | -77.07307216000
1/6/09 | 625922 | 809 | INTERSTATE 295 | NE | 1/6/09 | 79474 | 7A138 | (Light out) | DA 1-6-08 @ 1014pm T. Richards repaired pole #79474 | High Pressure Sodium | 38.88176234000 | -76.96414383000
1/6/09 | 625910 | 0 | 23RD ST | NW |  | 28318 | 2M274 | (Light out) | (VW) 1-14-08 R Waites Need new neck *no screws* broken screws DA 1-9-09 @ 205am R. Warren pole #28318 needs 400 hps kit. | High Pressure Sodium | 38.89313901000 | -77.05025238000
1/6/09 | 625904 | 812 | 7TH ST | NW | 1/7/09 | 22419 | 6M668 | (Light out) | DA 1-7-09 @ 340am S. Daniels repaired pole #22419 | High Pressure Sodium | 38.90058335000 | -77.02201480000
1/6/09 | 625901 | 0 | 7TH ST | NW | 1/7/09 | 22430 | 2A186 | (Light out) | DA 1-7-09 @ 336am S. Daniels pole #22430 N/C underground - duplicate ticket to wo #599768 | High Pressure Sodium | 38.89710115000 | -77.02201609000
1/6/09 | 625880 | 1125 | 11TH ST | NW |  | 25263 | 2M226 | (Light out) | DA 1-7-09 @ 415am S. Daniels - there are 2 lights out but can not access due to road construction - there are no visible signs with company name or phone number | High Pressure Sodium | 38.90526694000 | -77.02692404000
1/6/09 | 625878 | 1000 | H ST | NW | 1/9/09 | 22618 | 2G962 | (Light out) | DA 1-8-09 @ 1150pm R. Warren repaired pole #22618 | High Pressure Sodium | 38.89990719000 | -77.02660550000
1/6/09 | 625865 | 1717 | 17TH ST | NW | 1/8/09 | 26702 | 2M033 | (Light out) | DA 1-8-09 @ 335am R. Warren repaired pole #26702 | High Pressure Sodium | 38.91327520000 | -77.03840035000
1/6/09 | 625863 | 1500 | 18TH ST | NW | 1/8/09 | 26772 | 2M152 | (Light out) | DA 1-8-09 @ 423am R. Warren repaired pole #26772 using 400 hps bulb refer to wo #626385 | High Pressure Sodium | 38.91102666000 | -77.04173758000
1/6/09 | 625944 | 0 | 18TH ST | NW | 2/7/12 | 24534 | 2U529 | (Light out) | DA 1-9-09 @ 520am R. Warren pole #24534 Teardrop fixture refer to Ddot need wire ran fron top of pole to T base- - there is a streetlights (metal poles) are out and needs to be fixed. | High Pressure Sodium | 38.90591907000 | -77.04143681000
1/6/09 | 625943 | 0 | 18TH ST | NW | 2/7/12 | 24534 | 2U529 | (Light out) | DA 1-9-09 @ 520am R. Warren pole #24534 Teardrop fixture refer to Ddot need wire ran fron top of pole to T base- there are three streetlights (metal poles) are out and need to be fixed. | High Pressure Sodium | 38.90591907000 | -77.04143681000
1/5/09 | 625305 | 3901 | ALABAMA AVE | SE | 1/7/09 | 78524DC | 7E137 | (Light out) | DA 1-7-09 @ 219am T. Richards repaired pole #78524dc | High Pressure Sodium | 38.86548351000 | -76.95124229000
1/5/09 | 625304 | 3901 | PENNSYLVANIA AVE | SE | 1/7/09 | 78528DC | 7E131DC | (Light out) | DA 1-7-09 @ 225am T. Richards repaired pole #78528dc | High Pressure Sodium | 38.86609981000 | -76.95276035000
1/5/09 | 625278 | 2313 | MARTIN LUTHER KING JR AVE | SE | 1/6/09 | 82042DC | 82042 | (Light out) | DA 1-6-09 @ 333am R. Warren repaired pole #82042dc | High Pressure Sodium | 38.86321311000 | -76.99157505000
1/5/09 | 625268 | 920 | 11TH ST | SE | 1/8/09 | 66049 | 6L998 | (Light out) | DA 1-8-09 @ 244am T. Richards repaired pole #66049 (VW) 1-7-09 Pitts/Osvatics inst TLPC | High Pressure Sodium | 38.87853361000 | -76.99164274000
1/5/09 | 625267 | 400 | L ST | SE | 1/26/09 | 67702 | 6B462 | (Light out) | DA 1-7-09 @ 512am K. simmons pole #67702 N/C underground - there is alot of construction in area but no sign with company name or phone | High Pressure Sodium | 38.87758613000 | -77.00028077000
1/5/09 | 625265 | 1100 | HALF ST | SE | 1/7/09 | 67435 | 6B100 | (Light out) | DA 1-7-09 @ 523am K. Simmons repaired pole #67435 | High Pressure Sodium | 38.87824281000 | -77.00752674000
1/5/09 | 625356 | 0 | O ST | NE | 1/8/09 | 62314 | 5M113 | (Light out) | DA 1-8-09 @ 207am R. Warren repaired pole #62314 using 150 hps bulb refer to wo #625355 1401 CHURCH STREET NW, WASHINGTON, DC CORNER OF 14TH AND CHURCH - | High Pressure Sodium | 38.90852329000 | -77.00447657000
1/5/09 | 625353 | 36 | PORTER PL | NE | 1/8/09 | 56992 | 5M146 | (Light out) | - (VW) 1-8-09 Pitts/Osvatics Previously Repaired SIDE ON PORTER - streetlight out on metal pole, would like to have it repaired. pole #56992 | High Pressure Sodium | 38.91041299000 | -77.00788639000
1/5/09 | 625207 | 301 | MASSACHUSETTS AVE | NW | 1/6/09 | 60399 | 6A198 | (Light out) | DA 1-6-09 @ 1212am T. Richards pole #60399 light found okay | High Pressure Sodium | 38.90029659000 | -77.01558775000
1/2/09 | 624738 | 0 | P ST | NE | 1/5/09 | 57340 | 5M093 | (Light out) | DA 1-4-09 @ 1152pm K. Simmons repaired pole #57340 - installed and adjusted TLP meta pole # 57340 streetlight os on all the time, req imm repair | High Pressure Sodium | 38.90964250000 | -77.00656798000
1/2/09 | 624732 | 3267 | P ST | NW | 1/6/09 | 21017 | 2G142 | (Light out) | DA 1-6-09 @ 320am V. Cooke repaired pole #21017 - reset photocell DA 1-5-09 S. Daniels - Needs Van STREET SIDE - | High Pressure Sodium | 38.90886358000 | -77.06536598000
1/2/09 | 624587 | 2307 | WASHINGTON CIR | NW | 1/5/09 | 24654 | 2G670 | (Light out) | DA 1-5-09 @ 140am S. Daniels repaired pole #24654 | High Pressure Sodium | 38.90298616000 | -77.05064992000
1/1/09 | 624562 | 3300 | SHERMAN AVE | NW | 1/2/09 | 12896 | 1L282 | (Light out) | DA 1-2-09 @ 325am V. Cooke repaired pole #12896 FRONT - METAL POLE LIGHT IS OUT | High Pressure Sodium | 38.93114546000 | -77.02668665000
12/31/08 | 624151 | 127 | PIERCE ST | NW | 1/13/09 | 61097 | 6S262 | (Light out) | DA 1-5-09 @ 255am T. Richards pole #61097 light on and working - needs globe FRONT - is a metal pole is out about 4 days | High Pressure Sodium | 38.90464361000 | -77.01368699000
12/31/08 | 624091 | 1604 | 7TH ST | NW | 1/1/09 | 25653 | 6A819 | (No current) |  | High Pressure Sodium | 38.91140348000 | -77.02202187000
12/31/08 | 624075 | 809 | INTERSTATE 295 | NE | 1/6/09 | 79474 | 7A138 | (Light out) | DA 1-6-08 B. Black repaired teardrop fixture on pole #79474 (400 hps ballast kit) DA 1-5-09 S. Daniels removed teardrop fixture pole #79474 DA 1-2-09 @ 1227am T. Richards pole #79474 bad Transformer (teardrop fixture) | High Pressure Sodium | 38.88176234000 | -76.96414383000
12/31/08 | 624020 | 1000 | KENYON ST | NW | 1/2/09 | 12866 | 1L266 | (Light out) | DA 1-2-09 @ 130am S. Daniels repaired pole #12866 - spliced feed wire @ fixture | High Pressure Sodium | 38.92984478000 | -77.02653870000
12/30/08 | 623461 | 300 | L ST | SE | 12/31/08 | 67700 | 6A440 | (Light out) | DA 12-31-08 @ 201am T. Richards repaired pole #67700 | High Pressure Sodium | 38.87758686000 | -77.00135522000
12/30/08 | 623413 | 2319 | PENNSYLVANIA AVE | NW | 12/31/08 | 24653 | 2G667 | (Light out) | DA 12-31-08 @ 1220am S. Daniels repaired pole #24653 | High Pressure Sodium | 38.90301348000 | -77.05112594000
12/30/08 | 623411 | 2307 | WASHINGTON CIR | NW | 1/5/09 | 24654 | 2G670 | (Light out) | DA 12-31-08 @ 1230am S. Daniels repaired pole #24654 | High Pressure Sodium | 38.90298616000 | -77.05064992000
12/30/08 | 623405 | 1318 | 11TH ST | NW | 12/31/08 | 25281 | 2M249 | (Light out) | DA 12-31-08 @ 345am S. Daniels repaired pole #25281 | High Pressure Sodium | 38.90771911000 | -77.02715269000
12/30/08 | 623346 | 1604 | 7TH ST | NW | 1/17/09 | 25653 | 6A819 | (No current) | Damien & K. Greenfield unable to route from manhole of the pole. | High Pressure Sodium | 38.91140348000 | -77.02202187000
12/30/08 | 623319 | 1700 | 3RD ST | NW | 12/30/08 | 59992 | 5A183 | (Light out) | DA 12-30-08 @ 120am K. Simmons repaired pole #59992 | High Pressure Sodium | 38.91426862000 | -77.01583923000
12/29/08 | 622785 | 0 | H ST | NE | 12/29/08 | 62354 | 6S136 | (Light out) | DA 12-29-08 @ 1001pm T. Richards repaired pole #62354 | High Pressure Sodium | 38.90011064000 | -76.98535317000
12/29/08 | 622832 | 801 | H ST | NE | 12/31/08 | 62045 | 6S085 | (Light out) | DA 12-31-08 @ 1217am T. Richards reattached globe pole #62045 INTERSECTION OF - caller reports hanging globe | High Pressure Sodium | 38.90011889000 | -76.99480309000
12/29/08 | 622822 | 127 | PIERCE ST | NW | 12/31/08 | 61097 | 6S262 | (Light out) | DA 12-31-08 @ 258am T. Richards repaired pole #61097 FRONT - is a metal pole is out about 4 days | High Pressure Sodium | 38.90464361000 | -77.01368699000
12/29/08 | 622749 | 0 | KANSAS AVE | NW | 12/31/08 | 4K568 | 4G321 | (Light off/on) | DA 12-31-08 @ 257am R. Warren repaired pole #4k568 | High Pressure Sodium | 38.94326049000 | -77.02502562000
12/29/08 | 622743 | 4200 | 13TH ST | NW | 12/30/08 | 4J609 | 4U151 | (Light out) | DA 12-30-08 @ 400am R. Warren repaired pole #4j609 | High Pressure Sodium | 38.94196034000 | -77.02962652000
12/29/08 | 622741 | 1300 | MAINE AVE | SW | 12/30/08 | 66531 | 6M443 | (Light out) | DA 12-30-08 @ 211am T. Richards repaired pole #66531 -respliced t base | High Pressure Sodium | 38.88186010000 | -77.02828319000
12/29/08 | 622740 | 800 | 11TH ST | NW | 12/30/08 | 23378 | 2L020 | (Light out) | DA 12-30-08 @ 1205am S. Daniels repaired pole #23378 | High Pressure Sodium | 38.90015315000 | -77.02690628000
12/29/08 | 622732 | 0 | SOUTH DAKOTA AVE | NE | 12/29/08 | 58403 | 5M164 | (Light out) | DA 12-29-08 @ 304am K. Simmons repaired pole #58403 | High Pressure Sodium | 38.92284218000 | -76.96150143000
12/24/08 | 621832 | 800 | 11TH ST | NW | 12/29/08 | 23378 | 2L020 | (Light out) | DA 12-29-08 @ 240am S. Daniels repaired pole #23378 | High Pressure Sodium | 38.90015315000 | -77.02690628000
12/24/08 | 621827 | 0 | 7TH ST | NW | 12/29/08 | 22452 | 6M651 | (Light off/on) | DA 12-29-08 @ 345am S. Daniels repaired pole #22452 | High Pressure Sodium | 38.89955549000 | -77.02182020000
12/24/08 | 621819 | 4235 | 9TH ST | NW | 12/29/08 | 4K017 | 4G319 | (Light out) | DA 12-29-08 @ 1111pm R. Warren repaired pole #4k017 | High Pressure Sodium | 38.94272297000 | -77.02520204000
12/24/08 | 621786 | 3321 | IDAHO AVE | NW | 10/27/09 | 38888DC | 3U416 | (Light out) | DA 12-24-08 @ 155am V. Cooke pole #38888dc refer to ddot defective 400mv fixture | Mercury Vapor | 38.93408385000 | -77.07471732000
12/24/08 | 621785 | 2420 | WISCONSIN AVE | NW | 12/24/08 | 30147 | 3G067 | (Light out) | DA 12-24-08 @ 100am V. Cooke repaired pole #30147 | High Pressure Sodium | 38.92145383000 | -77.07236458000
12/23/08 | 621264 | 2307 | WASHINGTON CIR | NW | 12/24/08 | 24654 | 2G670 | (Light out) | DA 12-24-08 @ 220am S. Daniels repaired pole #24654 | High Pressure Sodium | 38.90298616000 | -77.05064992000
12/23/08 | 621261 | 801 | P ST | NW | 12/24/08 | 25808 | 6U460 | (Light out) | DA 12-24-08 @ 315am S. Daniels repaired pole #25808 | High Pressure Sodium | 38.90960163000 | -77.02357636000
12/22/08 | 620729 | 4000 | GEORGIA AVE | NW | 12/23/08 | 4J344 | 4G271 | (Light out) | DA 12-23-08 @ 1233am R. Warren repaired pole #4j344 | High Pressure Sodium | 38.93997233000 | -77.02490813000
12/22/08 | 620724 | 790 | 3RD ST | NE | 12/23/08 | 61519 | 6S046 | (Light out) | DA 12-23-08 @ 1248am T. Richards repaired pole #61519 | High Pressure Sodium | 38.90011266000 | -77.00193249000
12/22/08 | 620722 | 0 | M ST | NW | 12/23/08 | 23739 | 2G718 | (Light out) | DA 12-23-08 @ 225an S. Daniels repaired pole #23739 | High Pressure Sodium | 38.90513126000 | -77.04778068000
12/22/08 | 620683 | 4829 | NORTH CAPITOL ST | NW | 12/22/08 | 4R750 | 4A791 | (Light out) | DA 12-22-08 @ 220am V. Cooke repaired pole #4r750 | High Pressure Sodium | 38.94981176000 | -77.00891482000
12/22/08 | 620676 | 4500 | ROCK CREEK CHURCH RD | NE | 12/22/08 | 4R757 | 4A798 | (Light out) | DA 12-22-08 @ 155am V. Cooke repaired pole #4r757 | High Pressure Sodium | 38.94697525000 | -77.00871139000
12/18/08 | 619533 | 1826 | CALVERT ST | NW | 12/22/08 | 10729 | 1A013 | (Light out) | DA 12-22-08 @ 145am S. Daniels pole #10729 N/C underground LANIER AND CALVERT ST NW, THE NORTHEAST CORNER - streetlight is out, please repair. | High Pressure Sodium | 38.92339148000 | -77.04377813000
12/18/08 | 619524 | 1010 | MASSACHUSETTS AVE | NW | 12/22/08 | 25961 | 2M216 | (Light out) | DA 12-22-08 @ 210am S. Daniels repaired pole #25961 - adjusted photocell - street light on metal pole is out , | High Pressure Sodium | 38.90379985000 | -77.02690625000
12/17/08 | 618810 | 100 | FLORIDA AVE | NE | 12/18/08 | 56989 | 5M139 | (Light out) | DA 12-18-08 @ 1045pm K. Simmons adjusted TL photocell - light on and working | High Pressure Sodium | 38.90947523000 | -77.00574268000
12/17/08 | 618807 | 608 | CHAPLIN ST | SE |  | 76166 | 76166DC | (Light out) | DA 12-+18-08 @ 402am T. Richards pole #76166 N/C to overhead 3-3-09 S.Manning---remove tag(sconnor) | Mercury Vapor | 38.88137771000 | -76.93991272000
12/17/08 | 618575 | 0 | E ST | NW | 12/17/08 | 23334 | 2M356 | (Light out) | DA 12-17-08 @ 100am S. Daniels repaired pole #23334 | High Pressure Sodium | 38.89621967000 | -77.02247784000
12/17/08 | 618145 | 702 | 7TH ST | NW | 12/17/08 | 22427 | 6M642 | (Light out) | DA 12-17-08 @ 1250am S. Daniels repaired pole #22427 | High Pressure Sodium | 38.89872648000 | -77.02201436000
12/16/08 | 618080 | 1500 | KEARNEY ST | NE | 12/17/08 | 59986 | 5A177 | (Light out) | DA 12-17-08 @ 352am pole #59986 light found on and working | High Pressure Sodium | 38.91401980000 | -77.01759054000
12/16/08 | 618045 | 3400 | 14TH ST | NW | 12/16/08 | 13677 | 1G075 | (Light out) | DA 12-16-08 S. Daniels pole #13677 previously repaired using 400 hps bulb and TLP refer to wo #617224 | High Pressure Sodium | 38.93148309000 | -77.03266734000
12/16/08 | 618044 | 3112 | SHERMAN AVE | NW | 12/17/08 | 12857 | 1L258 | (Light out) | DA 12-16-08 @ 1035pm S. Daniels repaired pole #12857 | High Pressure Sodium | 38.92921064000 | -77.02639391000
12/16/08 | 618032 | 4235 | 9TH ST | NW | 12/17/08 | 4K017 | 4G319 | (Light out) | DA 12-17-08 @ 120am R. Warren repaired pole #4k017 | High Pressure Sodium | 38.94272297000 | -77.02520204000
12/16/08 | 618157 | 815 | KENNEDY ST | NW | 12/23/08 | 4M078 | 4M078DC | (Light out) | (VW) 12-23-08 K Greenfield/Dixon Made secondary tap at feed pole DA 12-18-08 @ 1223am R. Warren pole #4m078 FRONT - WOODEN POLE HAS BEEN OUT FOR SIX WEEKS | High Pressure Sodium | 38.95637067000 | -77.02492280000
12/15/08 | 617224 | 3400 | 14TH ST | NW | 12/16/08 | 13677 | 1G075 | (Light out) | DA 12-16-08 @ 315am S. Daniels repaired pole #13677 R Rapolla, 12-15-2008, referred by Jama Abdi | High Pressure Sodium | 38.93148309000 | -77.03266734000
12/15/08 | 617213 | 3150 | PENNSYLVANIA AVE | SE | 12/15/08 | 78552DC | 7E103DC | (Light out) | DA 12-15-08 @ 237am T. Richards repaired pole #78552dc | High Pressure Sodium | 38.86951864000 | -76.96115222000
12/12/08 | 616668 | 1010 | MASSACHUSETTS AVE | NW | 12/15/08 | 25961 | 2M216 | (Light out) | DA 12-15-08 @ 305am S. daniels Repaired pole #25961 | High Pressure Sodium | 38.90379985000 | -77.02690625000
12/12/08 | 616664 | 0 | 8TH ST | NW | 12/15/08 | 25807 | 6U463 | (Light out) | DA 12-15-08 @ 1110pm S. Daniels repaired pole #25807 | High Pressure Sodium | 38.90960201000 | -77.02275747000
12/12/08 | 616663 | 1541 | 7TH ST | NW | 12/15/08 | 25702 | 6A814 | (Light out) | DA 12-15-08 @ 1100pm S. Daniels repaired pole #25702 DA 12-15-08 @ 350am S. Daniels pole #25702 Needs 400hps power door | High Pressure Sodium | 38.91080483000 | -77.02182504000
12/12/08 | 616723 | 3100 | PENNSYLVANIA AVE | SE | 12/16/08 | 78560DC | 7E094DC | (Light out) | DA 12-15-08 @ 231am T. Richards pole #78560dc N/C to overhead STREET - CALLER IS REPORTING THAT THERE ARE SEVEN STREETLIGHT THAT ARE OUT AT THIS INTERSECTION AND ALSO AT PENNSYLVANIA AVE AND BRANCH AVE S.E. | High Pressure Sodium | 38.87059877000 | -76.96377234000
12/11/08 | 616001 | 1101 | BRENTWOOD RD | NE | 12/11/08 | 56628 | 5A245 | (Light off/on) | DA 12-11-08 @ 439am K. Simmons repaired pole #56628 | High Pressure Sodium | 38.91929246000 | -76.99152893000
12/11/08 | 616000 | 1101 | BRENTWOOD RD | NE | 12/11/08 | 56629 | 5A246 | (Light out) | DA 12-11-08 @ 434am K. Simmons repaired pole #56629 | High Pressure Sodium | 38.91961170000 | -76.99119145000
12/10/08 | 615520 | 0 | KANSAS AVE | NW | 12/18/08 | 4K568 | 4G321 | (Light out) | DA 12-10-08 @ 1150pm R. Warren pole #4k568- N/C underground - | High Pressure Sodium | 38.94326049000 | -77.02502562000
12/10/08 | 615498 | 3100 | PENNSYLVANIA AVE | SE | 12/16/08 | 78563 | 7E057 | (Light out) | DA 12-11-08 @ 103am T. Richards pole #78563 N/C underground - traffic pole | High Pressure Sodium | 38.87122821000 | -76.96470218000
12/10/08 | 615497 | 3100 | PENNSYLVANIA AVE | SE | 12/16/08 | 78562DC | 7E092DC | (Light out) | DA 12-11-08 @ 103am T. Richards pole #78562dc N/C to Overhead | High Pressure Sodium | 38.87088102000 | -76.96446252000
12/10/08 | 615496 | 3000 | PENNSYLVANIA AVE | SE | 12/16/08 | 78561DC | 7E093DC | (Light out) | DA 12-11-08 @ 103am T. Richards pole #78561dc N/C to Overhead | High Pressure Sodium | 38.87074474000 | -76.96412983000
12/10/08 | 615495 | 3100 | PENNSYLVANIA AVE | SE | 12/16/08 | 78560DC | 7E094DC | (Light out) | DA 12-11-08 @ 103am T. Richards pole #78560dc N/C to Overhead | High Pressure Sodium | 38.87059877000 | -76.96377234000
12/10/08 | 615494 | 3101 | PENNSYLVANIA AVE | SE | 12/11/08 | 78557DC | 7E098DC | (Light out) | DA 12-11-08 @ 110am T. Richards repaired pole #78557dc | High Pressure Sodium | 38.87018089000 | -76.96274548000
12/10/08 | 615394 | 4709 | NORTH CAPITOL ST | NE | 12/10/08 | 4R753 | 4A794 | (Light out) | DA 12-10-08 @ 130am K. Simmons repaired pole #4r753 | High Pressure Sodium | 38.94851572000 | -77.00881793000
12/9/08 | 614885 | 0 | WISCONSIN AVE | NW | 12/13/08 | 30135 | 3G009 | (Light off/on) | DA 12-11-08 @ 1245am V. Cook pole #30135 N/C underground broken neturial - Traffic pole | High Pressure Sodium | 38.92744531000 | -77.07330577000
12/9/08 | 614856 | 3931 | PENNSYLVANIA AVE | SE | 12/10/08 | 78520DC | 7E146DC | (Light out) | DA 12-10-08 @ 101am T. Richards repaired pole #78520dc | High Pressure Sodium | 38.86439405000 | -76.94857392000
12/9/08 | 614753 | 0 | KANSAS AVE | NW | 12/10/08 | 4K568 | 4G321 | (Light out) | DA 12-09-08 @ 1127pm R. Warren repaired pole #4K568 | High Pressure Sodium | 38.94326049000 | -77.02502562000
12/9/08 | 614231 | 633 | INDIANA AVE | NW | 12/9/08 | 60665 | 6S565 | (Light out) | DA 12-09-08 @ 1217am T. richards repaired pole #60665 | High Pressure Sodium | 38.89413265000 | -77.02076751000
12/8/08 | 614140 | 929 | MONROE ST | NE | 12/10/08 | 56163 | 56163DC | (Light out) | DA 12-10-08 @ 400am K. Simmons wires were reattached earlier today DA 12-09-08 @ 300am K. Simmons pole #56163 no wires coming from ground left by 3rd party Contractor , pole not hooked up - refer to ddot | High Pressure Sodium | 38.93252669000 | -76.99290402000
12/8/08 | 614074 | 0 | RIGGS RD | NE | 12/8/08 | 4P559DC | 4U185 | (Light out) | DA 12-07-08 @ 1135pm K. Simmons repaired pole #4p559dc | High Pressure Sodium | 38.95729012000 | -77.00222944000
12/7/08 | 614073 | 4709 | NORTH CAPITOL ST | NE | 12/8/08 | 4R753 | 4A794 | (Light out) | DA 12-07-08 @ 1125pm K. Simmons repaired pole #4R753 | High Pressure Sodium | 38.94851572000 | -77.00881793000
12/5/08 | 613586 | 462 | K ST | NW | 2/6/12 | 60463 | 6A113 | (Light out) | DA 12-11-08 @ 307am T. Richards pole #60463 N/C underground (pole is not taped- tech ran out) | High Pressure Sodium | 38.90260167000 | -77.01799763000
12/5/08 | 613585 | 841 | 7TH ST | NW | 12/10/08 | 22422 | 6M662 | (Light out) | DA 12-10-08 @ 325am S. Daniels repaired pole #22422 ran 80ft #10 wire and respliced hot and neturial @ base using rubber and black tape, scotch kote and 2 #8 butt splices DA 12-08-08 @ 355am S. Daniels pole #22422 needs neturial pulled | High Pressure Sodium | 38.90021373000 | -77.02201497000
12/5/08 | 613578 | 1778 | U ST | NW | 12/9/08 | 26113 | 21412 | (Light out) | DA 12-09-08 @ 225am S. Daniels repaired pole #26113 | High Pressure Sodium | 38.91688186000 | -77.04131949000
12/5/08 | 613543 | 702 | 7TH ST | NW | 12/9/08 | 22427 | 6M642 | (Light out) | DA 12-09-08 @ 330am S. Daniels repaired pole #22427 | High Pressure Sodium | 38.89872648000 | -77.02201436000
12/4/08 | 612926 | 3400 | 14TH ST | NW | 12/5/08 | 13679 | 1G079 | (Light out) | DA 12-04-08 @ 1150pm S. Daniels installed 400 hps bulb pole #13679 | High Pressure Sodium | 38.93178878000 | -77.03266428000
12/4/08 | 612853 | 1403 | KEARNEY ST | NW | 12/4/08 | 59990 | 5A182 | (Light out) | DA 12-04-08 @ 335am K. Simmons repaired pole #59990 | High Pressure Sodium | 38.91424947000 | -77.01606264000
12/4/08 | 612844 | 0 | 22ND ST | NW | 12/4/08 | 28283 | 2G696 | (Light out) | DA 12-04-08 @ 250am S. Daniels repaired pole #28283 | High Pressure Sodium | 38.90192527000 | -77.04889687000
12/4/08 | 612838 | 630 | E ST | SW | 12/10/08 | 21619 | 6A320 | (Light out) | wblack-12/9-tried to gain access through security contractor and was denied("private property") DA 12-08-08 @ 250am S. Daniels did not feel it was safe the distance he had to go to reach the pole #21619 12-05-08 @ 205am S. Daniels pole #21619 could not | High Pressure Sodium | 38.88336354000 | -77.02178186000
12/3/08 | 612155 | 740 | 6TH ST | NW | 12/4/08 | 22514 | 6S426 | (Light out) | DA 12-04-08 @ 1253am S. Daniels repaired pole #22514 | High Pressure Sodium | 38.89941296000 | -77.02001456000
12/3/08 | 612154 | 740 | 6TH ST | NW | 12/4/08 | 22513 | 6S425 | (Light out) | DA 12-04-08 @ 1245am S. Daniels repaired pole #22513 | High Pressure Sodium | 38.89950950000 | -77.02001122000
12/3/08 | 612136 | 1300 | BRYANT ST | NE | 12/3/08 | 51336DC | 5A254 | (Light out) | DA 12-03-08 @ 430am K. Simmons repaired pole #51336dc | High Pressure Sodium | 38.92097735000 | -76.98895164000
12/3/08 | 612126 | 1904 | 18TH ST | NW | 12/3/08 | 26782 | 2M096 | (Light out) | DA 12-03-08 @ 310am S. Daniels repaired pole #26782 | High Pressure Sodium | 38.91581064000 | -77.04174130000
12/3/08 | 611614 | 4001 | 12TH ST | NE | 12/3/08 | 55674 | 50944 | (Light out) | DA 12-03-08 @ 1230am K. Simmons repaired pole #55674 | High Pressure Sodium | 38.93852977000 | -76.99040955000
12/2/08 | 611544 | 5403 | NANNIE HELEN BURROUGHS AVE | NE | 12/3/08 | 72648 | 7A191 | (Light out) | DA 12-02-08 @ 1139pm T. Richards repaired pole #72648 | High Pressure Sodium | 38.89829839000 | -76.92250388000
12/2/08 | 611543 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 12/3/08 | 72645 | 7S073 | (Light out) | DA 12-02-08 @ 1101pm T. Richards repaired pole #72645 - redirected photocell | High Pressure Sodium | 38.89826452000 | -76.92554310000
12/2/08 | 611437 | 841 | 7TH ST | NW | 12/2/08 | 22422 | 6M662 | (Light out) | DA 12-02-08 @ 350am S. Daniels repaired pole #22422 | High Pressure Sodium | 38.90021373000 | -77.02201497000
12/1/08 | 610851 | 408 | RHODE ISLAND AVE | NW | 12/2/08 | 59989 | 5A181 | (Light out) | DA 12-02-08 @ 1230am K. simmons repaired pole #59989 | High Pressure Sodium | 38.91392931000 | -77.01700898000
12/1/08 | 610850 | 1403 | KEARNEY ST | NW | 12/2/08 | 59990 | 5A182 | (Light out) | DA 12-02-08 @ 1235am K. Simmons repaired pole #59990 | High Pressure Sodium | 38.91424947000 | -77.01606264000
12/1/08 | 610826 | 2318 | 32ND ST | SE | 12/1/08 | 74838DC | 7A102DC | (Light out) | DA 12-01-08 @ 1015pm T. Richards pole #74838dc - all lights are on and working after N/C to overhead was repaired refer to wo #610731 Hansen #1977606 | High Pressure Sodium | 38.86110733000 | -76.96087329000
12/1/08 | 610890 | 3209 | ALABAMA AVE | SE | 12/3/08 | 74836DC | 7A100DC | (Light out) | DA 12-03-08 @ 220am T. richards pole #74836dc light has been repaired on and working- wooden pole alleylight out 1 week, req imm replacement | High Pressure Sodium | 38.86132638000 | -76.96088830000
12/1/08 | 610887 | 2318 | 32ND ST | SE | 12/3/08 | 74839DC | 7A103DC | (Light out) | DA 12-03-08 @ 211aam T. Richards pole #74839dc light is on and working BEHIND - THIS WOODEN LIGHT POLE SHOULD NOT HAVE BEEN CLOSED OUT IF THE LIGHT IS STILL OUT, PLEASE COME AND REPAIR THE LIGHT PROPERLY, THANK YOU. OLD CONFIRMATION # 1967831 | High Pressure Sodium | 38.86076984000 | -76.96087210000
12/1/08 | 610804 | 0 | MASSACHUSETTS AVE | NW | 12/1/08 | 25964 | 2G953 | (Light out) | DA 12-01-08 @ 325am S. Daniels repaired pole #25964 | High Pressure Sodium | 38.90320032000 | -77.02510725000
12/1/08 | 610786 | 509 | 7TH ST | NW | 12/2/08 | 22431 | 6M628 | (Light out) | CP 12/2 - H Lancaster DA 12-01-08 @ 1240am S. Daniels pole #22431 N/C underground | High Pressure Sodium | 38.89648966000 | -77.02200839000
12/1/08 | 610785 | 629 | H ST | NW | 12/1/08 | 22562 | 6M698 | (Light out) | DA 12-01-08 @ 1230am S. Daniels repaired pole #22562 | High Pressure Sodium | 38.89973430000 | -77.02106497000
11/28/08 | 610731 | 2318 | 32ND ST | SE | 12/1/08 | 74838DC | 7A102DC | (Light out) | DA 12-01-08 @ 1227am T. Richards low voltage overhead 2315 33RD STREET ALLEY SE, WASHINGTON, DC ALLEY BEHIND ADDRESS - | High Pressure Sodium | 38.86110733000 | -76.96087329000
11/26/08 | 609856 | 3321 | IDAHO AVE | NW | 11/28/08 | 38888DC | 3U416 | (Light out) | R Rapolla, 11-28-2008, closed due to duplicate, WO#573095 | Mercury Vapor | 38.93408385000 | -77.07471732000
11/26/08 | 609714 | 2307 | WASHINGTON CIR | NW | 11/26/08 | 24654 | 2G670 | (Light out) | DA 11-26-08 @ 150am S. Daniels repaired pole #24664 | High Pressure Sodium | 38.90298616000 | -77.05064992000
11/25/08 | 609198 | 644 | H ST | NE | 11/25/08 | 61868 | 6S201 | (Light out) | DA 11-25-08 T. Richards respliced T Base pole #61868 ( elec. and rubber tape, scotch kote, 2 #8 butt splices ) | High Pressure Sodium | 38.90030139000 | -76.99660270000
11/25/08 | 609197 | 775 | H ST | NE | 11/25/08 | 61991 | 6S197 | (Light out) | DA 11-25-08 T. Richards respliced T Base pole #61991 ( elec. and rubber tape, scotch kote, 2 #8 butt splices ) | High Pressure Sodium | 38.90030060000 | -76.99586046000
11/25/08 | 609251 | 900 | UPSHUR ST | NW | 11/30/08 | 4J744 | 4G330 | (Light out) | DA 11-30-08 @ 1027pm R. Warren repaired pole #4J744 - street light on metal pole is out ,pole # 4j744 | High Pressure Sodium | 38.94182164000 | -77.02494834000
11/25/08 | 609211 | 3221 | CONNECTICUT AVE | NW | 2/24/09 | 30101 | 30423 | (Light out) | Pole is abandoned - new pole installed two feet away - 12/2 - H lancaster DA 12-01-08 @ 325am C. Ashton pole #30101 N/C underground FRONT - two street lights are out on a metal pole. | High Pressure Sodium | 38.93328522000 | -77.05704960000
11/25/08 | 609216 | 2318 | 32ND ST | SE | 12/1/08 | 74838DC | 7A102DC | (Light out) | DA 12-01-08 @ 1227am pole #74838dc N/C overhead duplicate ticket to wo #610731 Hansen #1977606 REAR - lights are out wood pole | High Pressure Sodium | 38.86110733000 | -76.96087329000
11/25/08 | 609045 | 0 | RIGGS RD | NE | 11/25/08 | 4P555DC | 4U176 | (Light out) | DA 11-25-08 @ 150am K. Simmons repaired pole #4p555dc | High Pressure Sodium | 38.95872032000 | -77.00127918000
11/24/08 | 608492 | 388 | H ST | NE | 11/24/08 | 61522 | 6S224 | (Light out) | DA 11-24-08 @ 1045pm T. Richards repaired pole #61522 | High Pressure Sodium | 38.90030233000 | -77.00072209000
11/24/08 | 608080 | 3200 | SHERMAN AVE | NW | 11/24/08 | 12873 | 1L276 | (Light out) | DA 11-24-08 @ 255am S. Daniels repaired pole #12873 | High Pressure Sodium | 38.93069190000 | -77.02661599000
11/24/08 | 608068 | 1021 | BRENTWOOD RD | NE | 11/24/08 | 51329DC | 5A240 | (Light out) | DA 11-24-08 @ 110am K. simmons repaired pole #51329dc | High Pressure Sodium | 38.91864300000 | -76.99199062000
11/24/08 | 608057 | 3209 | ALABAMA AVE | SE | 11/24/08 | 74836DC | 7A100DC | (Light out) | DA 11-23-08 @ 1150pm K. Simmons pole #74836dc low voltage - refer to overhead crew | High Pressure Sodium | 38.86132638000 | -76.96088830000
11/21/08 | 608031 | 2318 | 32ND ST | SE | 11/24/08 | 74839DC | 7A103DC | (Light out) | DA 11-23-08 @ 1140pm K. Simmons pole #74839dc low voltage 85 - refer to overhead crew 2315 33RD STREET SE ALLEY SE AND ALABAMA AVENUE ALLEY SE AND ALLEY SE, WASHINGTON, DC BEHIND 2315 33RD STREET SE - | High Pressure Sodium | 38.86076984000 | -76.96087210000
11/21/08 | 607828 | 0 | L ST | NE | 11/24/08 | 61206 | 6S237 | (Light out) | DA 11-24-08 @ 223am T. Richards repaired pole #61206 | High Pressure Sodium | 38.90378817000 | -77.00651378000
11/21/08 | 608034 | 3700 | GEORGIA AVE | NW | 11/25/08 | 4J359 | 4G236 | (Light out) | DA 11-25-08 @ 147am R. Warren repaired pole #4j359 ON THE GEORGIA AVENUE NW SIDE NEAR THE BUS STOP - | High Pressure Sodium | 38.93654675000 | -77.02448015000
11/20/08 | 607095 | 4709 | NORTH CAPITOL ST | NE | 11/20/08 | 4R753 | 4A794 | (Light out) | DA 1-20-08 @ 225am K . Simmons repaired pole #4R753dc | High Pressure Sodium | 38.94851572000 | -77.00881793000
11/19/08 | 606608 | 0 | 18TH ST | NW | 2/6/12 | 24534 | 2U529 | (No current) | Third party itear drop fixture nstallation is incomplete | High Pressure Sodium | 38.90591907000 | -77.04143681000
11/19/08 | 606505 | 0 | SEATON ST | NW | 11/19/08 | 11451 | 1A100 | (Light out) | DA 11-19-08 @ 405am S. Daniels repaired pole #11451 | High Pressure Sodium | 38.91753869000 | -77.04044580000
11/17/08 | 605264 | 2927 | PENNSYLVANIA AVE | SE | 11/18/08 | 78565DC | 7E090DC | (Light out) | DA 11-18-08 @ 1215am K. Simmons repaired pole #78565dc | High Pressure Sodium | 38.87118582000 | -76.96520944000
11/17/08 | 605336 | 2318 | 32ND ST | SE | 11/20/08 | 74839DC | 7A103DC | (Light out) | DA 11-19-08 @ 328am T. Richards poles 74839dc, 74836dc, and 74838dc N/C to Overhead BEHIND - light out....wooden pole | High Pressure Sodium | 38.86076984000 | -76.96087210000
11/14/08 | 604563 | 0 | EASTERN AVE | NE | 2/9/12 | 52365DC | 5L682 | (Light out) | STREET - Caller is reporting that there are streetlights that are leaning at this intersction. Please send some one out there to repair the streetlight and also so at Varnum street and Eastern Ave N.E. | High Pressure Sodium | 38.94310507000 | -76.97366566000
11/14/08 | 604354 | 1541 | 7TH ST | NW | 11/14/08 | 25702 | 6A814 | (Light out) | DA 11-14-08 @ 200am S. Daniels repaired pole #25702 | High Pressure Sodium | 38.91080483000 | -77.02182504000
11/13/08 | 603920 | 2010 | 48TH ST | NW | 11/17/08 | 35371DC | 3E028 | (Light out) | DA 11-17-08 @ 220am C. Ashton repaired pole #35371dc DA - this pole has no id tag | Incandescent | 38.91732328000 | -77.09428336000
11/12/08 | 603257 | 618 | I ST | NW | 11/13/08 | 22501 | 6S554 | (Light out) | DA 11-13-08 @ 1215am S. Daniels repaired pole #22501 | High Pressure Sodium | 38.90080778000 | -77.02080368000
11/12/08 | 603256 | 801 | 7TH ST | NW | 11/13/08 | 22453 | 6M655 | (Light out) | DA 11-13-08 duplicate ticket to wo #595932 Hansen #1951210 - ticket was refered to ddot Light is affected by third party construction - not yet activated | High Pressure Sodium | 38.89994386000 | -77.02181748000
11/12/08 | 603232 | 601 | KENNEDY ST | NW | 11/14/08 | 4M067 | 4M067DC | (Light out) | DA 11-14-08 @ 110am R. Warren repaired pole #4M067 | High Pressure Sodium | 38.95648496000 | -77.02110063000
11/10/08 | 602244 | 2715 | PENNSYLVANIA AVE | SE | 11/12/08 | 78586 | 7E066 | (Light out) | DA 11-12-08 @ 323am T. Richards repaired pole #78586 | High Pressure Sodium | 38.87257009000 | -76.96818889000
11/10/08 | 602235 | 900 | U ST | NW | 11/11/08 | 13983 | 1G551 | (Light out) | DA 11-11-08 @1020pm pole #13983 - refered to pepco refer to wo #595600 - No Hansen # | High Pressure Sodium | 38.91713116000 | -77.02591861000
11/10/08 | 602401 | 900 | UPSHUR ST | NW | 11/19/08 | 4J744 | 4G330 | (Light out) | CP 11/17 - H Lancaster (Pepco maps 792-403) DA 11-13-08 @ 1127pm R. Warren pole #4J744 Still a N/C underground SOUTHEAST CORNER - streetlight out on metal pole @ southeast corner of location, would like to have it repaired. | High Pressure Sodium | 38.94182164000 | -77.02494834000
11/10/08 | 602218 | 0 | ALLISON ST | NW | 11/13/08 | 4K101DC | 4U136DC | (Light off/on) | DA 11-13-08 @ 1220am R. Warren pole #4k101dc light found okay | High Pressure Sodium | 38.94511734000 | -77.02981962000
11/9/08 | 602178 | 1411 | H ST | NE | 11/11/08 | 62355 | 6M711 | (Light out) | DA 11-11-08 @ 1009pm T. Richards repaired pole #62355 121 10TH STREET NE, WASHINGTON, DC EAST SIDE, CENTER OF BLOCK - | High Pressure Sodium | 38.90010969000 | -76.98500705000
11/7/08 | 601550 | 0 | INTERSTATE 295 | SE | 11/7/08 | 67937 | 6L991 | (Light out) | DA 10-7-08 B. Black installed 400 hps lamp pole #67937 | High Pressure Sodium | 38.87762738000 | -76.99170117000
11/7/08 | 601663 | 2 | MASSACHUSETTS AVE | NE | 11/12/08 | 60929 | 6U603 | (Light out) | DA 11-12-08 @ 220am T. Richards repaired pole #60929 DA 11-10-08 T. Richards all lights in area found on can't locate this pole # @ this location 701 FIRST ST NE - pole number 68311's light fixture is gone. | High Pressure Sodium | 38.89781016000 | -77.00762917000
11/6/08 | 601690 | 1100 | CONNECTICUT AVE | NW | 11/10/08 | 24537 | 2U557 | (Light out) | DA 11-10-08 @ 300am S. Daniels repaired pole #24537 - metal pole street light out #24537 | High Pressure Sodium | 38.90429111000 | -77.04049306000
11/6/08 | 601034 | 3901 | PENNSYLVANIA AVE | SE | 11/10/08 | 78526DC | 7E134DC | (Light out) | DA 11-09-08 @ 1158pm T. Richards repaired pole #78526dc | High Pressure Sodium | 38.86581514000 | -76.95205676000
11/6/08 | 601033 | 3233 | PENNSYLVANIA AVE | SE | 11/10/08 | 78547DC | 7E110 | (Light out) | DA 11-09-08 @ 1148pm T. Richards repaired loose connection pole #78547dc | High Pressure Sodium | 38.86864144000 | -76.95900959000
11/6/08 | 601028 | 740 | 6TH ST | NW | 11/10/08 | 22513 | 6S425 | (Light out) | DA 11-10-08 @ 350am S. Daniels repaired pole #22513 | High Pressure Sodium | 38.89950950000 | -77.02001122000
11/6/08 | 600899 | 1717 | 17TH ST | NW | 11/7/08 | 26702 | 2M033 | (Light out) | CP 11/7 - H lancaster (Pepco maps 789-393 & 788-393) DA 11-06-08 @ 335am S. Daniels pole #26702 open neturial - refer to fault crew | High Pressure Sodium | 38.91327520000 | -77.03840035000
11/5/08 | 600403 | 1228 | 11TH ST | NW | 11/18/08 | 25279 | 2M255 | (Light out) | CP 11/18 - L Roberto DA 11-10-08 S. Daniels pole #25279 has pole and wire - no arm and fixture FRONT - THIS IS A WOODEN POLE LIGHT HAS BEEN OUT FOR THREE WEEKS | High Pressure Sodium | 38.90650398000 | -77.02715307000
11/5/08 | 600284 | 809 | INTERSTATE 295 | NE | 11/9/08 | 79474 | 7A138 | (Light out) | DA 11-09-08 @ 1009pm T. Richards repaired pole #79474 (3 Krimps, black tape) DA 11-07-08 @ 138am T. Richards pole #79474 needs 400 hps Starter | High Pressure Sodium | 38.88176234000 | -76.96414383000
11/5/08 | 600266 | 5336 | CALL PL | SE | 11/6/08 | 75598 | 75598DC | (Light out) | DA 11-05-08 @ 1030pm K. Simmons repaired pole #75598 | High Pressure Sodium | 38.88354836000 | -76.92520818000
11/4/08 | 599770 | 0 | 13TH ST | NW | 11/6/08 | 4K427 | 4U141 | (Light out) | DA 11-06-08 @ 255am R. Warren repaired pole #4k427- street light on metal pole #4k427 | High Pressure Sodium | 38.94426693000 | -77.02962255000
11/4/08 | 599768 | 0 | 7TH ST | NW | 11/27/11 | 22430 | 2A186 | (Light out) | New construction by third party - not yet turned over to Severn - DA 11-06-08 - S. Daniels pole #22430 N/C underground -@ base - no nuterial or hot to base- teardrop fixture SW CORNER - street light on metal pole is out pole #22430 | High Pressure Sodium | 38.89710115000 | -77.02201609000
11/4/08 | 599667 | 4479 | F ST | SE | 11/6/08 | 75749 | 75749DC | (Light out) | DA 11-04-08 @ 1105pm T. Richards pole #s 75749 and 75750 - N/C overhead - No Feed Wire | High Pressure Sodium | 38.88184868000 | -76.93731162000
11/4/08 | 599602 | 900 | U ST | NW | 11/4/08 | 13983 | 1G551 | (Light out) | DA 10-04-08 duplicate ticket to wo #595600 - refer to Pepco | High Pressure Sodium | 38.91713116000 | -77.02591861000
11/4/08 | 599252 | 601 | 4TH ST | NW | 11/4/08 | 60444 | 68627 | (Light out) | DA 11-04-08 @ 1233am T. Richards repaired pole #60444 | High Pressure Sodium | 38.89820486000 | -77.01611532000
11/1/08 | 598895 | 1330 | U ST | NW | 11/2/08 | 13281 | 1G520 | (Light out) | DA 11-02-08 @ 1005pm S. Daniels repaired pole #13281 | High Pressure Sodium | 38.91692624000 | -77.03085442000
10/31/08 | 598442 | 3321 | IDAHO AVE | NW | 11/4/08 | 38889DC | 3U414 | (Light out) | DA 11-04-08 @ 1220am C. Ashton repaired pole #38889dc | High Pressure Sodium | 38.93442754000 | -77.07435346000
10/31/08 | 598342 | 0 | 12TH ST | NW | 10/31/08 | 13984 | 1G536 | (Light out) | DA 10-31-08 @ 400am C. Ashton repaired pole #13984 | High Pressure Sodium | 38.91686452000 | -77.02815086000
10/30/08 | 597867 | 1012 | 14TH ST | NW | 10/31/08 | 27353 | 2M415 | (Light out) | DA 10-30-08 @ 1105pm S. Daniels repaired pole #27353 | High Pressure Sodium | 38.90334542000 | -77.03208521000
10/29/08 | 596983 | 2010 | 48TH ST | NW | 10/29/08 | 35371DC | 3E028 | (Light out) | DA 10-28-08 @ 1145pm c. ashton repaired pole #35371dc | Incandescent | 38.91732328000 | -77.09428336000
10/28/08 | 596529 | 0 | M ST | NW | 10/30/08 | 23729 | 2U531 | (Light out) | DA 10-30-08 duplicate ticket to wo #588218 M STREET NW AND CONNECTICUT AVENUE NW, WASHINGTON, DC TWO STREET LIGHTS AT THE CORNER OF M STREET AND CONNECTICUT AVENUE, NW 1700 BLOCK OF M STREET AND ONE STREET LIGHT AT THE CORNER OF M STREET AND CONNECTICUT | High Pressure Sodium | 38.90574984000 | -77.04138732000
10/27/08 | 595872 | 1312 | U ST | NW | 10/31/08 | 13282 | 1G524 | (Light out) | CP 10/30 J Lancaster (VW) 10-28-08 T Osvatics No current - pole has missig nuetral needs nuetral from M/H M/H is in street need **MOT** we roded 3ft and got stuck in mud | High Pressure Sodium | 38.91692555000 | -77.03016133000
10/27/08 | 595871 | 1330 | U ST | NW | 10/28/08 | 13281 | 1G520 | (Light out) | (VW) 10-28-08 T Osvatics inst TLP 1-250w hps lamp | High Pressure Sodium | 38.91692624000 | -77.03085442000
10/27/08 | 595950 | 2038 | 18TH ST | NW | 10/29/08 | 11414 | 1G510 | (Light out) | DA 10-29-08 @ 345am C. Ashton repaired pole #11414 18TH AND CALIFORNIA - | High Pressure Sodium | 38.91777981000 | -77.04149864000
10/27/08 | 595932 | 801 | 7TH ST | NW |  | 22453 | 6M655 | (Light out) | Light is affected by third party construction - not yet activated DA 10-28-08 @ 1000pm S. Daniels pole #22453 N/C underground - no wire to pole THE STREETLIGHT IS AT THE NORTHEAST CORNER OF 7TH AND H STREETS, N.W. - | High Pressure Sodium | 38.89994386000 | -77.02181748000
10/27/08 | 595641 | 1232 | H ST | NE | 10/28/08 | 62332 | 6S161 | (Light out) | DA 10-28-08 @ 1258am T. Richards repaired pole #62332 | High Pressure Sodium | 38.90029650000 | -76.98911501000
10/26/08 | 595601 | 3200 | O ST | NW | 10/27/08 | 21110 | 2G173 | (Light off/on) | DA 10-27-08 @ 1210am S. Daniels repaired pole #21110 | High Pressure Sodium | 38.90787881000 | -77.06482911000
10/26/08 | 595600 | 900 | U ST | NW | 6/3/09 | 13983 | 1G551 | (Light out) | DA 10-26-08 @ 1110pm S. Daniels pole #13983 - 120 volts - open neturial - refer to fault crew | High Pressure Sodium | 38.91713116000 | -77.02591861000
10/23/08 | 594370 | 430 | 1ST ST | SE | 10/24/08 | 65630 | 6A394 | (Light out) | DA 10-24-08 @ 207am T. Richards repaird pole #65630 | High Pressure Sodium | 38.88412965000 | -77.00580783000
10/23/08 | 594245 | 1224 | H ST | NE | 10/23/08 | 62348 | 6S114 | (Light out) | DA 10-23-08 @ 205am T. Richards repaired pole #62348 - needs T base | High Pressure Sodium | 38.90011721000 | -76.98943529000
10/23/08 | 594237 | 1900 | 37TH ST | NW | 10/23/08 | 36891 | 30482 | (Light out) | DA 10-23-08 @ 100am C. Ashton repaired pole #26891 | High Pressure Sodium | 38.91672906000 | -77.07292654000
10/23/08 | 594236 | 2730 | WISCONSIN AVE | NW | 10/28/08 | 30177 | 3G020 | (Light out) | CP 10/27 - H Lancaster DA 10-22-08 @ 1140pm C. AShton pole #30177 - installed 400 fixture, bulb, TLP and ran 70ft of wire - light still not on - bad neturial underground refer to fault crew | High Pressure Sodium | 38.92608314000 | -77.07307216000
10/22/08 | 593777 | 900 | U ST | NW | 10/22/08 | 13983 | 1G551 | (Light out) | DA 10-22-08 @ 1050pm C. Ashton repaired pole #13983 | High Pressure Sodium | 38.91713116000 | -77.02591861000
10/22/08 | 593602 | 900 | U ST | NW | 10/22/08 | 13983 | 1G551 | (Light out) | DA 10-22-08 @ 200am S. Daniels repaired pole #13983 | High Pressure Sodium | 38.91713116000 | -77.02591861000
10/22/08 | 593102 | 2010 | 48TH ST | NW | 10/22/08 | 35370DC | 3E030 | (Light out) | DA 10-22-08 @ 1200am C. Ashton repaired pole #35370dc | Incandescent | 38.91704622000 | -77.09453331000
10/21/08 | 593818 | 226 | RHODE ISLAND AVE | NW | 10/23/08 | 59994 | 5A186 | (Light out) | DA 10-23-08 @ 1057pm K. Simons repaired pole #59994 FRONT/220 AND 226 - street light is out metal pole maybe 2 lights | Incandescent | 38.91452540000 | -77.01525438000
10/21/08 | 593096 | 1541 | 7TH ST | NW | 10/22/08 | 25702 | 6A814 | (Light out) | DA 10-21-08 @ 1120pm S. Daniels repaired pole #25702 - reconnected hot and neturial @ base | High Pressure Sodium | 38.91080483000 | -77.02182504000
10/21/08 | 593129 | 900 | UPSHUR ST | NW | 10/29/08 | 4J744 | 4G330 | (Light out) | CP 10/29 - H Lancaster DA 10-27-08 @ 255am R. Warren pole #4J744 N/C underground FRONT/ SE CORNER - street light is out it's a metal pole | High Pressure Sodium | 38.94182164000 | -77.02494834000
10/21/08 | 593111 | 1111 | 11TH ST | NW | 10/24/08 | 25265 | 2M225 | (Light out) | DA 10-24-08 @ 200am S. Daniels repaird pole #25265 - Streetlight needs to be repaired | High Pressure Sodium | 38.90512472000 | -77.02692572000
10/21/08 | 593121 | 3223 | SHERMAN AVE | NW | 10/23/08 | 12872 | 1L273 | (Light out) | DA 10-23-08 @ 100am S. Daniels pole #12872 previously repaired refer to wo #590136 IN FRONT OF 3221 SHERMAN AVE, NW - streetlgiht on metal pole in front of 3221 Sherman ave, NW is out. please repair asap. | High Pressure Sodium | 38.93042323000 | -77.02636750000
10/21/08 | 592387 | 737 | 7TH ST | NW | 10/21/08 | 22449 | 6M645 | (Light out) | DA 10-21-08 @ 1200am S. Daniels repaired pole #22449 | High Pressure Sodium | 38.89917822000 | -77.02181820000
10/20/08 | 592423 | 1541 | 7TH ST | NW | 10/22/08 | 25702 | 6A814 | (Light out) | DA 10-21-08 @ 1133pm S. Daniels repaired pole #25702 - reconnected hot and neturial @ base FRONT - caller req to have street light repaired | High Pressure Sodium | 38.91080483000 | -77.02182504000
10/20/08 | 592223 | 2730 | WISCONSIN AVE | NW | 10/20/08 | 30177 | 3G020 | (Light out) | DA 10-20-08 @ 1200am C. Ashton repaired pole #30177 and repaired pole tag | High Pressure Sodium | 38.92608314000 | -77.07307216000
10/16/08 | 591700 | 0 | M ST | NW | 10/20/08 | 23729 | 2U531 | (Light out) | DA 10-20-08 duplicate ticket to wo #588218 was refered to DDot CORNER OF M STREET AND CONNECTICUT AVENUE - | High Pressure Sodium | 38.90574984000 | -77.04138732000
10/15/08 | 590147 | 1644 | PARK RD | NW | 11/3/08 | 10112 | 1G349 | (Light out) | DA 10-17-08 @ 250am R. Warren repaired pole #10112 - Needs tree trimmed | High Pressure Sodium | 38.93203016000 | -77.03755558000
10/15/08 | 590136 | 3223 | SHERMAN AVE | NW | 10/16/08 | 12872 | 1L273 | (Light out) | DA 10-15-08 @ 1155pm S. Daniels reconnected hot and neturial @ base pole #12872 | High Pressure Sodium | 38.93042323000 | -77.02636750000
10/14/08 | 589169 | 0 | 7TH ST | NW |  | 22430 | 2A186 | (Light out) | New construction by third party - not yet turned over to Severn DA 10-14-08 @ 405am S. Daniels pole #22430 N/C underground -@ base - no nuterial or hot to base- teardrop fixture | High Pressure Sodium | 38.89710115000 | -77.02201609000
10/14/08 | 589167 | 400 | VIRGINIA AVE | SW | 10/14/08 | 21626 | 6L715 | (Light out) | DA 10-14-08 @ 330am S. Daniels repaired pole #21616 | High Pressure Sodium | 38.88471591000 | -77.01896800000
10/13/08 | 589091 | 5326 | CONNECTICUT AVE | NW | 10/17/08 | 30542 | 3E017 | (Light out) | DA 10-15-08 @ 450am C. AShton pole #30542 N/C underground STREET LIGHT IS OUT ON CONNECTICUT AVE BETWEEN KANAWHA STREET AND MILITARY ROAD ON THE NORTH BOUND SIDE. - MILITARY | High Pressure Sodium | 38.96076273000 | -77.07303810000
10/13/08 | 588994 | 5326 | CONNECTICUT AVE | NW | 10/15/08 | 30542 | 3E017 | (Light out) | DA 10-15-08 @ 450am C. AShton pole #30542 N/C underground refer to wo #589091 | High Pressure Sodium | 38.96076273000 | -77.07303810000
10/12/08 | 588929 | 1425 | H ST | NE | 10/16/08 | 62325 | 6M714 | (Light out) | DA 10-16-08 @ 1225am T. Richards repaired pole #62325 | High Pressure Sodium | 38.90029705000 | -76.98474424000
10/12/08 | 588921 | 0 | H ST | NE | 10/17/08 | 62327 | 6S140 | (Light out) | CP 10/17 - D Smith DA 10-16-08 @ 1226am T. Richards pole #62327 ran 70 ft wire and made 2 splices pole had current upon arrival but after running wire pole had no Current refer to fault crew | High Pressure Sodium | 38.90029795000 | -76.98565875000
10/10/08 | 588338 | 3321 | IDAHO AVE | NW | 10/13/08 | 38888DC | 3U416 | (Light out) | DA 10-12-08 C.Ashton pole #38888dc refered to ddot defective 400 mv fixture refer to wo #573095 | Mercury Vapor | 38.93408385000 | -77.07471732000
10/10/08 | 588335 | 2 | WESTMORELAND CIR | NW | 10/13/08 | 34380 | 3M038 | (Light out) | DA 10-13-08 C. Ashton pole #34380 still Mercury Vapor fixutre - | Mercury Vapor | 38.94941039000 | -77.10097492000
10/10/08 | 588363 | 0 | WISCONSIN AVE | NW | 10/14/08 | 30137 | 3G019 | (Light out) | DA 10-13-08 @ 1140pm C. Ashton repaired pole #30137 adjusted photocell and secured pole tag NORTHWEST CORNER IN FRONT OF 2800 WISCONSIN AVE, NW - streetlight (on metal pole) is on some night and some night, it's off. it needs to be come on every nigh | High Pressure Sodium | 38.92630371000 | -77.07330137000
10/10/08 | 588225 | 0 | M ST | NW | 10/10/08 | 23718 | 2G720 | (Light out) | DA 10-10-08 @ 235am S. Daniels repaired pole #23718 | High Pressure Sodium | 38.90536068000 | -77.04765891000
10/10/08 | 588221 | 0 | 18TH ST | NW | 2/6/12 | 24534 | 2U529 | (Light out) | DA 10-10-08 @ 220am S .Daniels pole #24534 Teardrop fixture refer to Ddot need wire ran fron top of pole to T base | High Pressure Sodium | 38.90591907000 | -77.04143681000
10/10/08 | 588218 | 0 | M ST | NW | 2/6/12 | 23729 | 2U531 | (No current) | DA 10-10-08 @ 140am S .Daniels pole #23729 Teardrop fixture refer to Ddot need wire ran fron top of pole to T base | High Pressure Sodium | 38.90574984000 | -77.04138732000
10/9/08 | 587701 | 0 | CAMDEN ST | SE | 10/15/08 | 74755DC | 7A069DC | (Light out) | DA 10-15-08 @ 629am R. Warren repaired pole #74755dc CAMDEN STREET, SE - BRANCH | High Pressure Sodium | 38.85947895000 | -76.95992491000
10/9/08 | 587627 | 900 | NEW JERSEY AVE | SE | 10/13/08 | 67472 | 6A060 | (Light out) | DA 10-13-08 @ 307am T. Richards repaired pole #67472 | High Pressure Sodium | 38.87881747000 | -77.00509329000
10/9/08 | 587626 | 400 | L ST | SE |  | 67702 | 6B462 | (Light out) | Construction company on site has area torn up due to construction DA 10-15-08 @ 1040pm T. Richards pole #67702 N/C underground DA 10-14-08 @ 1148pm - Construction info Capitol Cor. / Phone #202-484-0360 DA 10-13-08 Tim, I need any info that you can get | High Pressure Sodium | 38.87758613000 | -77.00028077000
10/9/08 | 587619 | 500 | 6TH ST | NW | 10/10/08 | 60502 | 6S592 | (Light out) | DA 10-10-08 @ 400am T. Richards repaired pole #60502 | High Pressure Sodium | 38.89545797000 | -77.02001074000
10/9/08 | 587613 | 200 | K ST | NE | 10/10/08 | 61351 | 6B087 | (Light out) | DA 10-10-08 @ 335am T. Richards repaired pole #61351 | High Pressure Sodium | 38.90302176000 | -77.00210340000
10/9/08 | 587598 | 4829 | NORTH CAPITOL ST | NW | 10/10/08 | 4R750 | 4A791 | (Light out) | DA 10-09-08 @ 1155pm R. Warren repaired pole #4R750 | High Pressure Sodium | 38.94981176000 | -77.00891482000
10/9/08 | 587590 | 0 | ALLISON ST | NW | 10/10/08 | 4K101DC | 4U136DC | (Light dim) | DA 10-10-08 @ 417am R. Warren repaired pole #4k101dc | High Pressure Sodium | 38.94511734000 | -77.02981962000
10/9/08 | 587588 | 4235 | 9TH ST | NW | 10/13/08 | 4K017 | 4G319 | (Light out) | DA 10-13-08 @ 1247am R. Warren repaired pole #4K017 | High Pressure Sodium | 38.94272297000 | -77.02520204000
10/9/08 | 587587 | 4119 | 9TH ST | NW | 10/13/08 | 4J793 | 4G331 | (Light out) | DA 10-13-08 @ 100am R. Warren repaired pole #4J793 | High Pressure Sodium | 38.94117354000 | -77.02497316000
10/9/08 | 587533 | 236 | RHODE ISLAND AVE | NW | 10/10/08 | 59993 | 5A185 | (Light out) | 10-10-08 (VW) L Roberto/Marc found ok DA 10-09-08 @ 110am G. Hicks repaired pole #59993 Needs A globe | High Pressure Sodium | 38.91439745000 | -77.01561600000
10/8/08 | 586923 | 1527 | 18TH ST | NW | 10/8/08 | 26758 | 2M157 | (Light out) | DA 10-08-08 @ 320am S. Daniels repaired pole #26758 | High Pressure Sodium | 38.91061514000 | -77.04160716000
10/8/08 | 586911 | 1011 | NEW HAMPSHIRE AVE | NW | 10/8/08 | 23861 | 2G709 | (Light off/on) | DA 10-08-08 @ 155am S. Daniels repaire pole #23861 has new fixture and powerdoor installed TL photocell | High Pressure Sodium | 38.90365073000 | -77.04920348000
10/7/08 | 586307 | 0 | ANACOSTIA FWY | SE | 10/7/08 | 79491 | 7A160 | (Light out) | DA 10-07-08 B. Black repaired pole #79491 installed 250 powerdoor | High Pressure Sodium | 38.88928656000 | -76.95990942000
10/7/08 | 586280 | 0 | 1ST ST | NE | 10/8/08 | 59971 | 5M126 | (Light out) | DA 10-08-08 @ 1238am T. Richards repaired pole #59971 | High Pressure Sodium | 38.90875013000 | -77.00576789000
10/7/08 | 586273 | 1400 | BRENTWOOD PKY | NE | 10/7/08 | 52559 | 5M037 | (Light out) | DA 10-07-08 @ 1120pm G. Hicks repaired pole #52559 | High Pressure Sodium | 38.91138782000 | -76.99222307000
10/7/08 | 586240 | 0 | 8TH ST | NE | 10/8/08 | 56194DC | 56194 | (Light out) | DA 10-08-08 @ 1256am R. Warren repaired pole #56194dc | High Pressure Sodium | 38.93214286000 | -76.99503981000
10/7/08 | 586334 | 0 | H ST | NE | 10/9/08 | 62327 | 6S140 | (Light out) | DA 10-09-08 @ 1100pm T. Richards repaired pole #62327 CORNER.... - Streetlight out,cable cut... wasn't sure what type of pole... please repair. thanks | High Pressure Sodium | 38.90029795000 | -76.98565875000
10/6/08 | 585521 | 2425 | 14TH ST | NW | 2/6/12 | 12075 | 1G565 | (No current) | Pepco has power shut off to MH due to construction - Bateman | High Pressure Sodium | 38.92101358000 | -77.03175759000
10/5/08 | 585459 | 1010 | 11TH ST | NW |  | 29203 | 2M214 | (No current) | Combo pole/common duct - JBateman | High Pressure Sodium | 38.90369501000 | -77.02685773000
10/5/08 | 585457 | 1101 | L ST | NW | 10/6/08 | 25942 | 2M218 | (Light off/on) | DA 10-06-08 @ 1100pm S. Daniels repaired pole #25942 | High Pressure Sodium | 38.90408908000 | -77.02717553000
10/5/08 | 585453 | 1011 | NEW HAMPSHIRE AVE | NW | 10/6/08 | 23861 | 2G709 | (Light out) | DA 10-06-08 duplicate ticket to wo #585452 no hansen # | High Pressure Sodium | 38.90365073000 | -77.04920348000
10/5/08 | 585452 | 1011 | NEW HAMPSHIRE AVE | NW | 10/7/08 | 23861 | 2G709 | (Light out) | DA 10-07-08 @ 1220am S. Daniels repaired pole #23861 ( inventory updateed from cobra to cut offf fixture) | High Pressure Sodium | 38.90365073000 | -77.04920348000
10/5/08 | 585405 | 3460 | 14TH ST | NW | 10/6/08 | 13803 | 1G084 | (Light out) | DA 10-06-08 @ 245am S. Daniels repaired pole #13803 | High Pressure Sodium | 38.93314624000 | -77.03283352000
10/5/08 | 585350 | 5314 | B ST | SE | 10/6/08 | 75565 | 75565DC | (Light out) | DA 10-06-08 @ 115am T. Richards repaired pole #75565 | High Pressure Sodium | 38.88626314000 | -76.92486984000
10/3/08 | 584653 | 3430 | PENNSYLVANIA AVE | SE | 10/6/08 | 78534DC | 7E125DC | (Light out) | DA 10-06-08 @ 324am T. Richards repaired pole #78534dc | High Pressure Sodium | 38.86695624000 | -76.95485118000
10/3/08 | 584596 | 1154 | SUMNER RD | SE | 10/7/08 | 81566DC | 8A352 | (Light out) | DA 10-06-08 @ 1130pm R. Warren pole #81566dc - did burn test light found okay DA 10-04-08 @ 237am S. DAniels repaired pole #81566dc | High Pressure Sodium | 38.86072349000 | -76.99691194000
10/3/08 | 584519 | 0 | INTERSTATE 295 | SE | 10/3/08 | 86494 | 8A073 | (Light out) | Made secondary taps - Greenfield DA 10-0-08 @ 213am T. Richards pole #86494 per BCM needs plastic u guard and bolts refer to overhead | High Pressure Sodium | 38.84482511000 | -77.00710099000
10/3/08 | 584507 | 4636 | EASY PL | SE | 10/3/08 | 75824 | 75824DC | (Light out) | DA 10-03-08 @ 203am R. Warren repaired pole #75824 | High Pressure Sodium | 38.87603752000 | -76.93237688000
10/2/08 | 583889 | 1140 | CONNECTICUT AVE | NW | 10/3/08 | 24535 | 2U549 | (Light off/on) | DA 10-03-08 @ 255am S. Daniels repaired pole #24535 | High Pressure Sodium | 38.90503939000 | -77.04092719000
10/2/08 | 583886 | 1011 | CONNECTICUT AVE | NW | 10/3/08 | 27213 | 2G833 | (Light out) | DA 10-03-08 @ 310am S. Daniels repaired pole #27213 | High Pressure Sodium | 38.90292468000 | -77.03936525000
10/2/08 | 583884 | 1011 | NEW HAMPSHIRE AVE | NW | 10/6/08 | 23861 | 2G709 | (Light out) | DA 10-06-08 duplicate ticket to wo #585452 no hansen # | High Pressure Sodium | 38.90365073000 | -77.04920348000
10/2/08 | 583834 | 0 | NEW YORK AVE | NE | 10/2/08 | 61252 | 5M104 | (Light off/on) | 10-02-08 (V Ward) L Roberto/Marc Inst. 250w hps lamp, TLP | High Pressure Sodium | 38.90823571000 | -77.00619583000
10/2/08 | 583828 | 4514 | 13TH ST | NW | 10/3/08 | 4K422 | 4U131 | (Light off/on) | DA 10-02-08 @ 1153pm G. Hicks repaired pole #4K422 | High Pressure Sodium | 38.94571765000 | -77.02978404000
10/1/08 | 583232 | 1154 | SUMNER RD | SE | 10/3/08 | 81566DC | 8A352 | (Light out) | DA 10-03-08 @ 240am T. Richards repaired pole #81566dc | High Pressure Sodium | 38.86072349000 | -76.99691194000
10/1/08 | 583215 | 4620 | EASY PL | SE | 10/3/08 | 75825 | 75825DC | (Light out) |  | Incandescent | 38.87603739000 | -76.93290309000
9/30/08 | 582489 | 3112 | SHERMAN AVE | NW | 10/1/08 | 12857 | 1L258 | (Light off/on) | DA 9-30-08 @ 1130pm C. Ashton burned test on photocell pole #12857 found to be okay | High Pressure Sodium | 38.92921064000 | -77.02639391000
9/30/08 | 582481 | 44 | H ST | NW | 10/7/08 | 60396 | 68449 | (Light out) | DA 10-04-08 @ 430am S. Daniels pole #60396 N/C underground | High Pressure Sodium | 38.90035358000 | -77.01505913000
9/30/08 | 582470 | 4205 | KANSAS AVE | NW | 10/2/08 | 4K571 | 4G317 | (Light out) | DA 10-02-08 @ 1230am R. Warren repaired pole 4k571 | High Pressure Sodium | 38.94236617000 | -77.02546807000
9/30/08 | 582457 | 44 | H ST | NW | 10/2/08 | 60398 | 6A199 | (No current) | R Rapolla, 09-30-08, No Current tied to work order # 574341,SLPT#60399 | High Pressure Sodium | 38.90030973000 | -77.01534450000
9/29/08 | 581757 | 0 | 1ST ST | NE | 10/3/08 | 61239 | 6A264 | (Light out) | DA 10-03-08 @ 500am T. Richards repaired pole #61239 IT IS THE STREET LIGHT LOCATED ON THE SE CORNER OF THE INTERSECTION OF M ST NE AND FIRST ST NE. THANK YOU FOR YOUR ASSISTANCE ON THIS MATTER. AARON MCKEIVER, NOMA BID AMBASSADOR SUPERVISOR 202-423-9283 | High Pressure Sodium | 38.90515476000 | -77.00581203000
9/28/08 | 581796 | 1701 | 17TH ST | NW | 10/3/08 | 26736 | 2M062 | (Light out) | DA 10-03-08 @ 240am S. Daniels repaired pole #26736 NW CORNER OF INTERSECTION - | High Pressure Sodium | 38.91179662000 | -77.03856951000
9/25/08 | 580611 | 1717 | 17TH ST | NW | 9/30/08 | 26702 | 2M033 | (Light out) | DA 9-30-08 Duplicate ticket to wo #579776 no Hansen # FRONT - Caller states light needs repairs. | High Pressure Sodium | 38.91327520000 | -77.03840035000
9/25/08 | 580569 | 625 | INDIANA AVE | NW | 9/30/08 | 60661 | 6S574 | (Light out) | DA 9-30-08 @ 1215am T. Richards repaired pole #60661 | High Pressure Sodium | 38.89417281000 | -77.02112863000
9/25/08 | 580553 | 2425 | 14TH ST | NW | 9/29/08 | 12075 | 1G565 | (Light out) | DA 9-29-08 @ 1250am C. AShton pole #12075 light found okay | High Pressure Sodium | 38.92101358000 | -77.03175759000
9/25/08 | 580552 | 1372 | BELMONT ST | NW |  | 12076 | 1G566 | (Light out) | 10-02-08 (V Ward) H Lancaster CTI say's they had PEPCO to cut feed for about 4 lights due to construction DA 10-01-08 @ 140am C. Ashton pole #12076 N/C underground pole is construction area - Clark Consrtuction no phone # DA 9-29-08 @ 100am C. AShton | High Pressure Sodium | 38.92104903000 | -77.03154113000
9/25/08 | 580548 | 3223 | SHERMAN AVE | NW | 9/29/08 | 12872 | 1L273 | (Light out) | DA 9-29-08 @ 340am C. AShton repaired pole #12872 | High Pressure Sodium | 38.93042323000 | -77.02636750000
9/25/08 | 580515 | 1421 | 34TH ST | NW | 9/29/08 | 21073 | 2G189 | (Light out) | DA 9-29-08 @ 1245am K. Hollins repaired pole #21073 | High Pressure Sodium | 38.90848178000 | -77.06790108000
9/25/08 | 580513 | 3327 | P ST | NW | 9/29/08 | 21011 | 2G136 | (Light out) | DA 9-29-08 @ 1235am K. Hollins repaired pole #21011 | High Pressure Sodium | 38.90882393000 | -77.06707220000
9/25/08 | 580484 | 1224 | H ST | NE | 9/25/08 | 62348 | 6S114 | (Light out) | DA 9-25-08 @ 600am C. Ashton repaired pole #62348 | High Pressure Sodium | 38.90011721000 | -76.98943529000
9/24/08 | 579892 | 200 | L ST | SE | 9/25/08 | 67695 | 6A414 | (Light out) | DA 9-25-08 @ 440am C. Ashton repaired pole #67695 | Incandescent | 38.87766628000 | -77.00287950000
9/24/08 | 579891 | 388 | H ST | NE | 9/24/08 | 61522 | 6S224 | (Light out) | DA 9-24-08 @ 1055pm C. AShton repaired pole #61522 | High Pressure Sodium | 38.90030233000 | -77.00072209000
9/24/08 | 579825 | 1451 | MARYLAND AVE | NE | 9/25/08 | 62358 | 6M720 | (Light out) | DA 9-25-08 @ 200am C. AShton repaired pole #62358 | High Pressure Sodium | 38.90007909000 | -76.98391252000
9/24/08 | 579776 | 1717 | 17TH ST | NW | 10/1/08 | 26702 | 2M033 | (Light out) | 10/1 - JWB - 1 splice 9-30-08 (V Ward) L Roberto Installed T-Base door DA 9-30-08 @ 100am K. Hollins pole #26702 N/C @ base - 79 volts @ fixture underground feed Needs T base door | High Pressure Sodium | 38.91327520000 | -77.03840035000
9/23/08 | 579120 | 508 | MELLON ST | SE | 9/25/08 | 86496 | 8A358 | (Light out) | DA 9-24-08 @ 1150pm K. Hollins repaired pole #86496 BCM 9-24-08 REPLACE FIXTURE DA 9-24-08 @ 250am K. Hollins repaired pole #86496 | High Pressure Sodium | 38.86233552000 | -77.00031519000
9/23/08 | 579212 | 3641 | BANGOR ST | SE | 9/25/08 | 74815DC | 7A087DC | (Light out) | DA 9-25-08 @ 152am T. Richards repaired pole #74815dc REAR - WOODEN POLE 2 DAYS AGO | High Pressure Sodium | 38.86030331000 | -76.95456197000
9/23/08 | 579078 | 200 | 23RD ST | NW | 9/23/08 | 28319 | 2M276 | (Light off/on) | DA 9-23-08 @ 405am K. Hollins repaired pole #28319 | High Pressure Sodium | 38.89259094000 | -77.05025420000
9/23/08 | 579077 | 0 | 23RD ST | NW | 9/23/08 | 28320 | 2M268 | (Light off/on) | DA 9-23-08 @ 344am K. Hollins repaired pole #28320 - repositioned photocell | High Pressure Sodium | 38.89242239000 | -77.05003950000
9/23/08 | 579069 | 3709 | NEWARK ST | NW | 9/23/08 | 38994DC | 3U394 | (Light out) | DA 9-23-08 @ 220am C. Ashton repaired pole #38994dc | High Pressure Sodium | 38.93488284000 | -77.07368761000
9/23/08 | 578955 | 1332 | 35TH ST | NW | 9/23/08 | 20903 | 2G192 | (Light out) | DA 9-23-08 @ 100am K. Hollins repaired pole #20903 | High Pressure Sodium | 38.90762144000 | -77.06910533000
9/22/08 | 578443 | 3700 | NEWARK ST | NW | 9/23/08 | 38993DC | 3U395 | (Light out) | DA 9-23-08 @ 1230am C. Ashton repaired pole #38993dc | High Pressure Sodium | 38.93504796000 | -77.07376331000
9/22/08 | 578442 | 3321 | IDAHO AVE | NW | 9/23/08 | 38888DC | 3U416 | (Light out) | DA 9-23-08 Duplicate ticket to wo #573095 no Hansen # | Mercury Vapor | 38.93408385000 | -77.07471732000
9/22/08 | 578341 | 100 | FLORIDA AVE | NE | 9/22/08 | 56989 | 5M139 | (Light out) | DA 9-22-08 @ 435am C. Ashton repaired pole #56989 and secured t base door | High Pressure Sodium | 38.90947523000 | -77.00574268000
9/21/08 | 578303 | 2002 | 14TH ST | SE | 9/21/08 | 80945 | 8M027 | (Light out) | DA 9-21-08 @ 1121pm G. Hicks repaired pole #80945 | High Pressure Sodium | 38.86594660000 | -76.98526078000
9/21/08 | 578315 | 200 | K ST | NE | 9/23/08 | 61351 | 6B087 | (Light out) | DA 9-22-08 @ 1134pm T. Richards repaired pole #61351 AT THE INTERSECTION - metal pole...lights is on during the day... 61351 | High Pressure Sodium | 38.90302176000 | -77.00210340000
9/19/08 | 577712 | 0 | PIERCE ST | NE | 9/23/08 | 61236 | 6A258 | (Light out) | DA 9-22-08 @ 1142pm T. Richards repaired pole #61236 | High Pressure Sodium | 38.90445580000 | -77.00596738000
9/18/08 | 577154 | 1625 | MASSACHUSETTS AVE | NW | 9/19/08 | 27102 | 2M003 | (Light out) | 9-18-08 (V Ward) Marc/Lorenzo Installed 1 EE 1 screw drilled & tap DA 9-19-08 @ 433am R. Warren repaired pole #27102 Needs (2) ears | High Pressure Sodium | 38.90778988000 | -77.03832443000
9/18/08 | 577149 | 1010 | MASSACHUSETTS AVE | NW | 9/19/08 | 25961 | 2M216 | (Light off/on) | DA 9-19-08 @ 1215am K. Hollins repaired pole #25961 | High Pressure Sodium | 38.90379985000 | -77.02690625000
9/18/08 | 577138 | 0 | K ST | NW | 9/19/08 | 22402 | 6A100 | (Light out) | DA9-19-08 Duplicate ticket to wo #574321 N/C @ base - No Hansen # | High Pressure Sodium | 38.90245268000 | -77.01971021000
9/18/08 | 577134 | 0 | 9TH ST | NW | 9/19/08 | 25437 | 2L558 | (Light out) | DA 9-18-08 @ 1135pm K. Hollins repaired pole #25437 | High Pressure Sodium | 38.90380790000 | -77.02408338000
9/18/08 | 577131 | 1011 | NEW HAMPSHIRE AVE | NW | 9/22/08 | 23861 | 2G709 | (Light out) | DA 9-22-08 @ 335am K Hollins repaired pole #23861 | High Pressure Sodium | 38.90365073000 | -77.04920348000
9/18/08 | 577122 | 3513 | O ST | NW | 9/23/08 | 21096 | 2G159 | (Light out) | DA 9-22-08 @ 245am K. Hollins repaired pole #21096 Needs hole drilled for watchman 9-23-08 L.Roberto---repaired(sconnor) | High Pressure Sodium | 38.90777166000 | -77.06970579000
9/18/08 | 577096 | 401 | I ST | SE | 9/19/08 | 67653 | 6B422 | (Light out) | DA 9-19-08 @ 1210am C. Ashton repaired pole #67653 (updated inventory from cobra to cutoff fixture) | High Pressure Sodium | 38.87922775000 | -77.00050346000
9/18/08 | 577095 | 200 | I ST | SE | 10/14/08 | 67650 | 6A426 | (Light out) | 10-13-08 T Osvatics inst 2#10 butt spls, blk-rubber tape DA 9-18-08 @ 1155pm C. AShton repaired pole #67650 T Base needs repaired 10-13-08 Tom Osvatics---new pole by black rubber tape (2)#10 but splices (s. conor) 16 pole no t base needed | High Pressure Sodium | 38.87923749000 | -77.00159557000
9/18/08 | 577084 | 1100 | 2ND ST | SE | 9/22/08 | 68135 | 6A409 | (Light out) | DA 9-22-108 @ 115am T. Richards repaired pole #68135 - reset TLP | High Pressure Sodium | 38.87682972000 | -77.00287771000
9/18/08 | 577184 | 1116 | U ST | NW | 9/22/08 | 13285 | 1G538 | (Light out) | DA 9-21-08 @ 1130pm C. Ashton pole #13285 light previously repaired on 9-18-08 refer to wo #576354 ON THE CORNER - a metal pole is out | High Pressure Sodium | 38.91692228000 | -77.02795959000
9/18/08 | 577012 | 0 | 13TH ST | NW | 9/18/08 | 4K428 | 4U142 | (Light out) | DA 9-18-08 @ 436am R. Warren repaired pole #4k428 | High Pressure Sodium | 38.94404010000 | -77.02978696000
9/17/08 | 576445 | 0 | ANACOSTIA FWY | SE | 9/18/08 | 79493 | 7A146 | (Light out) | 9-18-08 ( V Ward) T Osvatics Installed 1-70w hps lamp, TLPC ALLEY - all wooden pole lights are out in the alley | High Pressure Sodium | 38.88732787000 | -76.96219078000
9/17/08 | 576377 | 1021 | BRENTWOOD RD | NE | 9/18/08 | 51329DC | 5A240 | (Light out) | DA 9-18-08 @ 402am G. Hicks repaired pole #51329dc | High Pressure Sodium | 38.91864300000 | -76.99199062000
9/17/08 | 576354 | 1116 | U ST | NW | 9/18/08 | 13285 | 1G538 | (Light out) | DA 9-17-08 @ 1135pm C. Ashton repaired pole #13285 (updated from side to front) and secured pole tag | High Pressure Sodium | 38.91692228000 | -77.02795959000
9/17/08 | 576347 | 334 | OAKDALE PL | NW | 9/19/08 | 14190DC | 14802DC | (Light out) | DA 9-18-08 @ 1110pm T. Richards repaired pole #14190dc DA 9-18-08 @ 300am C. Ashton pole #14190dc - Needs Van | High Pressure Sodium | 38.91817964000 | -77.01706140000
9/17/08 | 576336 | 803 | EASTERN AVE | NE | 9/18/08 | 79471 | 7A135 | (Light out) | DA 9-18-08 @ 257am T. Richards repaired pole #79471 | High Pressure Sodium | 38.88055222000 | -76.96517808000
9/17/08 | 576333 | 908 | EASTERN AVE | NE | 9/18/08 | 79483 | 7A152 | (Light out) | DA 9-18-08 @ 320am T. Richards repaired pole #79483 | High Pressure Sodium | 38.88978699000 | -76.95795735000
9/17/08 | 576292 | 388 | H ST | NE | 9/17/08 | 61522 | 6S224 | (Light out) | DA 9-17-08 @ 430am C. Ashton repaired pole #61522 | High Pressure Sodium | 38.90030233000 | -77.00072209000
9/17/08 | 576285 | 44 | H ST | NW | 9/17/08 | 60398 | 6A199 | (Light out) | DA 9-17-08 @ 156am T. Richards repaired pole #60398 | High Pressure Sodium | 38.90030973000 | -77.01534450000
9/17/08 | 575723 | 0 | KENILWORTH AVE | NE | 9/17/08 | 70014 | 7M047 | (Light out) | DA 9-17-08 @ 1259am G, Hicks repaired pole #70014 | High Pressure Sodium | 38.91119327000 | -76.93541543000
9/16/08 | 575572 | 1010 | MASSACHUSETTS AVE | NW | 9/16/08 | 25961 | 2M216 | (Light out) | DA 9-16-08 @ 235am P harvin repaired pole #25961 | High Pressure Sodium | 38.90379985000 | -77.02690625000
9/15/08 | 574977 | 601 | 4TH ST | NW | 9/22/08 | 60444 | 68627 | (Light out) | DA 9-17-08 @ 1219am T. Richards repaired pole tag missing 9-19-08 S.Manning---found already tagged(sconnor) | High Pressure Sodium | 38.89820486000 | -77.01611532000
9/15/08 | 574969 | 521 | G ST | NW | 9/19/08 | 60667 | 60081 | (Light out) | DA 9-18-08 @ 1125pm T. Richards repaired pole #60667- adjusted photocell DA 9-18-08 @ 1200am P. Harvin Bad address DA 9-17-08 @ 1206am T. Richards request for map - pole #s and address don't match up 9-17-08 D.Moore---blocked by construction(sconnor) | Incandescent | 38.89840382000 | -77.01908312000
9/15/08 | 574929 | 711 | D ST | NW | 9/17/08 | 60088 | 2M325 | (Light out) | DA 9-16-08 @ 1129pm T. Richards repaired pole #60088 - repaired loose connection in powerdoor | High Pressure Sodium | 38.89485723000 | -77.02246234000
9/15/08 | 574927 | 1044 | 5TH ST | NW | 9/16/08 | 60069 | 6A143 | (Light out) | DA 9-16-08 Duplicate N/C ticket to wo #497954 No Hansen # | High Pressure Sodium | 38.90338284000 | -77.01883666000
9/15/08 | 574924 | 425 | MASSACHUSETTS AVE | NW | 9/16/08 | 60482 | 6A192 | (Light out) | DA 9-16-08 @ 410am C. Ashton repaired pole #60482 | Mercury Vapor | 38.90049835000 | -77.01683728000
9/15/08 | 574918 | 654 | H ST | NE | 9/16/08 | 61869 | 6S199 | (Light out) | DA 9-16-08 @ 315am C. Ashton repaired pole #61869 | High Pressure Sodium | 38.90030334000 | -76.99631449000
9/12/08 | 574325 | 1010 | MASSACHUSETTS AVE | NW | 9/18/08 | 25961 | 2M216 | (Light off/on) | DA 9-18-08 @ 1210am C. Ashton repaired pole #25961 DA -9-17-08 @ 1240am P. Harvin pole needs new wire- Waiting on pole # | High Pressure Sodium | 38.90379985000 | -77.02690625000
9/12/08 | 574324 | 1010 | 11TH ST | NW | 9/16/08 | 29203 | 2M214 | (Light out) | DA 9-16-08 Duplicate ticket to wo #497756 No Hansen # | High Pressure Sodium | 38.90369501000 | -77.02685773000
9/12/08 | 574322 | 1101 | L ST | NW | 9/16/08 | 25942 | 2M218 | (Light out) | DA 9-16-08 @ 250am P harvin repaired pole #25942 | High Pressure Sodium | 38.90408908000 | -77.02717553000
9/12/08 | 574321 | 0 | K ST | NW | 9/19/08 | 22402 | 6A100 | (Light out) | 2 splices DA 9-17-08 @ 220am P. Harvin pole #22402 N/C underground | High Pressure Sodium | 38.90245268000 | -77.01971021000
9/12/08 | 574320 | 504 | K ST | NW | 9/16/08 | 60470 | 6A104 | (Light out) | DA 9-16-08 @ 1200am C. AShton repaired pole #60470 (inv. updated from front to NW corner) | High Pressure Sodium | 38.90245334000 | -77.01925493000
9/12/08 | 574299 | 1125 | 11TH ST | NW | 9/17/08 | 25263 | 2M226 | (Light off/on) | DA 9-16-08 @ 1040pm P. Harvin repaired pole #25263 | High Pressure Sodium | 38.90526694000 | -77.02692404000
9/12/08 | 574275 | 1000 | 5TH ST | SE | 9/17/08 | 67557 | 6B467 | (Light out) | N Woodland No pole tag Replaced street sign(VWard 9-12-08) | High Pressure Sodium | 38.87826913000 | -76.99959928000
9/12/08 | 574266 | 1000 | 5TH ST | SE | 9/12/08 | 67557 | 6B467 | (Light out) | N Woodland Replaced street sign (VWard 9-12-08) | High Pressure Sodium | 38.87826913000 | -76.99959928000
9/12/08 | 574341 | 301 | MASSACHUSETTS AVE | NW | 10/2/08 | 60399 | 6A198 | (Light out) | DA 9-17-08 @ 151am T. Richards pole #60399 N/C underground FRONT - POLES 60398, 60399 HAVE BURNT OUT, PLEASE REPAIR | High Pressure Sodium | 38.90029659000 | -77.01558775000
9/11/08 | 573095 | 3321 | IDAHO AVE | NW | 7/31/09 | 38888DC | 3U416 | (Light out) | DA 9-12-08 @ 1240am C. Ashton pole #38888dc - refer to DDOT defective 400 mv fixture (updated inventory from a 150 hps to 400 MV) | Mercury Vapor | 38.93408385000 | -77.07471732000
9/11/08 | 573068 | 908 | EASTERN AVE | NE | 9/12/08 | 79483 | 7A152 | (Light out) | DA 9-12-08 @ 250am T. Richards repaired pole #79483 | High Pressure Sodium | 38.88978699000 | -76.95795735000
9/11/08 | 573023 | 600 | MICHIGAN AVE | NE | 9/11/08 | 53649DC | 5U721 | (Light out) | 9-11-08 @ 1250am G. Hicks repaired pole #53649dc (update from mv to hps light type) | High Pressure Sodium | 38.93248081000 | -76.99750323000
9/10/08 | 572999 | 600 | MICHIGAN AVE | NE | 9/11/08 | 53649DC | 5U721 | (Light off/on) | DA- 9-12-08 @ 1112pm G. Hicks pole #53649dc previously repaired refer to wo #573023 | High Pressure Sodium | 38.93248081000 | -76.99750323000
9/10/08 | 572993 | 0 | NEW YORK AVE | NE | 9/11/08 | 56832 | 5M053 | (Light out) | 9-11-08 @ 326am G. Hicks repaired pole #56832 | High Pressure Sodium | 38.91324438000 | -76.99169504000
9/10/08 | 572989 | 0 | H ST | NE | 2/6/12 | 54406 | 5M277 | (Light off/on) | 9-29-08 (V Ward) Inside of construction zone DA - 9-12-08 @ 1050pm G. Hicks - installed 250 hps bulb - pole #54406, *fixture is mounted to pole with a steal band, the band is broke and held togather with tape. | High Pressure Sodium | 38.90031428000 | -76.98381797000
9/10/08 | 572982 | 4119 | 9TH ST | NW | 9/12/08 | 4J793 | 4G331 | (Light out) | DA 9-12-08 @ 1247am R. Warren repaired pole #4J793 9-11-08 @ 458am R. Warren pole #4j793 Needs 250hps fixture | High Pressure Sodium | 38.94117354000 | -77.02497316000
9/10/08 | 573214 | 635 | T ST | NW | 9/15/08 | 14389 | 1M006 | (Light out) | DA 9-15-08 @ 435am R. Warren repaired pole #14389 BASKETBALL COURT - callere requesting light be prepaired at location | High Pressure Sodium | 38.91563319000 | -77.02130285000
9/9/08 | 572152 | 1826 | CALVERT ST | NW | 9/10/08 | 11197 | 1A003 | (Light out) | 9-10-08 @ 400am R. Warren repaired pole #11197 | High Pressure Sodium | 38.92316276000 | -77.04378689000
9/9/08 | 572120 | 1420 | 17TH ST | NW | 9/9/08 | 26731 | 2M076 | (Light out) | 9-9-08 @ 240am K. Hollins repaired pole #26731 | High Pressure Sodium | 38.90955268000 | -77.03857681000
9/8/08 | 571445 | 0 | IOWA AVE | NW | 9/9/08 | 4K496 | 4U128 | (Light out) | 9-9-08 @ 311am R. Warren repaired pole #4k496 | High Pressure Sodium | 38.94605354000 | -77.02957834000
9/8/08 | 571477 | 0 | 1ST ST | NE | 9/11/08 | 61240 | 6A268 | (Light out) | 9-11-08 @ 1250an T. Richard secured t base door pole #61240 FRONT - STREETLIGHT BOX IS OPEN, PLEASE CORRECT. | High Pressure Sodium | 38.90555245000 | -77.00598444000
9/5/08 | 570840 | 1100 | HALF ST | SE | 9/8/08 | 67435 | 6B100 | (Light out) | 9-8-08 T. Richards repaired pole #67435 1100 K STREET SE - K Caller states metal pole needs repairing | High Pressure Sodium | 38.87824281000 | -77.00752674000
9/5/08 | 570799 | 643 | BARNES ST | NE | 9/5/08 | 72469 | 7U750 | (Light out) | 9-05-08 L Roberto/Marc Installed 1-118 globe 250w hps lamp, NWPC 4 screws and drilled holes for screws | High Pressure Sodium | 38.90075954000 | -76.95122635000
9/2/08 | 568607 | 1933 | 18TH ST | NW | 9/4/08 | 26784 | 21410 | (Light out) | 9-4-08 @ 1240am K. Hollins repaired pole #26784 (inventory updated from cobra to cutoff) IN FRONT OF ADDRESS - | High Pressure Sodium | 38.91663347000 | -77.04174081000
9/2/08 | 568405 | 2201 | G ST | NW | 9/3/08 | 27947 | 2M443 | (Light out) | 9-3-08 @ 230am K. Hollins repaired pole #27947 (updated from 250 hps to 400 hps) | High Pressure Sodium | 38.89827367000 | -77.04945470000
8/28/08 | 567288 | 1010 | 11TH ST | NW | 8/28/08 | 29203 | 2M214 | (Light out) | 8-28-08 D. Acab duplicate ticket to wo #497756 no Hansen # | High Pressure Sodium | 38.90369501000 | -77.02685773000
8/28/08 | 567280 | 3630 | GEORGIA AVE | NW | 8/29/08 | 12966 | 1G220 | (Light out) | 8-29-08 @ 420am C. Ashton repaired pole #12966 | High Pressure Sodium | 38.93494424000 | -77.02420680000
8/27/08 | 566672 | 206 | D ST | SE | 8/28/08 | 65644 | 65618 | (Light out) | 8-28-08 @ 437am R. Warren repaired pole #65644 | High Pressure Sodium | 38.88502510000 | -77.00336540000
8/27/08 | 566610 | 1100 | 2ND ST | SE | 9/11/08 | 68135 | 6A409 | (Light out) | 8-29-08 @ 220am R. Warren pole #68135 N/C underground | High Pressure Sodium | 38.87682972000 | -77.00287771000
8/27/08 | 566595 | 1000 | 4TH ST | SE | 8/28/08 | 67542 | 6A434 | (Light out) | 8-28-08 @ 454am R. Warren repaired pole #67542 | High Pressure Sodium | 38.87830526000 | -77.00064838000
8/27/08 | 566537 | 0 | SHERIDAN RD | SE | 8/27/08 | 81353DC | 8U654 | (Light out) | 8-27-08 T Osvatics Installed 400w hps lamp, TLP | High Pressure Sodium | 38.85641207000 | -76.99331957000
8/27/08 | 566529 | 900 | UPSHUR ST | NW | 8/27/08 | 4J744 | 4G330 | (Light out) | 8-27-08 @ 420am C. Ashton repaired pole #4J744 | High Pressure Sodium | 38.94182164000 | -77.02494834000
8/27/08 | 566519 | 0 | MASSACHUSETTS AVE | NW | 12/9/08 | 25965 | 2G955 | (Light out) | 8-27-08 @ 240am K. Hollins pole #25965 Needs new T Base AL JOHNSON 12/9/08 WORK COMPLETED FOUND OK NEW T-BASE | High Pressure Sodium | 38.90301953000 | -77.02459215000
8/26/08 | 565993 | 3033 | BLADENSBURG RD | NE | 8/28/08 | 58720DC | 5A172DC | (Light out) | 8-28-08 T Osvatics Installed 189 inc lamp 8-28-08 @ 1240am G. Hicks - Car Blocking light ALLEY - wooden alleylight is out | Incandescent | 38.92960546000 | -76.95868010000
8/26/08 | 565880 | 3233 | PENNSYLVANIA AVE | SE | 8/27/08 | 78547DC | 7E110 | (Light off/on) | 8-27-08 @ 142am G. Hicks repaired pole #78547dc (inventory updated) | High Pressure Sodium | 38.86864144000 | -76.95900959000
8/26/08 | 565833 | 0 | 7TH ST | NW | 8/26/08 | 22433 | 6M631 | (Light out) | 8-26-08 @ 250am R. Warren repaired pole #22433 | High Pressure Sodium | 38.89625834000 | -77.02182627000
8/25/08 | 565178 | 1610 | NEW HAMPSHIRE AVE | NW | 8/25/08 | 26873 | 2M143 | (Light dim) | 8-25-08 @ 1100pm K. Hollins ligjt previously repaired last night refer to wo #563892 | High Pressure Sodium | 38.91159504000 | -77.04174330000
8/22/08 | 563892 | 1610 | NEW HAMPSHIRE AVE | NW | 8/25/08 | 26873 | 2M143 | (Light out) | 8-25-08 @ 105am K. Hollins repaired pole #26873 | High Pressure Sodium | 38.91159504000 | -77.04174330000
8/21/08 | 563112 | 1329 | 11TH ST | NW | 8/21/08 | 25257 | 2M241 | (Light out) | 8-21-08 @ 210am K. Hollins repaired pole #25257 | High Pressure Sodium | 38.90827521000 | -77.02692382000
8/21/08 | 563108 | 1101 | 11TH ST | NW | 8/21/08 | 25267 | 2M221 | (Light out) | 8-21-08 @ 140am K. Hollins repaired pole #25267 | High Pressure Sodium | 38.90427518000 | -77.02692262000
8/20/08 | 562510 | 3901 | PENNSYLVANIA AVE | SE | 8/21/08 | 78525DC | 7E135DC | (Light off/on) | 8-21-08 @ 151am G. Hicks repaired pole #78525dc | High Pressure Sodium | 38.86569632000 | -76.95176682000
8/20/08 | 562403 | 422 | 8TH ST | NW | 8/20/08 | 60658 | 2M376 | (Light out) | 8-20-08 @ 350am K. Hollins repaired pole #60658 | High Pressure Sodium | 38.89566169000 | -77.02306645000
8/20/08 | 562384 | 2348 | BENNING RD | NE | 8/20/08 | 74442DC | 7E173 | (Light out) | 8-20-08 @ 1210am T. Richards repaired pole #74442dc | High Pressure Sodium | 38.89753179000 | -76.96912923000
8/20/08 | 562377 | 0 | 22ND ST | NW | 8/20/08 | 28287 | 2A222 | (Light out) | 8-20-08 @ 225am K. Hollins repaired pole #28287 | High Pressure Sodium | 38.90015885000 | -77.04890071000
8/19/08 | 561899 | 0 | 7TH ST | NW | 8/20/08 | 25654 | 6A815 | (Light out) | 8-20-08 D.Acab Duplicate ticket to wo #561206 No Hansen # STREETLIGHT IS ON SOUTHWEST CORNER OF INTERSECTION. - | High Pressure Sodium | 38.91104528000 | -77.02202690000
8/19/08 | 561724 | 1701 | MASSACHUSETTS AVE | NW | 8/19/08 | 27021 | 2M086 | (Light out) | 8-19-08 @ 340am K. Hollins repaired pole #27021 | High Pressure Sodium | 38.90807048000 | -77.03866125000
8/19/08 | 561209 | 1530 | 11TH ST | NW | 8/19/08 | 25286 | 2U045 | (Light out) | 8-19-08 @ 1230am K. Hollins repaired pole #25286 | High Pressure Sodium | 38.91105847000 | -77.02715860000
8/19/08 | 561206 | 0 | 7TH ST | NW | 4/3/09 | 25654 | 6A815 | (Light out) | DA 4-3-09 @ 1250am H. Darden pole #25654 is on and working 8-21-08 H Lancaster -REFER back to PEPCO traffic pole & S L Cable in same duct (Severn don't have key to vault ) 8-19-08 @ 1200am G. Hicks pole #25654 N/C @ base - refer to fault crew pole is | High Pressure Sodium | 38.91104528000 | -77.02202690000
8/19/08 | 561204 | 4514 | 13TH ST | NW | 8/19/08 | 4K422 | 4U131 | (Light out) | 8-18-08 @ 1145pm R. Warren repaired pole #4k422 | High Pressure Sodium | 38.94571765000 | -77.02978404000
8/15/08 | 560514 | 1350 | CONNECTICUT AVE | NW | 8/15/08 | 24527 | 2U491 | (Light out) | 8-15-08 @ 240am K. Hollins repaired pole #24527 | High Pressure Sodium | 38.90838138000 | -77.04291014000
8/15/08 | 560504 | 0 | PENNSYLVANIA AVE | NW | 8/15/08 | 23687 | 2G666 | (Light out) | 8-15-08 @ 150am K. Hollins repaired pole #23687 | High Pressure Sodium | 38.90280693000 | -77.05126474000
8/14/08 | 559954 | 1300 | 11TH ST | SE | 8/15/08 | 67735 | 6L924 | (Light out) | 8-15-08 @ 135am T. Richards repaired pole #67735 | High Pressure Sodium | 38.87450805000 | -76.99165530000
8/14/08 | 559951 | 0 | L ST | SE |  | 67703 | 6B463 | (Light out) | 8-18-08 H Lancaster PEPCO is putting in new M/H also, other construction going on in area feeds are cut off in M/H waiting for power to be restored 8-15-08 @ 1245am T. Richards pole #67703 N/C underground | High Pressure Sodium | 38.87758688000 | -76.99992078000
8/14/08 | 559950 | 1000 | 4TH ST | SE | 8/15/08 | 67542 | 6A434 | (Light out) | 8-15-08 @ 1205am T. Richards repaired pole #67542 | High Pressure Sodium | 38.87830526000 | -77.00064838000
8/14/08 | 559949 | 200 | I ST | SE | 8/15/08 | 67648 | 6A422 | (Light out) | 8-15-08 @ 1220am T. Richards repaired pole #67648 | High Pressure Sodium | 38.87934724000 | -77.00236217000
8/13/08 | 559401 | 0 | RIGGS RD | NE | 8/14/08 | 4P555DC | 4U176 | (Light out) | 8-14-08 @ 1210am R. Warren repaired pole #4P555DC | High Pressure Sodium | 38.95872032000 | -77.00127918000
8/13/08 | 559400 | 0 | CHILLUM PL | NE | 8/14/08 | 4P513DC | 4U169 | (Light out) | 8-14-08 @ 1205am R. Warren repaired pole #4P513DC | High Pressure Sodium | 38.95927698000 | -77.00253696000
8/13/08 | 559337 | 740 | 6TH ST | NW | 8/28/08 | 22514 | 6S426 | (No current) | 8/28/08 Jeramiah installed conduit , cable & made splices in MH & pole base , job complete | High Pressure Sodium | 38.89941296000 | -77.02001456000
8/12/08 | 558887 | 1822 | NEW HAMPSHIRE AVE | NW | 8/14/08 | 26863 | 2M046 | (Light out) | 8-14-08 @ 1130pm K. Hollins repaired pole #26863 ODD SIDE, MIDDLE OF BLOCK - 18TH | High Pressure Sodium | 38.91498083000 | -77.03857184000
8/12/08 | 558687 | 1627 | BENNING RD | NE | 8/12/08 | 63611 | 6M770 | (Light out) | 8-12-08 @ 500am T. Richards repaired pole #63611 | High Pressure Sodium | 38.89950280000 | -76.98055920000
8/12/08 | 558668 | 611 | 22ND ST | NW | 8/12/08 | 28290 | 2M437 | (Light out) | 8-12-08 @ 315am K. Hollins repaired pole #28290 | High Pressure Sodium | 38.89769965000 | -77.04891041000
8/12/08 | 558151 | 0 | 9TH ST | NW | 8/12/08 | 25437 | 2L558 | (Light out) | 8-11-08 @ 1155pm K. Hollins repaired pole #25437 | High Pressure Sodium | 38.90380790000 | -77.02408338000
8/8/08 | 557344 | 1915 | BENNING RD | NE | 8/11/08 | 74699DC | 6M785 | (Light out) | 8-10-08 @ 1030pm L. Keys repaired pole #74699dc | High Pressure Sodium | 38.89867900000 | -76.97586824000
8/8/08 | 557269 | 0 | K ST | NW | 8/8/08 | 24677 | 2G692 | (Light out) | 8-8-08 @ 434am K. Hollins repaired pole #24677 | High Pressure Sodium | 38.90236272000 | -77.04868832000
8/8/08 | 557250 | 0 | H ST | NW | 8/8/08 | 22569 | 2M434 | (Light out) | 8-8-08 @ 259am K. Hollins repaired pole #22569 | High Pressure Sodium | 38.89973622000 | -77.02284281000
8/8/08 | 556800 | 1815 | 17TH ST | NW | 8/8/08 | 26742 | 2M047 | (Light out) | 8-8-08 @ 104am K. Hollins repaired pole #26742 | High Pressure Sodium | 38.91462969000 | -77.03856203000
8/7/08 | 556524 | 200 | I ST | SE | 8/7/08 | 67648 | 6A422 | (Light out) | 8-7-08 @ 240am T. Richards repaired pole #67648 - reconnected loose wire | High Pressure Sodium | 38.87934724000 | -77.00236217000
8/7/08 | 556516 | 4608 | NANNIE HELEN BURROUGHS AVE | NE | 8/7/08 | 71300DC | 7A234 | (Light out) | 8-7-08 @ 252am G. Hicks repaired pole #71300dc and repaired pole tag | High Pressure Sodium | 38.89940450000 | -76.93569847000
8/7/08 | 556502 | 0 | NANNIE HELEN BURROUGHS AVE | NE | 8/8/08 | 72645 | 7S073 | (Light out) | 8-7-08 @ 1155pm T. Richards repaired pole #72645 8-7-08 @ 230am G. Hicks - Needs 400 hps powerdoor pole tag missing | High Pressure Sodium | 38.89826452000 | -76.92554310000
8/6/08 | 556043 | 5920 | GEORGIA AVE | NW | 8/7/08 | 4E219 | 4A824 | (Light out) | 8-7-08 @ 228am R. Warren repaired pole #4E219 | High Pressure Sodium | 38.96170865000 | -77.02785877000
8/6/08 | 555957 | 5127 | H ST | SE | 8/11/08 | 75492 | 75492DC | (Light out) | 8-6-08 @ 113am G. Hicks repaired pole #75492 Needs major tree trim | High Pressure Sodium | 38.87810752000 | -76.92948653000
8/5/08 | 555458 | 1454 | IRVING ST | NW | 8/6/08 | 12741 | 1G036 | (Light out) | 8-6-08 @ 230am K. Hollins repaired pole #12741 | High Pressure Sodium | 38.92872574000 | -77.03484302000
8/5/08 | 555500 | 0 | 1ST ST | NE | 8/6/08 | 61248 | 6A282 | (Light out) | 8-6-08 D. Acab duplicate ticket to wo #404559 no hansen # 8-6-08 @ 330am T. Richards pole #61248 S.W. CORNER OF INTERS - metal pole street light, wires dangling, and asrm missing over 1 year | High Pressure Sodium | 38.90791176000 | -77.00580646000
8/5/08 | 555511 | 1800 | 18TH ST | NW | 8/7/08 | 26779 | 2M110 | (Light out) | 8-7-08 @ 220am K. Hollins repaired pole #26779 IN FRONT OF GAS STATON AT CORNER OF 18TH AND S. - | High Pressure Sodium | 38.91448625000 | -77.04174656000
8/4/08 | 554882 | 1421 | 37TH ST | NW | 8/5/08 | 21143 | 2G207 | (Light out) | 8-5-08 @ 245am K. HOllins repaired pole #21143 reconnected hot @ fixture | High Pressure Sodium | 38.90829140000 | -77.07156966000
8/4/08 | 554913 | 1544 | KENILWORTH AVE | NE | 8/6/08 | 70297 | 7M049 | (Light out) | 8-6-08 @ 1205am L. Keys repaired pole #70297 FRONT - Streetlight on metal pole is constantly going on and off. caller would like to have the light looked at or blub changed. | High Pressure Sodium | 38.91061657000 | -76.93592995000
8/4/08 | 554799 | 0 | E ST | NW | 8/4/08 | 23334 | 2M356 | (Light out) | 8-4-08 @ 100am T. Richards repaired pole #23334 - reaimed photocell | High Pressure Sodium | 38.89621967000 | -77.02247784000
8/4/08 | 554781 | 0 | 13TH ST | NW | 8/4/08 | 4K431 | 4U145 | (Light out) | 8-4-08 @ 120am R. Warren repaired pole #4k431 | High Pressure Sodium | 38.94333464000 | -77.02962264000
8/1/08 | 554260 | 619 | H ST | NW | 8/5/08 | 22636 | 6M693 | (Light out) | 8-4-08 @ 1115pm K. Hollins repaired pole #22636 reconnected hot @ fixture and base 8-4-08 E Graves/Patterson Chinatown pole has current but, needs NWP or fixture REFER to Night Crew | High Pressure Sodium | 38.89990221000 | -77.02076719000
8/1/08 | 554259 | 740 | 6TH ST | NW | 8/5/08 | 22513 | 6S425 | (Light out) | 8-4-08 D.Acab duplicate tickst to wo #404538 No Hansen # 8-4-08 E Graves/Patterson no Current @ pole REFER to fault crew (underground) already open under N/C #404538 | High Pressure Sodium | 38.89950950000 | -77.02001122000
8/1/08 | 553723 | 0 | KENILWORTH AVE | NE | 8/1/08 | 79489 | 7A158 | (Light out) | 7-31-08 @ 1120pm C. Ashton repaired pole #79489 | High Pressure Sodium | 38.89044233000 | -76.95766327000
7/31/08 | 553666 | 0 | EAST CAPITOL ST | NE | 8/1/08 | 63634 | 6M824 | (Light out) | 8-1-08 @ 110am T. Richards repaired pole #63634 | High Pressure Sodium | 38.89007149000 | -76.97454092000
7/31/08 | 553664 | 0 | 22ND ST | NE | 8/1/08 | 63632 | 6M793 | (Light off/on) | 8-1-08 @ 140am T. Richards repired pole #63632 | High Pressure Sodium | 38.89028237000 | -76.97436503000
7/31/08 | 553641 | 1100 | 2ND ST | SE | 8/12/08 | 68135 | 6A409 | (Light out) | 8/8/08 H . Lancaster installed 295 lamp, TL photocell & mades splices in pole base. 7-31-08 @ 1240an T. Richards pole #68133 N/C underground 8-3-08-W.Black- address and pole number is now fixed | High Pressure Sodium | 38.87682972000 | -77.00287771000
7/30/08 | 553151 | 1010 | MASSACHUSETTS AVE | NW | 7/31/08 | 25961 | 2M216 | (Light out) | 7-31-08 @ 145am K. Hollins repaired pole #25961 - reconnected neturial @ base 7-30-08 No pole# | High Pressure Sodium | 38.90379985000 | -77.02690625000
7/30/08 | 553117 | 0 | H ST | NW | 7/31/08 | 22619 | 2G963 | (Light out) | 7-31-08 @ 130am K. Hollins repaired pole #22619 - reconnected switch leg on watchman | High Pressure Sodium | 38.89990649000 | -77.02637602000
7/30/08 | 553114 | 0 | 23RD ST | NW | 2/6/12 | 28320 | 2M268 | (Light out) | 9-18-08 (V Ward) REFER to DDOT New construction project 8-26-08 R Gray/Damien S Need Grey Crown or new pole need to be installed 7-31-08 @ 355am K. Hollins repaired pole #28320 - reconnected hot towards watchman Twin 20 metal west side has no arm o | High Pressure Sodium | 38.89242239000 | -77.05003950000
7/30/08 | 553170 | 0 | 7TH ST | NW | 8/1/08 | 25659 | 6A800 | (Light out) | 8-1-08 @ 1255am K. Hollins repaired pole #25659- metal pole... burnt out bulb | High Pressure Sodium | 38.90822210000 | -77.02201697000
7/29/08 | 552464 | 0 | CALIFORNIA ST | NW | 7/30/08 | 11159 | 1A102 | (Light out) | 7-30-08 @ 1235am C. Ashton repaired pole #11159 and secured pole tag @ 14ft | High Pressure Sodium | 38.91772320000 | -77.04056351000
7/29/08 | 552459 | 2412 | WISCONSIN AVE | NW | 7/30/08 | 30166 | 3G066 | (Light out) | 7-30-08 @ 120am C. Ashton pole #30166 previously repaired refer to wo #552376 | High Pressure Sodium | 38.92154388000 | -77.07218059000
7/29/08 | 552376 | 2412 | WISCONSIN AVE | NW | 7/29/08 | 30166 | 3G066 | (Light out) | 7-29-08 @ 315am C. Ashton repaired pole #30166 | High Pressure Sodium | 38.92154388000 | -77.07218059000
7/28/08 | 551874 | 2473 | 18TH ST | NW | 7/29/08 | 11406 | 1G478 | (Light out) | 7-29-08 @ 1225am L. Keys pole #11406 burn tested light found okay | High Pressure Sodium | 38.92224805000 | -77.04243267000
7/28/08 | 551807 | 0 | 23RD ST | NW | 7/29/08 | 28345 | 2M285 | (Light out) | 7-29-08 @ 205am K. Hollins repaired pole #28345 | High Pressure Sodium | 38.90189255000 | -77.05000095000
7/28/08 | 551788 | 0 | 35TH ST | NW | 7/30/08 | 36941 | 3G109 | (Light off/on) | 7-30-08 L Roberto Installed base door 7-29-08 @ 245am C. Ashton repaired pole #36941 *needs T base door | High Pressure Sodium | 38.91759465000 | -77.06949788000
7/28/08 | 551745 | 1404 | H ST | NE | 7/28/08 | 62326 | 6S139 | (Light out) | 7-28-08 G. Hicks repaired pole #62326 | High Pressure Sodium | 38.90029477000 | -76.98535817000
7/27/08 | 551933 | 611 | H ST | NW | 8/1/08 | 22637 | 6M692 | (Light out) | 8/1/08 H. Lancaster installed cable & made splices in (2) MH . job complete. | High Pressure Sodium | 38.89990283000 | -77.02054702000
7/27/08 | 551720 | 618 | H ST | NW | 7/29/08 | 22561 | 6M699 | (Light out) | 7-29-08 @ 355am K. Hollins repaired pole #22561(china town light)- street light ist working | High Pressure Sodium | 38.89973495000 | -77.02087482000
7/25/08 | 551105 | 1044 | 5TH ST | NW | 7/28/08 | 60069 | 6A143 | (Light out) | 7/28/08 New poles being installed by outside contractor, refer to DDot . 7-28-08 T. Richards pole #60069 open neturial refer to fault crew | High Pressure Sodium | 38.90338284000 | -77.01883666000
7/25/08 | 551103 | 462 | K ST | NW | 7/28/08 | 60463 | 6A113 | (Light out) | 7/28/08 New poles being installed by outside contractor, refer to DDot . 7-28-08 T. Richards pole #60463 open neturial refer to fault crew | High Pressure Sodium | 38.90260167000 | -77.01799763000
7/25/08 | 551078 | 0 | EAST CAPITOL ST | NE | 7/28/08 | 63634 | 6M824 | (Light out) | 7-28-08 L Roberto/Marc Installed 1-400w hps lamp, power door, fixture 75ft # 10 wire & TLP 7-28-08 @ 240am T. Richards pole #63634 needs 400 hps powerdoor | High Pressure Sodium | 38.89007149000 | -76.97454092000
7/25/08 | 551055 | 0 | KENILWORTH AVE | NE | 7/31/08 | 79489 | 7A158 | (Light out) | 7-31-08 @ 1100pm T. Richards repaired pole #79489 | High Pressure Sodium | 38.89044233000 | -76.95766327000
7/25/08 | 551039 | 0 | GRANT ST | NE | 7/29/08 | 72339DC | 7A216 | (Light out) | 7-29-08 @ 1200am L. Keys repaired pole #72339dc | High Pressure Sodium | 38.89843429000 | -76.93131145000
7/25/08 | 551019 | 3144 | PENNSYLVANIA AVE | SE | 7/30/08 | 78554DC | 7E101DC | (Light out) | 7-30-08 @ 140am L. Keys repaired pole #78554dc 7-29-08 M Brewer NEED MOT TOO MUCH TRAFFIC | High Pressure Sodium | 38.86981292000 | -76.96183892000
7/25/08 | 550976 | 0 | EAST CAPITOL ST | NE | 7/28/08 | 63634 | 6M824 | (Light out) | 7-28-08 L Roberto/Marc Installed 1-power door, lamp. TLP 7-25-08 M Craig Need to install 400 hps fixture 7-25-08 @ 420am T. Richards pole #63634 Needs 400 hps powerdoor | High Pressure Sodium | 38.89007149000 | -76.97454092000
7/25/08 | 550958 | 1404 | H ST | NE | 7/25/08 | 62326 | 6S139 | (Light out) | 7-25-08 @ 305am T. Richard repaired pole #62326 | High Pressure Sodium | 38.90029477000 | -76.98535817000
7/24/08 | 550355 | 1627 | BENNING RD | NE | 7/25/08 | 63611 | 6M770 | (Light out) | 7-25-08 @ 300am T. Richards repaired pole #63611 | High Pressure Sodium | 38.89950280000 | -76.98055920000
7/24/08 | 550212 | 3300 | O ST | NW | 7/24/08 | 21106 | 2G177 | (Light out) | 7-24-08 @ 155am K. Hollins repaired pole #21106 | High Pressure Sodium | 38.90770069000 | -77.06613582000
| 549732 | 3300 | O ST | NW | 7/25/08 | 21106 | 2G177 | (Light out) | 7-25-08 K. Hollins light previously repaired refer to wo #550212 AT THE INTERSECTION - the globe and light on this historic light post is just hanging on by the wires.(metal) | High Pressure Sodium | 38.90770069000 | -77.06613582000
7/22/08 | 548973 | 7051 | SPRING PL | NW | 7/22/08 | 4H523DC | 4H523 | (Light out) | 7-22-08 @ 155am R. Warren repaired pole #4h523dc | Incandescent | 38.97594098000 | -77.01865986000
7/22/08 | 548972 | 7051 | SPRING PL | NW | 7/22/08 | 4H522DC | 4H522 | (Light out) | 7-22-08 @ 153am R. Warren repaired pole #4h522dc | Incandescent | 38.97614004000 | -77.01896257000
7/22/08 | 548485 | 0 | RHODE ISLAND AVE | NW | 7/22/08 | 59997 | 5A189 | (Light out) | 7-22-08 @ 107am G. Hicks repaired pole #59997 | High Pressure Sodium | 38.91491231000 | -77.01415169000
7/20/08 | 548287 | 1825 | NEW HAMPSHIRE AVE | NW | 7/20/08 | 26888 | 2M043 | (Light out) | 7-20-08 @1120pm K. Hollins repaired pole #26888 | High Pressure Sodium | 38.91488933000 | -77.03835762000
7/18/08 | 547677 | 400 | RHODE ISLAND AVE | NW | 7/18/08 | 59988 | 5A180 | (Light out) | 7-18-08 @ 335am G. HIcks repaired pole #59988 | High Pressure Sodium | 38.91371248000 | -77.01761756000
7/18/08 | 547672 | 0 | I ST | NW | 7/18/08 | 22496 | 6S558 | (Light out) | 7-18-08 @ 325am K. HOllins repaired pole #22496 | High Pressure Sodium | 38.90081044000 | -77.02175292000
7/18/08 | 547671 | 629 | H ST | NW | 7/18/08 | 22633 | 6M696 | (Light out) | 7-18-08 @ 340am K. Hollins diconnected fixture and made safe | High Pressure Sodium | 38.89990404000 | -77.02140626000
7/18/08 | 547670 | 1100 | 2ND ST | SE | 7/18/08 | 68135 | 6A409 | (Light out) | 7-18-08 @ 310am T. Richards reset tl phoocell pole #68135 | High Pressure Sodium | 38.87682972000 | -77.00287771000
7/18/08 | 547606 | 2218 | WISCONSIN AVE | NW | 7/18/08 | 30161 | 3G086 | (Light out) | 7-18-08 @ 200am C. Ashton repaired pole #30161 | High Pressure Sodium | 38.91961236000 | -77.07085524000
7/18/08 | 547595 | 400 | RHODE ISLAND AVE | NW | 7/18/08 | 59987 | 5A178 | (Light out) | 7-18-08 @ 1255am G. Hicks repaired pole #59987 | High Pressure Sodium | 38.91400893000 | -77.01743154000
7/18/08 | 547162 | 0 | M ST | NW | 7/18/08 | 23728 | 2U535 | (Light out) | 7-17-08 @ 1145pm K. Hollins repaired pole #23728 | High Pressure Sodium | 38.90574873000 | -77.04183268000
7/17/08 | 547637 | 0 | PATTERSON ST | NE | 7/23/08 | 61261 | 6A274 | (Light out) | 7-23-08 M Craig Installed T-Base door 7-21-08 @ 1205am T. Richards pole #61261 **needs t base door AT THE INTERSECTION - the panel door is missing from the base of the streetlight. | High Pressure Sodium | 38.90650714000 | -77.00604658000
7/17/08 | 547124 | 926 | T ST | NW | 7/21/08 | 13450 | 1L367 | (Light out) | 7-20-08 @ 1140pm R. Warren pole #13450 light found okay - previously repaired | High Pressure Sodium | 38.91552698000 | -77.02529625000
7/17/08 | 547121 | 0 | H ST | NE | 7/18/08 | 62347 | 6S110 | (Light out) | 7-18-08 @ 115am T. Richards repaired pole #62347 | High Pressure Sodium | 38.90011694000 | -76.99007929000
7/16/08 | 547651 | 2700 | WISCONSIN AVE | NW | 7/22/08 | 30140 | 3G033 | (Light out) | 7-21-08 @ 1135pm C. Ashton repaired pole #30140 FRONT - street lights are out | High Pressure Sodium | 38.92473706000 | -77.07330419000
7/16/08 | 546539 | 0 | SHERMAN AVE | NW | 7/17/08 | 14220 | 1G456 | (Light out) | 7-16-08 @ 1155pm C. Ashton repaired pole #14220 and secured pole tag @ 14ft | High Pressure Sodium | 38.92254478000 | -77.02525138000
7/16/08 | 546538 | 2400 | SHERMAN AVE | NW | 7/17/08 | 12585 | 1G465 | (Light out) | 7-17-08 @ 155am C. Ashton repaired pole #12585 | High Pressure Sodium | 38.92169397000 | -77.02539372000
7/16/08 | 546530 | 3123 | SHERMAN AVE | NW | 7/17/08 | 12851 | 1L261 | (Light out) | 7-17-08 @ 120am C. Ashton repaired pole #12851 | High Pressure Sodium | 38.92946499000 | -77.02622282000
7/16/08 | 546528 | 1454 | IRVING ST | NW | 7/17/08 | 12741 | 1G036 | (Light out) | 7-17-08 @ 1210am K. Hollins repaired pole #12741 | High Pressure Sodium | 38.92872574000 | -77.03484302000
7/16/08 | 546519 | 0 | EAST CAPITOL ST | SE | 7/17/08 | 73588 | 73588DC | (Light out) | 7-17-08 @ 345am L. Keys repaired pole #73588 | High Pressure Sodium | 38.88965078000 | -76.92405517000
7/16/08 | 546495 | 400 | RHODE ISLAND AVE | NW | 7/18/08 | 59987 | 5A178 | (Light out) | 7-18-08 @ 400am G. Hicks repaired pole #59987 | High Pressure Sodium | 38.91400893000 | -77.01743154000
7/16/08 | 546342 | 454 | I ST | NW | 7/16/08 | 61059 | 6A740 | (Light out) | 7-16-08 @ 135am T. Richards repaired pole #61059 | High Pressure Sodium | 38.90185344000 | -77.01769222000
7/15/08 | 545695 | 3848 | SOUTH CAPITOL ST | SE | 7/21/08 | 85647 | 8M006 | (Light out) | 7-21-08 @ 145am L. Keys repaired pole #85647 | High Pressure Sodium | 38.83413920000 | -77.00815861000
7/15/08 | 545679 | 508 | MELLON ST | SE | 7/21/08 | 86496 | 8A358 | (Light out) | 7-21-08 @ 1235am L. Keys pole #s and addres don't match up | High Pressure Sodium | 38.86233552000 | -77.00031519000
7/15/08 | 545662 | 0 | RHODE ISLAND AVE | NW | 7/15/08 | 59997 | 5A189 | (Light out) | 7-15-08 @ 1054pm G. Hicks repaired pole #59997 | High Pressure Sodium | 38.91491231000 | -77.01415169000
7/15/08 | 545576 | 1100 | 2ND ST | SE | 7/15/08 | 68135 | 6A409 | (Light out) | 7-15-08 @ 105am T. Richards repaired pole #68135 | High Pressure Sodium | 38.87682972000 | -77.00287771000
7/14/08 | 544937 | 0 | 9TH ST | NW | 7/15/08 | 25437 | 2L558 | (Light out) | 7-15-08 K. Hollins pole #25437 previously repaired | High Pressure Sodium | 38.90380790000 | -77.02408338000
7/14/08 | 544870 | 2811 | PENNSYLVANIA AVE | SE | 7/15/08 | 78569DC | 7E084DC | (Light out) | 7-15-08 @ 1245am L. Keys repaired pole #78569dc | High Pressure Sodium | 38.87190486000 | -76.96697603000
7/14/08 | 544808 | 1217 | 11TH ST | NW | 7/14/08 | 25261 | 2M231 | (Light out) | 7-14-08 @ 110am K. Hollins repaired pole #25261 | High Pressure Sodium | 38.90622963000 | -77.02692296000
7/11/08 | 544103 | 200 | I ST | SE | 7/14/08 | 67648 | 6A422 | (Light out) | 7-14-08 @ 435am T. Richards repaired pole #67648 | High Pressure Sodium | 38.87934724000 | -77.00236217000
7/11/08 | 544102 | 1100 | 2ND ST | SE | 7/14/08 | 68135 | 6A409 | (Light out) | 7-14-08 @ 445am T. Richards / bad address pole #68135 can not find at this location | High Pressure Sodium | 38.87682972000 | -77.00287771000
7/11/08 | 544078 | 0 | EASTERN AVE | NE | 2/9/12 | 52365DC | 5L682 | (Light out) | 7-14-08 @ 112am G. Hicks repaired pole #52365dc G EDWARDS 7/15/08 transformer & traffic on pole | High Pressure Sodium | 38.94310507000 | -76.97366566000
7/11/08 | 544077 | 0 | EASTERN AVE | NE | 7/14/08 | 52364DC | 5L681 | (Light out) | 7-14-08 @ 114am G. Hicks repaired pole #52364dc | High Pressure Sodium | 38.94326497000 | -76.97356153000
7/11/08 | 543593 | 1500 | PARK RD | NW | 7/11/08 | 12703 | 1G369 | (Light out) | 7-11-08 @ 1200am C. Ashton repaired pole #12703 | High Pressure Sodium | 38.93118367000 | -77.03534967000
7/10/08 | 543489 | 0 | L ST | SE | 7/15/08 | 67703 | 6B463 | (Light out) | 7-15-08 R Waites Secured globe 7-10-08 Metal Pole# 67703 Globe hanging pole marked w/red tape | High Pressure Sodium | 38.87758688000 | -76.99992078000
7/10/08 | 543487 | 400 | L ST | SE |  | 67702 | 6B462 | (Light out) | 7-15-08 W Kates/UGO Unable to rod to find feed, REFER to construction crew lead cable in duct 7-11-08 @ 140am K. Hollins pole #67702 N/C under ground 7-10-08 Metal Pole# 67702 pole marked w/red tape | High Pressure Sodium | 38.87758613000 | -77.00028077000
7/8/08 | 542059 | 0 | 1ST ST | NE | 7/9/08 | 61248 | 6A282 | (Light out) | 7-9-08 D. Acab duplicate ticket refer to wo #460808 | High Pressure Sodium | 38.90791176000 | -77.00580646000
7/8/08 | 542052 | 0 | H ST | NE | 7/23/08 | 54406 | 5M277 | (Light out) | -7-21-08 L Roberto Pole missing REFER to Wayne R 7-8-08 @ 1115pm G. Hicks pole has no id tag Needs new arm and secured t base door Installed Tag 54406 | High Pressure Sodium | 38.90031428000 | -76.98381797000
7/8/08 | 542051 | 0 | BENNING RD | NE | 7/8/08 | 59597 | 5M275 | (Light out) | 7-8-08 @ 1100pm G. Hicks repaired pole #59597 and secured t base door | High Pressure Sodium | 38.90028965000 | -76.98347853000
7/8/08 | 541854 | 2915 | PENNSYLVANIA AVE | SE | 7/10/08 | 78568DC | 7E086DC | (Light out) | 7-10-08 @ 245am L. Keys repaired pole #78568dc | High Pressure Sodium | 38.87173975000 | -76.96656845000
7/3/08 | 540715 | 0 | EAST CAPITOL ST | NE | 7/9/08 | 73516 | 73516DC | (Light out) | 7-03-08 D Smith/R Gray/W Kates Installed 400w hps fixture, tear drop took down 250 made secondary tap no pole# TAG FOUND OK | High Pressure Sodium | 38.88988897000 | -76.92617008000
7/3/08 | 540613 | 1101 | NEW HAMPSHIRE AVE | NW | 7/3/08 | 23859 | 2G712 | (Light out) | 7-3-08 @ 243am K. Hollins repaired pole #23859 | High Pressure Sodium | 38.90420020000 | -77.04868539000
7/2/08 | 540636 | 150 | RHODE ISLAND AVE | NW | 7/4/08 | 59998 | 5A190 | (Light out) | 7-4-08 @ 205am T.Richards pole #59998 closed opened lens FRONT - the globe is hanging off the bulb on the pole requesting streetlight repair | High Pressure Sodium | 38.91503228000 | -77.01379913000
7/2/08 | 540060 | 1520 | 18TH ST | NW | 7/4/08 | 26771 | 2M162 | (Light out) | 7-4-08 @ 100am K. Hollins repaired pole #26771 | High Pressure Sodium | 38.91026099000 | -77.04174044000
7/2/08 | 540037 | 0 | M ST | NW | 7/3/08 | 23728 | 2U535 | (Light out) | 7-3-08 @ 100am K. Hollins repaired pole #24728 - reset TL photocell | High Pressure Sodium | 38.90574873000 | -77.04183268000
7/2/08 | 540026 | 0 | 9TH ST | NW | 7/3/08 | 25437 | 2L558 | (Light out) | 7-2-08 @ 1145pm K. Hollins repaired pole #25437 | High Pressure Sodium | 38.90380790000 | -77.02408338000
7/1/08 | 539295 | 1500 | PARK RD | NW | 7/2/08 | 12703 | 1G369 | (Light out) | 7-2-08 @ 111am T.Richards repaired pole #12703 | High Pressure Sodium | 38.93118367000 | -77.03534967000
7/1/08 | 539292 | 1454 | IRVING ST | NW | 7/3/08 | 12741 | 1G036 | (Light out) | 7/2/08 O. Taylor installed cable from pole to MH , made splices ,job complete 7-2-08 @ 1256am T. Richards pole #12741 open neturial underground refer to fault crew | High Pressure Sodium | 38.92872574000 | -77.03484302000
7/1/08 | 539289 | 3630 | GEORGIA AVE | NW | 7/2/08 | 12966 | 1G220 | (Light out) | 7-2-08 @ 217am T. Richards repaired pole #12966 | High Pressure Sodium | 38.93494424000 | -77.02420680000
7/1/08 | 539198 | 4601 | SOUTHERN AVE | SE | 7/3/08 | 75653 | 75653DC | (Light out) | 7-3-08 @ 257am L. Keys repaired pole #75653 | High Pressure Sodium | 38.87424204000 | -76.93342524000
7/1/08 | 538575 | 2407 | 18TH ST | NW | 7/1/08 | 11533 | 1G491 | (Light out) | 7-1-08 @ 1200am chris ashton repaired pole #11533 | High Pressure Sodium | 38.92063969000 | -77.04213470000
6/30/08 | 538415 | 2348 | BENNING RD | NE | 7/4/08 | 74442DC | 7E173 | (Light out) | 7-4-08 L. Keys cna not access light due to street construction on benning road 7-2-08 @ 1120pm L. Keys could not get to pole because of construction 6-30-08 Wood pole# 56152dc - pole marked w/ red tape also, ple is in construction area - second poleEast | High Pressure Sodium | 38.89753179000 | -76.96912923000
6/29/08 | 538336 | 1529 | 17TH ST | NW | 7/1/08 | 26706 | 2M021 | (Light out) | 7-1-08 @ 100am tim richards repaired pole #26706 FRONT - metal pole out. | High Pressure Sodium | 38.91077777000 | -77.03840283000
6/27/08 | 537700 | 3535 | O ST | NW | 7/1/08 | 21094 | 2G157 | (Light off/on) | 6-30-08 @ 1130pm tim richards repaired pole #21094 | High Pressure Sodium | 38.90776458000 | -77.07026540000
6/27/08 | 537594 | 1100 | 2ND ST | SW | 6/27/08 | 68133 | 6A413 | (Light out) | 6-26-08 @ 1130pm tim richards repaired pole #68133 | Incandescent | 38.87749103000 | -77.00282119000
6/27/08 | 537158 | 5101 | EASTERN AVE | NE | 6/27/08 | 50489DC | 5L657 | (Light out) | 6-27-08 @ 107am gary hicks repaired pole #50489dc | High Pressure Sodium | 38.95409137000 | -76.98748801000
6/26/08 | 537110 | 0 | 9TH ST | NW | 6/26/08 | 25437 | 2L558 | (Light out) | 6-26-08 @ 1145pm roger warren repaired pole #25437 c/p 25436 and 25438 found okay | High Pressure Sodium | 38.90380790000 | -77.02408338000
6/26/08 | 537099 | 618 | H ST | NW | 6/27/08 | 22561 | 6M699 | (Light out) | 6-27-08 @ 1241am roger warren repaired pole #22561 (inventory updated) c/p 22562 and 22560 found okay | High Pressure Sodium | 38.89973495000 | -77.02087482000
6/26/08 | 537095 | 715 | 7TH ST | NW | 6/27/08 | 22448 | 6M643 | (Light out) | 6-27-08 @ 1248am roger warren repaired pole #22448 (inventory updated) c/p 22449 and 22447 found okay | High Pressure Sodium | 38.89900931000 | -77.02182156000
6/26/08 | 537083 | 0 | WASHINGTON CIR | NW | 6/30/08 | 28509 | 2M286 | (Light out) | 6-30-08 @ 145am tim richards repaired pole #28509 | High Pressure Sodium | 38.90199338000 | -77.04975164000
6/24/08 | 535814 | 0 | 9TH ST | NW | 6/25/08 | 25437 | 2L558 | (Light out) | 6-24-08 @ 1150pm kevin hollins repaired pole #25437 c/p 25436 found okay | High Pressure Sodium | 38.90380790000 | -77.02408338000
6/24/08 | 535810 | 1826 | 18TH ST | NW | 6/25/08 | 26780 | 2M106 | (Light off/on) | 6-25-08 @ 200am kevin hollins repaired pole #26780 c/p 26779 found okay | High Pressure Sodium | 38.91492300000 | -77.04174945000
6/24/08 | 535803 | 1520 | 18TH ST | NW | 6/25/08 | 26771 | 2M162 | (Light off/on) | 6-25-08 @ 217am kevin hollins laight was repaired last night | High Pressure Sodium | 38.91026099000 | -77.04174044000
6/24/08 | 535774 | 0 | FLORIDA AVE | NE | 6/25/08 | 54443 | 5M132 | (Light out) | 5-25-08 @ 133am gary hicks repaired pole #54443 ( secured photocell) | High Pressure Sodium | 38.90877588000 | -77.00407804000
6/23/08 | 535130 | 702 | 7TH ST | NW | 6/24/08 | 22427 | 6M642 | (Light out) | 6-24-08 @ 125am kevin hollins repaired pole #22427 c/p 22444 found okay | High Pressure Sodium | 38.89872648000 | -77.02201436000
6/23/08 | 535129 | 0 | 7TH ST | NW | 6/24/08 | 22455 | 6M667 | (Light out) | 6-24-08 @ 105am kevin hollins repaired pole #22455 c/p 22479 found okay | High Pressure Sodium | 38.90101301000 | -77.02181903000
6/23/08 | 534862 | 1330 | U ST | NW | 6/25/08 | 13281 | 1G520 | (Light out) | 6-25-08 @ 135am tim richards repaired pole #13281 | High Pressure Sodium | 38.91692624000 | -77.03085442000
6/23/08 | 534855 | 4514 | 13TH ST | NW | 6/24/08 | 4K422 | 4U131 | (Light off/on) | 6-24-08 @ 234am roger warren repaired pole#4k422 c/p 4k421 and 4k423 found okay | High Pressure Sodium | 38.94571765000 | -77.02978404000
6/23/08 | 534811 | 504 | K ST | NW | 6/26/08 | 60461 | 6A101 | (Light off/on) | 6-26-08 @ 130am tim richards repaired pole #60461 | High Pressure Sodium | 38.90260703000 | -77.01950617000
6/23/08 | 534808 | 740 | 6TH ST | NW | 6/24/08 | 22513 | 6S425 | (Light out) | 6-24-08 @ 118am DA duplicate ticket to wo #479157 hansen #1724451 | High Pressure Sodium | 38.89950950000 | -77.02001122000
6/23/08 | 534804 | 0 | FLORIDA AVE | NE | 6/26/08 | 54443 | 5M132 | (Light out) | 6-26-08 @ 102am tim richards repaired pole #54443 - redirectd photocell | High Pressure Sodium | 38.90877588000 | -77.00407804000
6/20/08 | 534065 | 216 | RHODE ISLAND AVE | NW | 6/20/08 | 59995 | 5A187 | (Light out) | 6-20-08 @ 315am gary hicks repaired pole #59995 | High Pressure Sodium | 38.91463757000 | -77.01493167000
6/20/08 | 533504 | 0 | WASHINGTON CIR | NW | 6/20/08 | 28509 | 2M286 | (Light out) | 6-20-08 @ 1205am kevin hollins repaired pole #28509 (reset photo cell) | High Pressure Sodium | 38.90199338000 | -77.04975164000
6/20/08 | 533502 | 0 | 23RD ST | NW | 6/20/08 | 28342 | 2M279 | (Light out) | 6-20-08 @ 1155pm kevin hollins repaired pole #28342 (inventory updated) | High Pressure Sodium | 38.90081677000 | -77.05001410000
6/20/08 | 533497 | 1529 | 17TH ST | NW | 6/20/08 | 26706 | 2M021 | (Light out) | 6-20-08 @ 1135pm kevin hollins repaired pole #26706 (reset photocell) | High Pressure Sodium | 38.91077777000 | -77.03840283000
6/19/08 | 534014 | 1529 | 17TH ST | NW | 6/21/08 | 26706 | 2M021 | (Light out) | 6-21-08 @ 105am kevin hollins pole #26706 repaired last night refer to wo #533497 - street light is out | High Pressure Sodium | 38.91077777000 | -77.03840283000
6/19/08 | 533306 | 0 | ANACOSTIA FWY | NE | 6/19/08 | 79490 | 7A159 | (Light out) |  | High Pressure Sodium | 38.88986353000 | -76.95869496000
6/19/08 | 533281 | 2 | MASSACHUSETTS AVE | NE | 6/19/08 | 60931 | 6U605 | (Light out) | 6-19-08 @ 330am tim richards repaired pole #60931 | High Pressure Sodium | 38.89741533000 | -77.00777006000
6/19/08 | 532699 | 0 | WASHINGTON CIR | NW | 6/19/08 | 28509 | 2M286 | (Light out) | 6-19-08 @ 1258am kevin hollins repaired pole #28509 ( reset tl photocell) | High Pressure Sodium | 38.90199338000 | -77.04975164000
6/18/08 | 533265 | 3610 | CAMDEN ST | SE |  | 74764DC | 7A078DC | (Light out) | 6-19-08 D Dixon NO problem found with light, home owner concerned about pole leaning (SEE WAYNE R) FRONT - wooden pole is leaning to the house due to limb that fell over | High Pressure Sodium | 38.85947257000 | -76.95586520000
6/18/08 | 533263 | 226 | RHODE ISLAND AVE | NW | 6/20/08 | 59994 | 5A186 | (Light out) | 6-20-08 @ 330am gary hicks repaired pole #59994 c/p 59995 opened wo #534065 FRONT - light out wood pole | Incandescent | 38.91452540000 | -77.01525438000
6/18/08 | 532614 | 0 | E ST | NW | 6/19/08 | 23334 | 2M356 | (Light out) | 6-19-08 @ 310am kevin hollins repaired pole #23334 ( when kevin arrived he found both 400 hps bulbs new - but went ahead and changed out bulbs) | High Pressure Sodium | 38.89621967000 | -77.02247784000
6/17/08 | 531883 | 580 | 23RD PL | NE | 6/18/08 | 74315 | 7E159 | (Light out) | 6-17-08 @ 1045pm leroy keys repaired pole #74315 | High Pressure Sodium | 38.89816568000 | -76.97316755000
6/17/08 | 531118 | 2300 | 24TH ST | NE | 6/17/08 | 74702 | 7E162 | (Light out) | 6-16-08 @ 1130pm tim richards repaired pole #74702 | High Pressure Sodium | 38.89805271000 | -76.97229886000
6/17/08 | 531117 | 580 | 23RD PL | NE | 6/17/08 | 74315 | 7E159 | (Light out) | 6-16-08 @ 1100pm tim richards repaired pole #74315 - reset photocell | High Pressure Sodium | 38.89816568000 | -76.97316755000
6/14/08 | 530817 | 1100 | 2ND ST | SE | 6/14/08 | 68135 | 6A409 | (Light out) | 6-14-08 @ 355am tim richards repaired pole #68135 - reattached loose neturial | High Pressure Sodium | 38.87682972000 | -77.00287771000
6/14/08 | 530762 | 100 | POTOMAC AVE | SE | 6/18/08 | 67759DC | 68462 | (Light out) | 6-18-08 D Smith/R Gray light working properly 6-14-08 @ 146am tim richards repaired pole #67759 - N/C underground hot wire is to short and there is no neturial | High Pressure Sodium | 38.87164315000 | -77.00642420000
6/14/08 | 530760 | 200 | I ST | SE | 6/14/08 | 67648 | 6A422 | (Light out) | 6-14-08 @ 1250am tim richards repaired pole #67648 | High Pressure Sodium | 38.87934724000 | -77.00236217000
6/14/08 | 530759 | 900 | 2ND ST | SW | 6/14/08 | 68129 | 6A416 | (Light out) | 6-14-08 @ 1255am tim richards repaired pole #68129 - rewired photocell | High Pressure Sodium | 38.87878241000 | -77.00287862000
6/14/08 | 530759 | 900 | 2ND ST | SW | 6/14/08 | 68129 | 68621 | (Light out) | 6-14-08 @ 1255am tim richards repaired pole #68129 - rewired photocell | High Pressure Sodium | 38.90623996000 | -77.01082515000
6/14/08 | 530757 | 900 | 2ND ST | SW | 6/14/08 | 68129 | 6A416 | (Light out) | 6-14-08 @ 1255am tim richards repaired pole #68129 - adjusted photocell | High Pressure Sodium | 38.87878241000 | -77.00287862000
6/14/08 | 530757 | 900 | 2ND ST | SW | 6/14/08 | 68129 | 68621 | (Light out) | 6-14-08 @ 1255am tim richards repaired pole #68129 - adjusted photocell | High Pressure Sodium | 38.90623996000 | -77.01082515000
6/13/08 | 530230 | 4601 | SOUTHERN AVE | SE | 6/14/08 | 75653 | 75653DC | (Light out) | 6-14-08 @ 502am leroy keys repaired pole #75653 | High Pressure Sodium | 38.87424204000 | -76.93342524000
6/13/08 | 530772 | 206 | RHODE ISLAND AVE | NW | 6/17/08 | 59996 | 5A188 | (Light out) | 6-17-08 @ 1230am gary hicks repaired pole #59996 C/P 59995 found okay 100- 400 RHODE ISLAND NW - Csller states metal pole lights needs repairing | Incandescent | 38.91473859000 | -77.01463730000
6/13/08 | 529953 | 1835 | WILTBERGER ST | NW | 6/13/08 | 29508 | 1M012 | (Light out) | 6-13-8 @ 120am kevin hollins repaired pole #29508 - reattached crown | High Pressure Sodium | 38.91528456000 | -77.02091849000
6/13/08 | 529455 | 504 | H ST | NE | 6/13/08 | 61725 | 6S218 | (Light out) | 6-13-08 P Harvin Installed 1 EE 6-13-08 @ 1230am tim richards repaired pole #61725 - ** needs (1) ear | High Pressure Sodium | 38.90030323000 | -76.99936233000
6/13/08 | 529454 | 0 | M ST | NW | 6/13/08 | 23728 | 2U535 | (Light out) | 6-13-08 @ 1230am kevin hollins repaired pole #23728 - reset tl photocell | High Pressure Sodium | 38.90574873000 | -77.04183268000
6/13/08 | 529453 | 0 | 12TH ST EXPY | SW | 6/13/08 | 28754 | 68648 | (Light out) | 6-13-08 @ 1225am kevin hollins repaired pole #28754- reset tl photocell c/p # 28728 open wo #529454 | High Pressure Sodium | 38.88580666000 | -77.02716048000
6/12/08 | 529198 | 1100 | 1ST ST | NW | 6/12/08 | 60858 | 6S272 | (Light out) | 5-12-08 @ 430am tim richards repaired pole #60858 | High Pressure Sodium | 38.90405924000 | -77.01223048000
6/12/08 | 529185 | 515 | H ST | NE | 6/12/08 | 61722 | 6S062 | (Light out) | 5-12-08 @ 430am tim richards repaired pole #61722 | High Pressure Sodium | 38.90011936000 | -76.99890875000
6/11/08 | 529138 | 1835 | WILTBERGER ST | NW | 6/13/08 | 29508 | 1M012 | (Light out) | 6-13-08 @ 115am kevin hollins repaired pole #29508 FRONT - STREET LIGHT IS OUT IT'S A METAL POLE | High Pressure Sodium | 38.91528456000 | -77.02091849000
6/11/08 | 528358 | 580 | 23RD PL | NE | 6/11/08 | 74315 | 7E159 | (Light out) | 6-11-08 @ 115am tim richards repaired pole #74315 | High Pressure Sodium | 38.89816568000 | -76.97316755000
6/11/08 | 528355 | 0 | 17TH ST | NE | 6/14/08 | 62974 | 6M774 | (Light out) | 6-11-08 @ 1255am tim richards repaired pole pole tag missing INSTALLED TAG#62974 | High Pressure Sodium | 38.89925729000 | -76.97942649000
6/10/08 | 527857 | 909 | U ST | NW | 6/11/08 | 13290 | 1G554 | (Light dim) | 6-10-08 @ 1135pm kevin hollins repaired pole #13290 | High Pressure Sodium | 38.91692297000 | -77.02444701000
6/10/08 | 527829 | 2811 | PENNSYLVANIA AVE | SE | 6/12/08 | 78569DC | 7E084DC | (Light out) | 6-10-08 @ 1130pm leroy keys repaired pole #78569dc | High Pressure Sodium | 38.87190486000 | -76.96697603000
6/10/08 | 527818 | 2915 | PENNSYLVANIA AVE | SE | 6/12/08 | 78568DC | 7E086DC | (Light out) | 6-12-08 @ 430am leroy keys pole #78568 previously repaired | High Pressure Sodium | 38.87173975000 | -76.96656845000
6/10/08 | 527682 | 0 | FERN PL | NW | 6/10/08 | 4D591DC | 4D891DC | (Light out) | 6-10-08 @ 118am roger warren repaired pole #4d591dc c/p 4d592dc found okay | Incandescent | 38.97836028000 | -77.02202042000
6/9/08 | 527055 | 0 | SOUTH DAKOTA AVE | NE | 6/11/08 | 57964 | 5M083 | (Light out) | 6-11-08 @ 322am gary hicks repaired pole #57964 | High Pressure Sodium | 38.92723868000 | -76.96712989000
6/7/08 | 526577 | 1711 | 18TH ST | NW | 6/7/08 | 26753 | 2M128 | (Light out) | 6-7-08 @ 1243am kevin holins repaired pole #26753 | High Pressure Sodium | 38.91307048000 | -77.04160463000
6/7/08 | 526347 | 0 | M ST | NW | 6/7/08 | 23728 | 2U535 | (Light out) | 6-67-08 @ 1230am kevin hollins repaired pole #23728 reset photocell t/l | High Pressure Sodium | 38.90574873000 | -77.04183268000
6/6/08 | 526285 | 624 | H ST | NE | 6/10/08 | 61866 | 6S206 | (Light out) | 6-9-08 @ 1100pm tim richards repaired pole #61866 6-09-08 M Craig there are no 400 hps power door in the warehouse 6-7-08 @ 1222am tim richards pole #61866 *needs 400 hs powerdoor | High Pressure Sodium | 38.90030032000 | -76.99736620000
6/6/08 | 526174 | 0 | M ST | NW | 6/6/08 | 23728 | 2U535 | (Light out) | 6-6-08 @ 122am kevin hollins repaired pole #23728 -reset t/l photocell | High Pressure Sodium | 38.90574873000 | -77.04183268000
6/5/08 | 526847 | 1529 | 17TH ST | NW | 6/9/08 | 26706 | 2M021 | (Light out) | 6-9-08 @ 1100pm kevin hollins pole #26706 light previously repaired STREET LIGHT - Street light on metal pole is out (directly in front of business) need repairing | High Pressure Sodium | 38.91077777000 | -77.03840283000
6/4/08 | 525096 | 1901 | 4TH ST | NW | 6/6/08 | 14104 | 15049 | (Light out) | 6-6-08 @ 1238am gary hicks repaired pole #14104 reset photocell c/p 14183 and 14040 found ok | High Pressure Sodium | 38.91602650000 | -77.01728653000
6/4/08 | 525021 | 4514 | 13TH ST | NW | 6/7/08 | 4K422 | 4U131 | (Light out) | 6-7-08 da duplicate ticket to wo # 525019 | High Pressure Sodium | 38.94571765000 | -77.02978404000
6/4/08 | 525019 | 4514 | 13TH ST | NW | 6/7/08 | 4K422 | 4U131 | (Light off/on) | 6-7-08 @ 1232am roger warren repaired pole #4k422 c/p 4k423 and 4k421 found ok | High Pressure Sodium | 38.94571765000 | -77.02978404000
6/3/08 | 524285 | 5335 | B ST | SE | 6/4/08 | 75564 | 75564DC | (Light out) | 6-4-08 @ 1202am tim richards repaired pole #75564 | High Pressure Sodium | 38.88622800000 | -76.92459483000
6/3/08 | 524258 | 4651 | BENNING RD | SE | 6/7/08 | 75822 | 75822DC | (Light off/on) | 6-7-08 @ 1229am leroy keys repaired pole #75822 | High Pressure Sodium | 38.87611644000 | -76.93130301000
6/3/08 | 524844 | 0 | 23RD ST | NW | 6/5/08 | 28318 | 2M274 | (Light out) | 6-05-08 M Brewer Found ok FRONT - metal streetlight is out | High Pressure Sodium | 38.89313901000 | -77.05025238000
6/3/08 | 523535 | 801 | D ST | NW | 6/3/08 | 60087 | 2M371 | (Light out) | 6-3-08 @ 1237am tim richards repaired pole #60087 | High Pressure Sodium | 38.89493542000 | -77.02306697000
6/3/08 | 523534 | 801 | D ST | NW | 6/3/08 | 60176 | 2M330 | (Light out) | 6-3-08 @ 1225am tim richards repaired pole #60176 | High Pressure Sodium | 38.89474698000 | -77.02312090000
6/2/08 | 524097 | 610 | H ST | NW | 6/4/08 | 22559 | 6M700 | (Light out) | 6-3-08 @ 1125pm kevin hollins repaired pole #22559 THE STREETLIGHT IS IN FRONT OF 618 H STREET, N.W. - | High Pressure Sodium | 38.89973402000 | -77.02073448000
6/2/08 | 524110 | 0 | M ST | NW | 6/4/08 | 23728 | 2U535 | (Light out) | 6-4-08 @ 1215am kevin hollins repaired pole #23728 - reset photocell THE STREETLIGHT IS AT THE NORTHWEST CORNER OF 18TH AND M STREETS, N.W. - | High Pressure Sodium | 38.90574873000 | -77.04183268000
6/2/08 | 523370 | 919 | T ST | NW | 6/3/08 | 13451 | 1L370 | (Light off/on) | 6-3-08 @ 120am tim richards repaired pole #13451 | High Pressure Sodium | 38.91563328000 | -77.02474424000
5/30/08 | 523263 | 0 | E ST | NW | 6/3/08 | 23328 | 2M334 | (Light out) | 6-3-08 @ 1245am tim richards repaired pole # 23328 IN FRONT OF THE WOOLLEY MAMMOTH THEATER - 7TH | High Pressure Sodium | 38.89622093000 | -77.02027487000
5/30/08 | 522798 | 0 | GRANT ST | NE | 6/4/08 | 72339DC | 7A216 | (Light off/on) |  | High Pressure Sodium | 38.89843429000 | -76.93131145000
5/30/08 | 522795 | 0 | GRANT ST | NE | 6/5/08 | 72339DC | 7A216 | (Light out) | 6-05-08 M Craig Found ok Previously serviced | High Pressure Sodium | 38.89843429000 | -76.93131145000
5/30/08 | 522792 | 4922 | NANNIE HELEN BURROUGHS AVE | NE | 6/4/08 | 71281DC | 7A214 | (Light out) | 6-4-08 @ 1212am leroy keys repaired pole #71281dc | High Pressure Sodium | 38.89848333000 | -76.93033462000
5/30/08 | 522771 | 0 | EAST CAPITOL ST | NE | 6/5/08 | 74205DC | 7A063DC | (Light out) | 6-05-08 P Harvin Installed 250w hps lamp | High Pressure Sodium | 38.89216210000 | -76.94254713000
5/30/08 | 522765 | 0 | KENILWORTH AVE | NE | 6/6/08 | 70311 | 7M067 | (Light out) | 6-06-08 R Gray/D Smith Installed 160ft #6 triplex, made 4 splices 2 taps light working 6-5-08 @ 1110pm chris ashton pole # 70311 N/C to overhead C/P 70310 wo #522764 | High Pressure Sodium | 38.90629475000 | -76.93975849000
5/30/08 | 522764 | 0 | KENILWORTH AVE | NE | 6/6/08 | 70310 | 7M065 | (Light out) | 6-06-08 R Gray/D Smith made splices and light working 6-5-08 @ 1105pm chris ashton pole #70310 N/C to overhead -- replaced t base door C/P 70309 wo #522763 and 70308 found okay | High Pressure Sodium | 38.90683547000 | -76.93927718000
5/30/08 | 522763 | 0 | KENILWORTH AVE | NE | 6/6/08 | 70309 | 7M064 | (Light out) | 6-06-08 R Gray/D Smith Installed 160ft #6 triplex, made 4 splices 2 taps 6-5-08 @ 1100pm chris ashton pole #70309dc N/C to overhead C/P 70308dc found okay | High Pressure Sodium | 38.90704511000 | -76.93909072000
5/30/08 | 522762 | 0 | KENILWORTH AVE | NE | 6/5/08 | 70306 | 7M058 | (Light out) | 6-5-08 chris ashton repaired pole #70306 C/P 70305 and 70304 found okay | High Pressure Sodium | 38.90838237000 | -76.93790987000
5/29/08 | 522661 | 1529 | 17TH ST | NW | 5/31/08 | 26706 | 2M021 | (Light out) | 5-31-08 @ 224am kevin hollins pole #26706 previously repaired refer to wo #510619 EAST SIDE OF THE STREET - | High Pressure Sodium | 38.91077777000 | -77.03840283000
5/29/08 | 522175 | 1201 | BRENTWOOD PKY | NE | 6/14/08 | 56830 | 5M058 | (Light out) | 5-29-08 R Gray/Kates removed temp wire & plastic duct over the outer bank, disabled power new wire is up power back on (no pole#) TAG FOUND OK | High Pressure Sodium | 38.91354293000 | -76.99082318000
5/29/08 | 522035 | 700 | MICHIGAN AVE | NE | 5/30/08 | 53648DC | 5U716 | (Light out) | 5-30-08 @ 323am gary hicks repaired pole #53648dc | High Pressure Sodium | 38.93266695000 | -76.99717259000
5/29/08 | 522030 | 0 | 1ST ST | NE | 5/30/08 | 61248 | 6A282 | (Light out) | 5-30-08 DA duplicate ticket to wo # 404559 no hansen # | High Pressure Sodium | 38.90791176000 | -77.00580646000
5/29/08 | 522016 | 0 | NEW YORK AVE | NE | 6/4/08 | 56793 | 5M072 | (Light out) | 6-4-08 W KAtes/UGO MAde splices in M/H & checked all lights found ok, had to pump two M/H's 6-2-08 @ 1140pm gary hicks pole #56793 N/C underground | High Pressure Sodium | 38.91387856000 | -76.99078019000
5/29/08 | 522015 | 0 | NEW YORK AVE | NE | 6/4/08 | 56794 | 5M069 | (Light out) | 6-4-08 W KAtes/UGO MAde splices in M/H & checked all lights found ok, had to pump two M/H's 6-2-08 @ 1130pm gary hicks pole #56794 N/C underground | High Pressure Sodium | 38.91411047000 | -76.99006934000
5/29/08 | 522014 | 0 | NEW YORK AVE | NE | 6/4/08 | 56795 | 5M066 | (Light out) | 6-4-08 W KAtes/UGO MAde splices in M/H & checked all lights found ok, had to pump two M/H's 6-2-08 @ 1125pm gary hicks pole #56795 N/C underground | High Pressure Sodium | 38.91430291000 | -76.98938427000
5/29/08 | 522006 | 100 | NEW YORK AVE | NE | 6/3/08 | 56753 | 5M130 | (Light out) | Refer to WO#372321 Refered to Ddot- railroad lines to close to fixture. unable to fix problem because of high voltage lines. | High Pressure Sodium | 38.90888813000 | -77.00500782000
5/29/08 | 521998 | 1400 | FLORIDA AVE | NE | 5/29/08 | 54409 | 5M287 | (Light out) | 5-29-08 @ 1135pm gary hicks repaired pole #54409 | High Pressure Sodium | 38.90038000000 | -76.98467707000
5/29/08 | 521893 | 0 | 9TH ST | NW | 5/29/08 | 22988 | 2G982 | (Light out) | 5-29-08 @ 115am kevin hollins repaired pole #22988 | High Pressure Sodium | 38.90042206000 | -77.02407679000
5/28/08 | 521281 | 903 | 4TH ST | NW | 6/9/08 | 60452 | 6S492 | (Light out) | 6/9/08 O Taylor installed cable from MH TO MH made in both , job competed | High Pressure Sodium | 38.90212698000 | -77.01625073000
5/28/08 | 521275 | 206 | D ST | SE | 5/31/08 | 65644 | 65618 | (Light out) | 5-31-08 @ 421am tim richards repaired pole # 65644 | High Pressure Sodium | 38.88502510000 | -77.00336540000
5/28/08 | 521918 | 0 | H ST | NE | 5/30/08 | 62347 | 6S110 | (Light out) | 5-30-08 @ 319am tim richards repaired pole #62347- reset photocell H STREET SE CORNER NEXT TO AUTOZONE - | High Pressure Sodium | 38.90011694000 | -76.99007929000
5/28/08 | 521255 | 0 | I ST | NW | 5/29/08 | 22487 | 2G985 | (Light out) | 5-29-08 @ 1250am kevin hollins repaired pole #22487 - reset photocell | High Pressure Sodium | 38.90081220000 | -77.02379981000
5/28/08 | 521251 | 0 | 9TH ST | NW | 5/29/08 | 25437 | 2L558 | (Light out) | 5-29-08 @ 1215am kevin hollins repaired pole #25437 | High Pressure Sodium | 38.90380790000 | -77.02408338000
5/28/08 | 521248 | 2307 | WASHINGTON CIR | NW | 5/29/08 | 24654 | 2G670 | (Light out) | 5-29-08 @ 235am kevin hollins repaired pole #24654 - reset T/L photocell | High Pressure Sodium | 38.90298616000 | -77.05064992000
5/28/08 | 521231 | 2311 | 18TH ST | NW | 5/29/08 | 11409 | 1G496 | (Light out) | 5-29-08 @ 318am gary hicks repaired pole #11409 | High Pressure Sodium | 38.92009844000 | -77.04170982000
5/28/08 | 521219 | 0 | H ST | NW | 5/29/08 | 22622 | 2G972 | (Light out) | 5-29-08 kevin hollins pole #22622 was completed last night | High Pressure Sodium | 38.89990526000 | -77.02482158000
5/28/08 | 521160 | 800 | 4TH ST | NW | 5/31/08 | 60448 | 6S459 | (Light out) | 5-31-08 @ 1222am tim richards repaird pole #60448 | High Pressure Sodium | 38.90032749000 | -77.01608012000
5/28/08 | 521158 | 1404 | H ST | NE | 5/31/08 | 62326 | 6S139 | (Light out) | 5-31-08 @ 135am tim richards repaired pole #62326 | High Pressure Sodium | 38.90029477000 | -76.98535817000
5/27/08 | 521074 | 2407 | 18TH ST | NW | 5/29/08 | 11533 | 1G491 | (Light out) | 5-29-08 @ 310am gary hicks repaired pole #11533 FRONT - street light out on a metal pole | High Pressure Sodium | 38.92063969000 | -77.04213470000
5/27/08 | 521090 | 2311 | 18TH ST | NW | 5/29/08 | 11409 | 1G496 | (Light out) | 5-29-08 @ 320am gary hicks repaired pole #114909 FRONT - street light out on a metal pole | High Pressure Sodium | 38.92009844000 | -77.04170982000
5/27/08 | 521089 | 2335 | 18TH ST | NW | 5/29/08 | 10259 | 1G494 | (Light out) | 5-29-08 @ 325am gary hicks repaired pole #10259 FRONT - street light is on and off on a metal pole | High Pressure Sodium | 38.92037631000 | -77.04180732000
5/23/08 | 520124 | 801 | P ST | NW | 5/28/08 | 25808 | 6U460 | (Light out) | 5-28-08 @ 155am kevin hollins repaired pole #25808- THE SIGNAL LIGHT FIXTURE FAIL AND CITIZEN MOVED IT TO THE SIDEWALK. | High Pressure Sodium | 38.90960163000 | -77.02357636000
5/22/08 | 518952 | 3233 | PENNSYLVANIA AVE | SE | 5/28/08 | 78547DC | 7E110 | (Light off/on) | 5-28-08 @ 350am chris ashton repaired pole #78547dc | High Pressure Sodium | 38.86864144000 | -76.95900959000
5/22/08 | 519467 | 2010 | 48TH ST | NW | 5/24/08 | 35370DC | 3E030 | (Light out) | 5-24-08 @ 155an chris ashton repaired pole #35370 FRONT ACROSS THE STREET - Streetlight burnt out | Incandescent | 38.91704622000 | -77.09453331000
5/22/08 | 518315 | 3102 | CLEVELAND AVE | NW | 5/22/08 | 37361 | 37561 | (Light out) | 5-22-08 @ 1205am chris ashton repaired pole #37361 C/P 37362 and 37360 found okay | High Pressure Sodium | 38.92574190000 | -77.06111143000
5/21/08 | 518304 | 0 | L ST | SE | 5/22/08 | 67701 | 6A438 | (Light out) | 5-22-08 @ 331am tim richards repaired pole #67701 - secured globe | High Pressure Sodium | 38.87758258000 | -77.00088038000
5/20/08 | 517713 | 0 | 12TH ST | NE | 5/22/08 | 54576 | 5C022 | (Light out) | 5-22-08 @ 1215am gary hicks repaired pole #54756 | High Pressure Sodium | 38.93063767000 | -76.99092926000
5/20/08 | 518218 | 719 | 15TH ST | SE | 5/22/08 | 64363DC | 6A053 | (Light out) | 5-22-08 @ 442am tim richards repaired pole #64363dc ALLEY - two alleylights one on a metal pole and one on a wooden pole is out in the alley, please repair. | Incandescent | 38.88032991000 | -76.98412324000
5/20/08 | 517664 | 0 | 9TH ST | NE | 5/20/08 | 52561 | 5M036 | (Light out) | 5-20-08 @ 410am gary hicks repaired pole #52561 | High Pressure Sodium | 38.91169939000 | -76.99207526000
5/20/08 | 517600 | 206 | D ST | SE | 5/20/08 | 65644 | 65618 | (Light out) | 5-20-08 @ 140am tim richards repaired pole #65644 reset photocel | High Pressure Sodium | 38.88502510000 | -77.00336540000
5/19/08 | 516871 | 0 | 14TH ST | NW | 5/22/08 | 12073 | 1G564 | (Light out) | - 5-22-08 W Kates/UGO Installed 150ft f #10 cable from base to M/H and made splices 5-20-08 @ 1203am gary hicks pole #12073 N/C underground 5-19-08 Pole# 12073 Why did construction site kill power? | High Pressure Sodium | 38.92089953000 | -77.03174747000
5/18/08 | 516821 | 0 | NEW YORK AVE | NE | 2/6/12 | 56793 | 5M072 | (No current) | 5/22/08 Outage due to mudslide due to repair/reconstruction of rail system adjacent to light infrastructure , refer to DDot. | High Pressure Sodium | 38.91387856000 | -76.99078019000
5/18/08 | 516820 | 0 | NEW YORK AVE | NE | 2/6/12 | 56794 | 5M069 | (No current) | 5/22/08 Outage due to mudslide due to repair/reconstruction of rail system adjacent to light infrastructure , refer to DDot. | High Pressure Sodium | 38.91411047000 | -76.99006934000
5/18/08 | 516819 | 0 | NEW YORK AVE | NE | 2/6/12 | 56795 | 5M066 | (No current) | 5/22/08 Outage due to mudslide due to repair/reconstruction of rail system adjacent to light infrastructure , refer to DDot. | High Pressure Sodium | 38.91430291000 | -76.98938427000
5/18/08 | 516815 | 0 | NEW YORK AVE | NE | 2/6/12 | 56832 | 5M053 | (No current) | 5/22/08 Outage due to mudslide due to repair/reconstruction of rail system adjacent to light infrastructure , refer to DDot. | High Pressure Sodium | 38.91324438000 | -76.99169504000
5/18/08 | 516810 | 0 | NEW YORK AVE | NE | 2/6/12 | 56776 | 5M016 | (No current) | 5/22/08 Outage due to mudslide due to repair/reconstruction of rail system adjacent to light infrastructure , refer to DDot. | High Pressure Sodium | 38.91315068000 | -76.99287151000
5/18/08 | 516799 | 0 | 9TH ST | NE | 2/6/12 | 56779 | 5M079 | (No current) | 5/22/08 Outage due to mudslide due to repair/reconstruction of rail system adjacent to light infrastructure , refer to DDot. | High Pressure Sodium | 38.91333345000 | -76.99224593000
5/18/08 | 516798 | 0 | 9TH ST | NE | 5/18/08 | 56779 | 5M079 | (No current) | R Rapolla, 5-18-2008, Duplicate to 516799 | High Pressure Sodium | 38.91333345000 | -76.99224593000
5/16/08 | 516206 | 0 | NEW YORK AVE | NE | 5/19/08 | 50005 | 5A039 | (Light out) | pole #50005 -- NEEDS BIG BOOM TRUCK | High Pressure Sodium | 38.91734425000 | -76.96859446000
5/16/08 | 516205 | 0 | NEW YORK AVE | NE | 5/17/08 | 50010 | 5A044 | (Light out) | 5-17-08 tom osvatics repaired pole #50010 pole #50010 -- NEEDS BIG BOOM TRUCK | High Pressure Sodium | 38.91713437000 | -76.96502016000
5/16/08 | 516204 | 0 | NEW YORK AVE | NE | 5/17/08 | 50009 | 5A043 | (Light out) | 5-17-08 tom osvatics repaired pole #50009 pole #50009 -- NEEDS BIG BOOM TRUCK | High Pressure Sodium | 38.91719217000 | -76.96575011000
5/16/08 | 516203 | 0 | NEW YORK AVE | NE | 5/19/08 | 50006 | 5A040 | (Light out) | pole #50006-- NEEDS BIG BOOM TRUCK | High Pressure Sodium | 38.91731218000 | -76.96789154000
5/16/08 | 516202 | 0 | NEW YORK AVE | NE | 5/17/08 | 50013 | 5A048 | (Light out) | 5-17-08 tom osvatics repaired pole #50013 pole #50013 -- NEEDS BIG BOOM TRUCK | High Pressure Sodium | 38.91696428000 | -76.96182720000
5/16/08 | 516197 | 3200 | P ST | NW | 5/20/08 | 21015 | 2G140 | (Light out) | 5-20-08 @ 301am kevin hollins pole #21015 previously repaired | High Pressure Sodium | 38.90884750000 | -77.06599836000
5/14/08 | 514982 | 2403 | BENNING RD | NE | 5/14/08 | 59616DC | 5M310 | (Light out) | 5-14-08 @ 1100pm gary hicks repaired pole #59616dc 5-14-08 Metal Pole# 59616dc pole is marked w/red tape | High Pressure Sodium | 38.89825539000 | -76.97195297000
5/14/08 | 514979 | 1770 | BENNING RD | NE | 5/15/08 | 63615 | 6M778 | (Light out) | 5-15-08 @ 458am tim richards repaired pole #63615 5-14-08 Metal Pole# 63615 pole is marked w/red tape 1st pole west of 18th St | High Pressure Sodium | 38.89907267000 | -76.97811088000
5/14/08 | 514978 | 0 | BENNING RD | NE | 2/17/09 | 59523 | 5M302 | (Light out) | 5/29/08 O. Taylor pole located in construction zone unable DDot. | High Pressure Sodium | 38.89781249000 | -76.96932119000
5/14/08 | 514935 | 0 | H ST | NE | 5/14/08 | 62347 | 6S110 | (Light out) | 5-14-08 @ 311am tim richards repaired pole #62347 | High Pressure Sodium | 38.90011694000 | -76.99007929000
5/13/08 | 514236 | 901 | 9TH ST | NW | 5/14/08 | 22987 | 2G988 | (Light out) | 5-13-08 @ 1150pm kevin hollins repaired pole #22987 | High Pressure Sodium | 38.90092176000 | -77.02415354000
5/13/08 | 513715 | 1005 | 1ST ST | NE | 5/19/08 | 61231 | 6S439 | (Light out) | 5-13-08 @ 1204am tim richards N/C underground no id tag between poles 61232 and 61230 Installed tag#61231 | High Pressure Sodium | 38.90311217000 | -77.00596908000
5/13/08 | 513714 | 0 | 9TH ST | NW | 5/13/08 | 25437 | 2L558 | (Light out) | 5-12-08 @ 1145pm kevin hollins repaired pole #25437 | High Pressure Sodium | 38.90380790000 | -77.02408338000
5/12/08 | 514189 | 0 | 14TH ST | NW | 5/14/08 | 12073 | 1G564 | (Light out) | 5-14-08 @ 1203am DA duplicate ticket to wo #471572 na hansen # ON THE CORNER - | High Pressure Sodium | 38.92089953000 | -77.03174747000
5/12/08 | 514196 | 629 | H ST | NW | 5/21/08 | 22634 | 6M695 | (Light out) | 5/21/08 H. Lancaster re-spliced cable in pole base & installed 250 hps kit, job completed K. greenfield | High Pressure Sodium | 38.89990420000 | -77.02118022000
5/10/08 | 513512 | 0 | KENILWORTH AVE | NE | 5/10/08 | 70306 | 7M058 | (Light out) | 5-10-08 leroy keys repaired pole #70306 | High Pressure Sodium | 38.90838237000 | -76.93790987000
5/10/08 | 513504 | 3200 | P ST | NW | 5/10/08 | 21015 | 2G140 | (Light out) | 5-10-08 @305am kevin hollins repaired pole #21015 | High Pressure Sodium | 38.90884750000 | -77.06599836000
5/9/08 | 513480 | 131 | M ST | NE | 5/12/08 | 62268 | 6S346 | (Light out) | 5-12-08 @1109pm tim richards pole #62268 is getting ready to be removed FRONT - one metal pole light base is brocken and exposed wire...please repair asap | High Pressure Sodium | 38.90570457000 | -77.00451927000
5/9/08 | 513060 | 0 | H ST | NE |  | 62345 | 6S103 | (Light out) | 5-10-08 @359 am tim richards repaired pole #62345 **needs new base 5-09-08 Pole# 62345 J CHEEKS 5/14/08 TRAFFIC POLE | High Pressure Sodium | 38.90012051000 | -76.99138683000
5/9/08 | 513058 | 0 | H ST | NE | 3/23/09 | 62347 | 6S110 | (Light out) | 5-13-08 M Craig Traffic pole DDOT REFER 5-10-08 @415 am tim richards repaired pole #62347 **needs (4) ears 5-09-08 Pole# 62347 | High Pressure Sodium | 38.90011694000 | -76.99007929000
5/9/08 | 513057 | 961 | H ST | NE | 5/10/08 | 62342 | 6S094 | (Light off/on) | 5-10-08 @345 am tim richards repaired pole #62342 secured wires @ fixture 5-09-08 Pole# 62342 | High Pressure Sodium | 38.90011933000 | -76.99310039000
5/8/08 | 512586 | 600 | 2ND ST | NE | 2/6/12 | 61306 | 6S276 | (No current) | 6-02-08 W Kates/UGO New poles being instlled by outside contractor REFER to DDOT | High Pressure Sodium | 38.89832767000 | -77.00344709000
5/8/08 | 512580 | 911 | 2ND ST | NE | 5/13/08 | 61296 | 6S298 | (No current) | 5/13/08 H Lancaster made3 nsplices in pole base installed lamp & photocell.completed K. Greenfield | High Pressure Sodium | 38.90176798000 | -77.00363405000
5/8/08 | 512579 | 921 | 2ND ST | NE | 2/6/12 | 61294 | 6S302 | (No current) | IPMA PROJECT 5/13/08 H. Lancaster new being installed by out side contractor, old poles terminated. refer to DDot | High Pressure Sodium | 38.90239026000 | -77.00360443000
5/8/08 | 512512 | 601 | D ST | NW | 5/10/08 | 60094 | 6S600 | (Light out) | 5-10-08 @ 1230am kevin hollins flash tested pole #60094 found okay | High Pressure Sodium | 38.89486033000 | -77.02070899000
5/8/08 | 512489 | 0 | BENNING RD | NE | 5/10/08 | 59597 | 5M275 | (Light out) | 5-10-08 @ 1252am gary hicks repaired pole #59597 and secured t base door c/p 54496 and 54407 found okay | High Pressure Sodium | 38.90028965000 | -76.98347853000
5/8/08 | 512421 | 0 | M ST | NW | 5/8/08 | 23728 | 2U535 | (Light out) | 5-8-08 kevin hollins repaired pole #23728 reset photocell | High Pressure Sodium | 38.90574873000 | -77.04183268000
5/8/08 | 511954 | 2730 | WISCONSIN AVE | NW | 5/8/08 | 30177 | 3G020 | (Light out) | 5-8-08 chris ashton repaired pole #30177 | High Pressure Sodium | 38.92608314000 | -77.07307216000
5/7/08 | 511933 | 0 | M ST | NW | 5/15/08 | 23739 | 2G718 | (Light out) | 5/15/08 H. Lancaster replaced TL photocell job complete. K. Greenfield | High Pressure Sodium | 38.90513126000 | -77.04778068000
5/7/08 | 511908 | 1101 | L ST | NW | 5/7/08 | 25942 | 2M218 | (Light off/on) | 5-7-08 kevin hollins repaired pole #25942 reset t/l photocell | High Pressure Sodium | 38.90408908000 | -77.02717553000
5/7/08 | 511903 | 1451 | MARYLAND AVE | NE | 5/7/08 | 62358 | 6M720 | (Light out) | 5-7-08 gary hicks repaired pole #62358 | High Pressure Sodium | 38.90007909000 | -76.98391252000
5/6/08 | 511309 | 3700 | MILITARY RD | NW | 5/7/08 | 32716DC | 3E023 | (Light out) | 5-7-08 D Smith/R Gray Made splice on secondary, lights working properly 5-7-08 chris ashton repaired pole #32716dc no current to overhead | High Pressure Sodium | 38.96062593000 | -77.07197706000
5/6/08 | 511269 | 1100 | 11TH ST | SE | 5/10/08 | 67614 | 6L993 | (Light out) | 5-10-08 @1240am tim richards repaired pole #67614 and secured pole tag @ 14ft | High Pressure Sodium | 38.87689854000 | -76.99165831000
5/6/08 | 511177 | 1300 | 1ST ST | NE | 5/19/08 | 61247 | 6A279 | (Light out) | 5-6-08 tim richards repaired pole adjusted photo cell no id tag INSTALLED TAG NUBER #61247 | High Pressure Sodium | 38.90758804000 | -77.00596758000
5/6/08 | 510619 | 1529 | 17TH ST | NW | 5/6/08 | 26706 | 2M021 | (Light out) | 5-6-08 kevin hollins pole #26706 reset photocell | High Pressure Sodium | 38.91077777000 | -77.03840283000
5/6/08 | 510618 | 301 | K ST | SE | 5/8/08 | 67660 | 6A449 | (Light out) | 5-08-08 M Craig Installed base door 5-6-08 tim richards repaired pole #67660 secured pole tag @14ft **needs t base door | High Pressure Sodium | 38.87835619000 | -77.00175680000
5/5/08 | 511203 | 633 | D ST | NW | 5/7/08 | 60175 | 6S602 | (Light out) | 5-07-08 N Woodalnd REplaced 150w hps lamp, NWP FRONT - Metal pole Caller states that the street light in from of this location stays on all day. | High Pressure Sodium | 38.89474457000 | -77.02113373000
5/5/08 | 510595 | 0 | E ST | NW | 5/7/08 | 23334 | 2M356 | (Light out) | 5-7-08 kevin hollins repaired pole #23334 | High Pressure Sodium | 38.89621967000 | -77.02247784000
5/5/08 | 511223 | 457 | MASSACHUSETTS AVE | NW | 5/19/08 | 60481 | 6A195 | (Light out) | 5-9-08 @ 1132pm tim richards - new poles this one has a new base but no pole yet STREET - CALLER REPORTING THAT THERE IS A STREETLIGHT THAT IS KNOCKED DOWN POLE TAGS FOUND OK RIGHT BEHIND THIS ADDRESS. THE STREETLIGHT IS ON A MANTAL POLE.THE REIS | High Pressure Sodium | 38.90073307000 | -77.01753805000
5/5/08 | 510574 | 4620 | EASY PL | SE | 5/8/08 | 75825 | 75825DC | (Light off/on) | 5-8-08 leroy keys pole #75825dc 189 inc found okay | Incandescent | 38.87603739000 | -76.93290309000
5/5/08 | 510562 | 0 | 13TH ST | NW | 5/6/08 | 4K425 | 4U138 | (Light out) | 5-6-08 roger warren repaired pole #4k425 | High Pressure Sodium | 38.94497938000 | -77.02978632000
5/5/08 | 510536 | 5314 | B ST | SE | 5/28/08 | 75565 | 75565DC | (Light out) | 5-08-08 R Gray/D Smith made taps on secondary light working properly 5-8-08 leroy keys - No Current to overhead 5-05-08 Pole # ( NO POLE #) 5-27-08 D.Webb----Found already tagged | High Pressure Sodium | 38.88626314000 | -76.92486984000
5/2/08 | 509696 | 2407 | 18TH ST | NW | 5/3/08 | 11533 | 1G491 | (Light out) | 5-3-08 chris ashton repaired pole #11533 | High Pressure Sodium | 38.92063969000 | -77.04213470000
5/2/08 | 509693 | 0 | W ST | NW | 5/3/08 | 11808 | 1G576 | (Light off/on) | 5-3-08 gary hicks repaired pole #11808 c/p 11807, 12063, 11806 found ok | High Pressure Sodium | 38.91938866000 | -77.03020579000
5/2/08 | 509681 | 0 | HIATT PL | NW | 5/12/08 | 13017 | 15047 | (Light out) | 5-08-08 UGO/W Kates Made splice in M/H pole nees tag 5-06-08 O Taylor REFER to Construction line & load in same pipe also, need tag 5-3-08 gary hicks pole #13017 N/C underground refer to fault crew | High Pressure Sodium | 38.92918664000 | -77.03463049000
5/2/08 | 509646 | 504 | K ST | NW | 5/2/08 | 60461 | 6A101 | (Light out) | 5-2-08 tim richards repaired pole #60461 adjusted p/c | High Pressure Sodium | 38.90260703000 | -77.01950617000
5/2/08 | 509634 | 900 | 2ND ST | SW | 5/22/08 | 68129 | 6A416 | (Light out) | 5-2-08 tim richards no id tag N/C undergrounG New GPS AND TAG#68129 | High Pressure Sodium | 38.87878241000 | -77.00287862000
5/2/08 | 509634 | 900 | 2ND ST | SW | 5/22/08 | 68129 | 68621 | (Light out) | 5-2-08 tim richards no id tag N/C undergrounG New GPS AND TAG#68129 | High Pressure Sodium | 38.90623996000 | -77.01082515000
5/2/08 | 509553 | 0 | M ST | NW | 5/2/08 | 23728 | 2U535 | (Light out) | 5-2-08 kevin hollins repaired pole #23728 reset photocell | High Pressure Sodium | 38.90574873000 | -77.04183268000
5/1/08 | 509574 | 900 | 3RD ST | SW | 5/6/08 | 68144 | 6A461 | (Light out) | 6-5-08 tim richards secured wires and repaired pole #68144 STREET LIGHT - At the corner of 3rd and K Street, S.E. street light on metal pole need replaceing. | High Pressure Sodium | 38.87851901000 | -77.00211175000
4/30/08 | 508930 | 775 | H ST | NE | 5/2/08 | 61991 | 6S197 | (Light out) | 5-2-08 tim richards rpeiared pole #61991 FRONT - caller is requesting repair for a streetlight that is very dim//metal pole | High Pressure Sodium | 38.90030060000 | -76.99586046000
4/30/08 | 508288 | 801 | D ST | NW | 4/30/08 | 60087 | 2M371 | (Light out) | 4-30-08 tim richards repaired pole #60087 | High Pressure Sodium | 38.89493542000 | -77.02306697000
4/29/08 | 507766 | 900 | 7TH ST | NW | 4/30/08 | 22462 | 6A084 | (Light out) | 4-30-08 kevin hollins repaired pole #22462 c/ pole 22463 - needs ears open wo 508403 | High Pressure Sodium | 38.90225041000 | -77.02177737000
4/29/08 | 507765 | 509 | 7TH ST | NW | 5/9/08 | 22431 | 6M628 | (Light out) | 5-1-08 kevin hollins repaired pole reset t/l photocell no id tag 5-8-08 S. Manning----pole id found ok | High Pressure Sodium | 38.89648966000 | -77.02200839000
4/29/08 | 507467 | 1101 | L ST | NW | 4/30/08 | 25942 | 2M218 | (Light out) | 4-30-08 kevin hollins pole #25942 previously repaired refer to wo #499161 | High Pressure Sodium | 38.90408908000 | -77.02717553000
4/29/08 | 507449 | 408 | RHODE ISLAND AVE | NW | 4/29/08 | 59989 | 5A181 | (Light out) | 4-29-08 gary hicks repaired pole #59989 needs t base repaired JORDAIN LEWIS 4/09/08 | High Pressure Sodium | 38.91392931000 | -77.01700898000
4/29/08 | 508302 | 2222 | WISCONSIN AVE | NW | 5/1/08 | 30162 | 3G082 | (Light out) | 4-30-08 chris ashton repaired pole #30162 c/ poles 30161 and 30152 found okay 3600 W PLACE NW, WASHINGTON, DC THE STREET LIGHT IS AT THE ENTRANCE OF THE WISCONSIN BUSINESS PARK (CONDOS). THE BRIGHTER THE BETTER. THANKS. - HALL **SRCB** IS THE POLE | High Pressure Sodium | 38.91993778000 | -77.07113468000
4/28/08 | 506960 | 0 | 9TH ST | NW | 4/29/08 | 25437 | 2L558 | (Light out) | 4-29-08 kevin hollins pole #25437 found okay | High Pressure Sodium | 38.90380790000 | -77.02408338000
4/28/08 | 506959 | 1101 | L ST | NW | 4/29/08 | 25942 | 2M218 | (Light out) | 4-29-08 kevin hollins pole #25942 found okay | High Pressure Sodium | 38.90408908000 | -77.02717553000
4/28/08 | 507421 | 388 | H ST | NE | 4/30/08 | 61522 | 6S224 | (Light out) | 4-30-08 tim richards repaired pole #61522 FRONT - Caller states flashing lights needs repairing | High Pressure Sodium | 38.90030233000 | -77.00072209000
4/28/08 | 506920 | 600 | S ST | NW | 5/6/08 | 14129 | 1G581 | (Light out) | 5-06-08 O Taylor Found ok (SEE OT) 5/1/08 light found ok | High Pressure Sodium | 38.91414861000 | -77.02137785000
4/26/08 | 506774 | 1421 | 34TH ST | NW | 4/26/08 | 21073 | 2G189 | (Light out) | 4-26-08 kevin hollins repaired pole #21073 | High Pressure Sodium | 38.90848178000 | -77.06790108000
4/26/08 | 506729 | 0 | M ST | NW | 4/26/08 | 23728 | 2U535 | (Light out) | 4-26-08 kevin hollins repaired pole #23728 | High Pressure Sodium | 38.90574873000 | -77.04183268000
4/25/08 | 506743 | 3300 | SHERMAN AVE | NW | 4/29/08 | 12896 | 1L282 | (Light out) | 4-29-08 orger warren repaired pole #12896 c/p #12897 and 12895 ok STREET LIGHT OUT - Street Light on metal pole in front of an apartment building need replacing | High Pressure Sodium | 38.93114546000 | -77.02668665000
4/25/08 | 506222 | 4601 | SOUTHERN AVE | SE | 5/5/08 | 75653 | 75653DC | (Light out) | 4-26-08 leroy keys repaired pole #75653 checked pole 76562 found ok | High Pressure Sodium | 38.87424204000 | -76.93342524000
4/25/08 | 506218 | 0 | EAST CAPITOL ST | NE | 4/30/08 | 63629 | 6M837 | (Light out) | 4-3008 tim richards pole #63629 did burn test found okay | High Pressure Sodium | 38.88956256000 | -76.97418443000
4/25/08 | 506757 | 0 | 12TH ST | NW | 4/30/08 | 12929 | 1G535 | (Light out) | 4-30-08 chris ashton repaired pole #12929 c/poles 12930 and 12928 found okay NW CORNER. ON THE SIDE OF ISLANDER RESTAURANT - metal pole ...light out | High Pressure Sodium | 38.91709450000 | -77.02827101000
4/25/08 | 506754 | 0 | 1ST ST | NE | 4/29/08 | 61238 | 6A261 | (Light out) | 4-29-08 all lights in this area found okay checked poles 61238 and 61243 FRONT - PATTERSON | High Pressure Sodium | 38.90488153000 | -77.00596863000
4/25/08 | 506185 | 1801 | 18TH ST | NW | 4/25/08 | 26751 | 2M113 | (Light out) | 4-2-08 kevin hollins repaired pole #26751 | High Pressure Sodium | 38.91419269000 | -77.04157712000
4/25/08 | 506127 | 0 | I ST | NW | 4/25/08 | 22483 | 2M184 | (Light out) | 4-2-08 kevin hollins repaired pole #22483 | High Pressure Sodium | 38.90094603000 | -77.02278261000
4/24/08 | 506168 | 740 | 6TH ST | NW | 4/26/08 | 22513 | 6S425 | (Light out) | 4-26-08 DA N/C ticket to wo #404538 no hansen # EVEN SIDE. 22-513 IS A COBRA HEAD ON A MAST ARM. 22-514 IS A DECORATIVE "CHINATOWN" STYLE LIGHT. - | High Pressure Sodium | 38.89950950000 | -77.02001122000
4/24/08 | 505587 | 1915 | BENNING RD | NE | 4/25/08 | 74699DC | 6M785 | (Light out) | 4-25-08 leroy keys repaired pole #74699DC | High Pressure Sodium | 38.89867900000 | -76.97586824000
4/24/08 | 505528 | 3300 | SHERMAN AVE | NW | 4/25/08 | 12898 | 1L288 | (Light out) | 4-25-08 gary hicks repaired pole #12898 | High Pressure Sodium | 38.93167505000 | -77.02676573000
4/24/08 | 505523 | 0 | SHERIDAN RD | SE | 4/24/08 | 81364DC | 8M048 | (Light out) | 4-24-08 leroy keys repaired pole #81364dc | High Pressure Sodium | 38.85942886000 | -76.99337741000
4/24/08 | 505514 | 508 | MELLON ST | SE | 6/24/08 | 86496 | 8A358 | (Light out) | 4-24-08 leroy keys repaired no pole tag 6-23-08 D.Webb-----installed and re gps pole# 86496 | High Pressure Sodium | 38.86233552000 | -77.00031519000
4/24/08 | 505512 | 1915 | BENNING RD | NE | 4/24/08 | 74699DC | 6M785 | (Light out) | 4-24-08 tim richards repaired pole #74699dc | High Pressure Sodium | 38.89867900000 | -76.97586824000
4/24/08 | 505508 | 1333 | H ST | NE | 4/24/08 | 62351 | 6S125 | (Light out) | 4-24-08 tim richards repaired pole #62351 | High Pressure Sodium | 38.90011679000 | -76.98753683000
4/24/08 | 505011 | 0 | 18TH ST | NW | 4/24/08 | 26770 | 2M164 | (Light out) | 4-24-08 kevin hollins repaired pole #26770 | High Pressure Sodium | 38.91009872000 | -77.04173924000
4/24/08 | 505010 | 1800 | 18TH ST | NW | 4/24/08 | 26779 | 2M110 | (Light out) | 4-24-08 kevin holiins repaired pole #26779 | High Pressure Sodium | 38.91448625000 | -77.04174656000
4/24/08 | 505009 | 1840 | 18TH ST | NW | 4/24/08 | 26781 | 2M099 | (Light out) | 4-24-08 kevin holiins repaired pole #26781 | High Pressure Sodium | 38.91550824000 | -77.04159641000
4/24/08 | 505006 | 206 | D ST | SE | 4/24/08 | 65644 | 65618 | (Light out) | 4-24-08 tim richards repaired pole #65644 | High Pressure Sodium | 38.88502510000 | -77.00336540000
4/23/08 | 505478 | 0 | H ST | NE | 4/25/08 | 62354 | 6S136 | (Light out) | 4-25-08 tim richards repaired pole #62354 SIDE OF - | High Pressure Sodium | 38.90011064000 | -76.98535317000
4/23/08 | 504878 | 0 | FERN PL | NW | 4/24/08 | 4D591DC | 4D891DC | (Light off/on) | 4-24-08 roger warren repaired pole #4D591DC | Incandescent | 38.97836028000 | -77.02202042000
4/23/08 | 504867 | 0 | CHILLUM PL | NE | 4/24/08 | 4P517DC | 4U175 | (Light out) | 4-24-08 roger warren repaired pole #4p517dc | High Pressure Sodium | 38.95886157000 | -77.00144501000
4/22/08 | 504810 | 633 | D ST | NW | 4/24/08 | 60175 | 6S602 | (Light out) | 4-24-08 tim richards pole #60175 instaled 118 globe FRONT SOUTHSIDE - street light cover is gone on a metal pole | High Pressure Sodium | 38.89474457000 | -77.02113373000
4/22/08 | 504224 | 2318 | 32ND ST | SE | 4/23/08 | 74838DC | 7A102DC | (Light out) | 4-23-08 leroy keys repaired pole #74838DC | High Pressure Sodium | 38.86110733000 | -76.96087329000
4/22/08 | 504202 | 0 | 12TH ST | NW | 4/22/08 | 12929 | 1G535 | (Light out) | 4-22-08 chris ashton repaired pole #12929 | High Pressure Sodium | 38.91709450000 | -77.02827101000
4/22/08 | 504149 | 0 | K ST | NW | 4/28/08 | 22407 | 6A081 | (Light out) | 4/28/08 H. Lancaster , installed new fixture , job completed. k. Greenfield 4/25/08 W. Kates has current need bucket truck to check fixture. | High Pressure Sodium | 38.90260339000 | -77.02144707000
4/22/08 | 504147 | 825 | 7TH ST | NW | 4/22/08 | 22454 | 6M663 | (Light out) | 4-22-08 kevin hollins repaired pole #22454 | High Pressure Sodium | 38.90048495000 | -77.02182106000
4/22/08 | 504143 | 800 | 8TH ST | NW | 4/22/08 | 22969 | 2M383 | (Light out) | 4-22-08 kevin hollins repaired pole #22969 | High Pressure Sodium | 38.90023907000 | -77.02300991000
4/22/08 | 504141 | 0 | I ST | NW | 4/22/08 | 22487 | 2G985 | (Light out) | 4-22-08 kevin hollins repaired pole #22487 | High Pressure Sodium | 38.90081220000 | -77.02379981000
4/22/08 | 503733 | 900 | 4TH ST | SE | 4/22/08 | 67541 | 6B425 | (Light out) | 4-22-08 tim richards repaired pole #67541 | High Pressure Sodium | 38.87860117000 | -77.00051529000
4/20/08 | 504181 | 0 | WISCONSIN AVE | NW | 4/24/08 | 30137 | 3G019 | (Light out) | - 4-24-08 chris ashton repaired pole #30137 also checked pole #30138, and 30177 found okay streetlight is out | High Pressure Sodium | 38.92630371000 | -77.07330137000
4/18/08 | 503015 | 64 | NEW YORK AVE | NE | 4/18/08 | 56752 | 5M127 | (Light off/on) | 4-18-08 gary hicks repaired pole #56752 | High Pressure Sodium | 38.90868561000 | -77.00559893000
4/18/08 | 503013 | 2 | L ST | NE | 4/22/08 | 61201 | 6A240 | (Light out) | 4-22-08 tim richards previously repaired 4/18/08 | High Pressure Sodium | 38.90378899000 | -77.00858856000
4/18/08 | 503012 | 2 | L ST | NE | 4/19/08 | 61201 | 6A240 | (Light out) | 4-19-08 tim richards repaired pole #61201 | High Pressure Sodium | 38.90378899000 | -77.00858856000
4/18/08 | 503007 | 0 | DELAWARE AVE | NE | 4/19/08 | 61286 | 6S317 | (Light out) | 4-19-08 tim richards pole #61286 getting replaced with new pole | High Pressure Sodium | 38.90515180000 | -77.00317119000
4/18/08 | 503004 | 1299 | DELAWARE AVE | NE | 4/19/08 | 61287 | 6S315 | (Light out) | 4-19-08 tim richards pole #61287 getting replaced with new pole | High Pressure Sodium | 38.90477566000 | -77.00330616000
4/18/08 | 503002 | 1101 | 2ND ST | NE | 4/19/08 | 61290 | 6S309 | (Light off/on) | 4-19-08 tim richards pole #61290 getting replaced with new pole | High Pressure Sodium | 38.90386136000 | -77.00350103000
4/18/08 | 503001 | 921 | 2ND ST | NE | 4/19/08 | 61294 | 6S302 | (Light out) | 4-19-08 tim richards pole #61294 getting replaced with new pole | High Pressure Sodium | 38.90239026000 | -77.00360443000
4/18/08 | 502946 | 509 | 7TH ST | NW | 6/2/08 | 22431 | 6M628 | (Light out) | 4-18-08 kevin hollins repaired no pole tag Installed tag#22431 | High Pressure Sodium | 38.89648966000 | -77.02200839000
4/18/08 | 502396 | 580 | 23RD PL | NE | 4/18/08 | 74315 | 7E159 | (Light out) | 4-18-08 tim richards repaired pole #74315 | High Pressure Sodium | 38.89816568000 | -76.97316755000
4/17/08 | 502345 | 1742 | 18TH ST | NW | 4/18/08 | 26778 | 2M116 | (Light off/on) | 4-18-08 kevin hollins checked pole #26778 light found ok | High Pressure Sodium | 38.91399493000 | -77.04172986000
4/17/08 | 502048 | 840 | E ST | NW | 4/17/08 | 60181 | 2M345 | (Light out) | 4-17-08 kevin hollins repaired pole #60181 | High Pressure Sodium | 38.89605528000 | -77.02218319000
4/16/08 | 502039 | 725 | 20TH ST | NE | 6/24/08 | 74300 | 7E155 | (Light out) | 4-17-08 D Smith/Gray/Manning Replaced 400w hps power door, lamp, starter and reconnect the ground wire need pole tag 4-17-08 leroy keys N/C to overhead needs pole tag 6-23-08 D.Webb------pole found already tagged | High Pressure Sodium | 38.89833444000 | -76.97424631000
4/16/08 | 502037 | 0 | E ST | NW | 4/17/08 | 23333 | 2M352 | (Light out) | 4-17-08 kevin hollins repaired pole #23333 | High Pressure Sodium | 38.89621843000 | -77.02226690000
4/16/08 | 502032 | 4448 | KENILWORTH AVE | NE | 4/17/08 | 70305 | 7M057 | (Light out) | 4-17-08 leroy keyd repaired pole #70305 | High Pressure Sodium | 38.90849117000 | -76.93770064000
4/16/08 | 501950 | 0 | WISCONSIN AVE | NW | 4/17/08 | 30137 | 3G019 | (Light off/on) | 4-17-08 chris ashton pole #30137 checked p/c light found okay | High Pressure Sodium | 38.92630371000 | -77.07330137000
4/16/08 | 501906 | 0 | KENILWORTH AVE | NE | 4/16/08 | 70306 | 7M058 | (Light out) | 4-16-08 leroy keys repaired pole #70306 | High Pressure Sodium | 38.90838237000 | -76.93790987000
4/15/08 | 501293 | 775 | H ST | NE | 4/15/08 | 61991 | 6S197 | (Light out) | 4-15-08 tim richards repaired pole #61991 | High Pressure Sodium | 38.90030060000 | -76.99586046000
4/15/08 | 501898 | 3200 | KENYON PL | NW | 5/1/08 | 14683 | 1G052 | (Light out) | -4-17-08 roger warren repaired pole #14683 light out on metal pole 5-1-08 R.Waites----repaired pole tag | High Pressure Sodium | 38.93003166000 | -77.03236323000
4/15/08 | 501165 | 5573 | SOUTHERN AVE | SE | 4/16/08 | 75511 | 75511DC | (Light out) | 4-16-08 leroy keys repaired pole #75511 | High Pressure Sodium | 38.88389291000 | -76.92103667000
4/15/08 | 501163 | 4406 | NANNIE HELEN BURROUGHS AVE | NE | 4/16/08 | 71307DC | 7A242 | (Light out) | 4-16-08 leroy keys repaired pole #71307dc | High Pressure Sodium | 38.90023779000 | -76.93819749000
4/15/08 | 501162 | 4448 | KENILWORTH AVE | NE | 4/16/08 | 70305 | 7M057 | (Light out) | 4-16-08 leroy keys repaired pole #70305 | High Pressure Sodium | 38.90849117000 | -76.93770064000
4/15/08 | 501154 | 0 | MARYLAND AVE | NE | 4/15/08 | 59543 | 5M235 | (Light out) | 4-15-08 gary hicks repaired pole #59543 | High Pressure Sodium | 38.90048084000 | -76.98254108000
4/15/08 | 501130 | 1905 | 9TH ST | NE | 4/17/08 | 56682DC | 5M025 | (Light out) | 4-17-08 gary hiks repaired pole #56682dc 4-15-08 A Young Wood pole 56682dc 1st pole South of T St | High Pressure Sodium | 38.91522709000 | -76.99357003000
4/15/08 | 501065 | 1000 | NEW YORK AVE | NW | 4/15/08 | 22948 | 2L032 | (Light out) | 4-15-08 kevin hollins repaired pole #22948 | High Pressure Sodium | 38.90132896000 | -77.02684244000
4/15/08 | 501060 | 1335 | 11TH ST | NW | 4/15/08 | 25282 | 2M248 | (Light out) | 4-15-08 kevin holins repaired pole #25282 | High Pressure Sodium | 38.90790310000 | -77.02715169000
4/15/08 | 500494 | 0 | K ST | NW | 4/15/08 | 22402 | 6A100 | (Light out) | 4-15-08 tim richards repaired pole #22402 | High Pressure Sodium | 38.90245268000 | -77.01971021000
4/15/08 | 500492 | 4709 | NORTH CAPITOL ST | NE | 4/15/08 | 4R753 | 4A794 | (Light out) | 4-15-08 kevin hollins repaired pole #4r753 | High Pressure Sodium | 38.94851572000 | -77.00881793000
4/14/08 | 500383 | 509 | KENNEDY ST | NW | 4/15/08 | 4M065 | 4M065DC | (Light out) | 4-15-08 roger warren repaired pole #4m065 | High Pressure Sodium | 38.95650364000 | -77.02039698000
4/12/08 | 500178 | 1021 | 17TH ST | NE | 4/12/08 | 59346 | 59346 | (Light out) | 4-12-08 gary hicks repaired pole #59346 | High Pressure Sodium | 38.90312888000 | -76.97890387000
4/12/08 | 500128 | 200 | I ST | SE | 4/12/08 | 67648 | 6A422 | (Light out) | 4-12-08 tim richards repaired pole #67648 rewired @ base | High Pressure Sodium | 38.87934724000 | -77.00236217000
4/11/08 | 499614 | 1100 | HALF ST | SE | 4/11/08 | 67435 | 6B100 | (Light out) | 4-11-08 tim richards repaired pole #67435 (reset tl/pc) | High Pressure Sodium | 38.87824281000 | -77.00752674000
4/11/08 | 499565 | 1215 | CONNECTICUT AVE | NW | 4/11/08 | 24533 | 2U523 | (Light out) | 4-11-08 kevin hollins repaired pole #24533 | High Pressure Sodium | 38.90616068000 | -77.04157912000
4/11/08 | 499548 | 4502 | NANNIE HELEN BURROUGHS AVE | NE | 4/11/08 | 71304DC | 7A241 | (Light out) | 4-11-08 leroy keys repaired pole #71304dc (400 hps bulb, powerdoor,fixture, tl/pc) complete | High Pressure Sodium | 38.89991666000 | -76.93777979000
4/11/08 | 499542 | 0 | M ST | NW | 4/11/08 | 23730 | 2U534 | (Light out) | 4-11-08 kevin hollins repaired pole #23730 | High Pressure Sodium | 38.90557436000 | -77.04154706000
4/11/08 | 499519 | 1218 | CONNECTICUT AVE | NW | 4/11/08 | 24532 | 2U519 | (Light out) | 4-11-08 kevin hollins repaired pole #24532 | High Pressure Sodium | 38.90651643000 | -77.04185036000
4/11/08 | 499163 | 0 | 11TH STREET BRG | SE | 4/18/08 | 68043 | 6L999 | (Light out) | 4-18-08 M Brewer/Osvatics Replaced safe cap, removed MV transf. out of hand box on jersey wall and made two new splices in hand box, removed the ground from the nuetral - 1 #10 splice 7 1 split bolt 4-11-08 billy black pole #68043 305 volts - refer to f | High Pressure Sodium | 38.87823994000 | -76.99138115000
4/11/08 | 499161 | 1101 | L ST | NW | 4/11/08 | 25942 | 2M218 | (Light out) | 4-11-08 kevin hollins repaired pole #25942 reset tl/pc and will monitor over next 24 hours | High Pressure Sodium | 38.90408908000 | -77.02717553000
4/11/08 | 499160 | 0 | 9TH ST | NW | 4/11/08 | 25437 | 2L558 | (Light out) | 4-11-08 kevin hollins repaired pole #25437 | High Pressure Sodium | 38.90380790000 | -77.02408338000
4/10/08 | 499085 | 4815 | TEXAS AVE | NE | 4/10/08 | 76839 | 76939 | (Light out) |  | High Pressure Sodium | 38.88961077000 | -76.93822815000
4/10/08 | 499084 | 4815 | TEXAS AVE | NE | 4/10/08 | 76839 | 76939 | (Light out) |  | High Pressure Sodium | 38.88961077000 | -76.93822815000
4/10/08 | 499042 | 3709 | NEWARK ST | NW |  | 38994DC | 3U394 | (Light out) |  | High Pressure Sodium | 38.93488284000 | -77.07368761000
4/9/08 | 498476 | 650 | MASSACHUSETTS AVE | NW | 4/10/08 | 22465 | 6A979 | (Light out) | 4-9-08 kevin hollins repaired pole #22465 (400 hps bulb) complete | High Pressure Sodium | 38.90204075000 | -77.02130668000
4/9/08 | 498473 | 0 | K ST | NW | 4/9/08 | 22402 | 6A100 | (Light out) | 4-9-08 kevin hollins repaired pole #22402 (reset p/c) complete | High Pressure Sodium | 38.90245268000 | -77.01971021000
4/9/08 | 498429 | 826 | 2ND ST | NE |  | 61300 | 6S290 | (Light out) | A. Byrd 5-19-08 Area currently under construction by Chesapeake Electric/ Fort Myer Construction. Contractor (Chesapeake Electric) is currently awaiting Pepco feed point connections. 4-10-08 - Construction - New poles refer to Ddot Please let City | High Pressure Sodium | 38.90069257000 | -77.00363545000
4/9/08 | 497815 | 1338 | W ST | NW | 4/9/08 | 12065 | 1G572 | (Light out) | 4-9-08 gary hicks repaired pole #12065 (400 hps bulb) complete | High Pressure Sodium | 38.91924307000 | -77.03106855000
4/8/08 | 497767 | 1111 | 14TH ST | NW | 4/11/08 | 27350 | 2M423 | (Light out) |  | High Pressure Sodium | 38.90469050000 | -77.03208800000
4/8/08 | 497761 | 740 | 6TH ST | NW | 5/21/08 | 22513 | 6S425 | (Light out) | 4-09-08 P Harvin No Current DDOT REFER Found ok | High Pressure Sodium | 38.89950950000 | -77.02001122000
4/8/08 | 497759 | 0 | L ST | NW | 4/11/08 | 29222 | 2M215 | (Light out) | 4/11/08 W. Kates made splices in MH , job completed K. greenfield 4-9-08 kevin hollins pole #29222 still N/C underground | High Pressure Sodium | 38.90380035000 | -77.02723524000
4/8/08 | 497758 | 1010 | MASSACHUSETTS AVE | NW | 4/11/08 | 25961 | 2M216 | (Light out) | 4/11/08 W. Kates made splices in MH , job completed K. greenfield 4-9-08 kevin hollins pole #25961 still N/C underground | High Pressure Sodium | 38.90379985000 | -77.02690625000
4/8/08 | 497756 | 1010 | 11TH ST | NW |  | 29203 | 2M214 | (Light out) | 4/11/08 combo pole with traffic & SL in common duct, refer to DDot . 4-9-08 kevin hollins pole #29203 still N/C underground | High Pressure Sodium | 38.90369501000 | -77.02685773000
4/8/08 | 497754 | 1044 | 5TH ST | NW |  | 60069 | 6A143 | (Light out) | IPMA PROJECT 4-17-08 UGo/Kates new poles & MH being installed by out side contractor refer to DDot. 4-17-08 O Taylor/Chris under construction 4-17-08 W Kates/UGO Lights are off due to reconstructing lights for proposed new property 4-9-08 tim ric | High Pressure Sodium | 38.90338284000 | -77.01883666000
4/8/08 | 497752 | 425 | MASSACHUSETTS AVE | NW | 5/28/08 | 60482 | 6A192 | (Light out) | R Rapolla, 5-28-2008, Duplicate to ticket #481048 4-9-08 tim richards pole #60482 N/C under ground refer to fault crew Refer to DDot New poles | Mercury Vapor | 38.90049835000 | -77.01683728000
4/8/08 | 497751 | 1209 | U ST | NW | 4/9/08 | 13284 | 1G534 | (Light out) | 4-9-08 DA duplicate ticket to wo #496867 hansen #1755964 | High Pressure Sodium | 38.91691923000 | -77.02846873000
4/8/08 | 497747 | 0 | M ST | NW | 4/9/08 | 23739 | 2G718 | (Light out) | 4-09-08 P Harvin Found ok putting up new SL | High Pressure Sodium | 38.90513126000 | -77.04778068000
4/8/08 | 497746 | 0 | M ST | NW | 4/9/08 | 23739 | 2G718 | (Light out) | 4-09-08 P Harvin Found ok | High Pressure Sodium | 38.90513126000 | -77.04778068000
4/8/08 | 497736 | 650 | MASSACHUSETTS AVE | NW | 4/9/08 | 22465 | 6A979 | (Light out) | 4-09-08 P Harvin TLP | High Pressure Sodium | 38.90204075000 | -77.02130668000
4/8/08 | 497709 | 801 | D ST | NW | 4/8/08 | 60087 | 2M371 | (Light out) | 4-8-08 tim richards repaired pole #60087 (400 hps bulb) complete | High Pressure Sodium | 38.89493542000 | -77.02306697000
4/8/08 | 497325 | 1625 | MASSACHUSETTS AVE | NW | 4/8/08 | 27102 | 2M003 | (Light out) | 4-8-08 kevin hollins repaired pole #27102 (400 hps bulb) complete | High Pressure Sodium | 38.90778988000 | -77.03832443000
4/7/08 | 497125 | 159 | V ST | NW | 4/7/08 | 14155 | 53125 | (Light out) | 4-7-08 gary hicks light is on and working fine- marked with no current tape but light is working | High Pressure Sodium | 38.91850290000 | -77.01401173000
4/7/08 | 497123 | 3460 | 14TH ST | NW | 4/8/08 | 13803 | 1G084 | (Light out) | 4-8-08 chris ashton pole #13804 N/C underground refer to wo #485581, hansen #173686 | High Pressure Sodium | 38.93314624000 | -77.03283352000
4/7/08 | 497120 | 0 | 14TH ST | NW | 4/8/08 | 12073 | 1G564 | (Light out) | 4-7-08 chris ashton pole #12073 N/C underground refer to wo #471572 | High Pressure Sodium | 38.92089953000 | -77.03174747000
4/7/08 | 497118 | 3429 | 14TH ST | NW | 4/8/08 | 13804 | 1G082 | (Light out) | 4-8-08 chris ashton pole #13804 N/C underground | High Pressure Sodium | 38.93260036000 | -77.03283470000
4/7/08 | 497114 | 4115 | 42ND ST | NE | 4/8/08 | 70329 | 7M085 | (Light out) |  | High Pressure Sodium | 38.90318186000 | -76.94427070000
4/7/08 | 497080 | 3310 | 14TH ST | NW | 4/10/08 | 13815 | 1G064 | (Light out) | 4-10-08 M Craig Previously Serviced 4-09-08 R Waites Street under construction unable to block one lane open to traffic 4-8-08 chris ashton repaired pole no id tag (adjusted p/c) complete | High Pressure Sodium | 38.93069614000 | -77.03283445000
4/7/08 | 497078 | 3310 | 14TH ST | NW | 4/8/08 | 13815 | 1G064 | (Light off/on) | 4-8-08 chri ashton repaired pole #13815 (400 hps bulb) complete | High Pressure Sodium | 38.93069614000 | -77.03283445000
4/7/08 | 497024 | 4406 | NANNIE HELEN BURROUGHS AVE | NE | 4/11/08 | 71307DC | 7A242 | (Light out) | 4-11-08 leroy keys repaired pole #71307dc (400 hps bulb, tl/pc) complete | High Pressure Sodium | 38.90023779000 | -76.93819749000
4/7/08 | 497018 | 0 | KENILWORTH AVE | NE | 4/15/08 | 70308 | 7M061 | (Light dim) | 4-15-08 leroy keys repaired pole #70308 4-12-08 leroy keys - cars are traveling at to high of a speed to repair pole - refer to ay shift | High Pressure Sodium | 38.90758876000 | -76.93860988000
4/5/08 | 496898 | 1630 | PARK RD | NW | 4/5/08 | 10113 | 1G350 | (Light out) | 4-5-08 roger warren repaired pole #10113 complete ( 400 hps bulb ) | High Pressure Sodium | 38.93200838000 | -77.03722437000
4/5/08 | 496427 | 0 | M ST | NW | 4/5/08 | 23719 | 2G722 | (Light out) | 4-5-08 kevin hollins repaired pole #23719 (400 hps bulb) complete | High Pressure Sodium | 38.90557300000 | -77.04706313000
4/4/08 | 496867 | 1209 | U ST | NW | 4/9/08 | 13284 | 1G534 | (Light out) | 4-9-08 gary hicks repaired pole #13284 (400 hps bulb, powerdoor, tl/pc) complete IN FRONT OF 1212 U ST. NW. SOUTHSIDE OF U ST. NW - | High Pressure Sodium | 38.91691923000 | -77.02846873000
4/4/08 | 496217 | 1770 | BENNING RD | NE | 4/4/08 | 63615 | 6M778 | (Light out) | 4-4-08 tim richards repaired pole #63615 (400 hps bulb) complete | High Pressure Sodium | 38.89907267000 | -76.97811088000
4/4/08 | 496193 | 0 | WISCONSIN AVE | NW | 4/4/08 | 30137 | 3G019 | (Light out) | 4-4-08 chris ashton repaired pole #30137 (400 hps bulb) complete | High Pressure Sodium | 38.92630371000 | -77.07330137000
4/3/08 | 495648 | 0 | O ST | NE | 4/3/08 | 62315 | 5M112 | (Light out) | 4-3-08 tim richards repaired pole #62315 (250 hps bulb, powerdoor) complete | High Pressure Sodium | 38.90852270000 | -77.00482604000
4/3/08 | 495583 | 1524 | EASTERN AVE | NE | 4/5/08 | 71133 | 7S085 | (Light out) | 4-5-08 darryl hooker repaired pole #71133 complete ( 400 hps bulb ) | High Pressure Sodium | 38.91031434000 | -76.93176145000
4/3/08 | 495561 | 723 | BARNES ST | NE | 4/4/08 | 72463DC | 7A472 | (Light out) | 4-4-08 darryl hooker repaired pole #72463dc (400 hps bulb) complete | High Pressure Sodium | 38.90181026000 | -76.94988632000
4/3/08 | 495556 | 0 | KENILWORTH AVE | NE | 4/4/08 | 70014 | 7M047 | (Light out) | 4-4-08 darryl hooker repaired pole #70014 (400 hps bulb) complete | High Pressure Sodium | 38.91119327000 | -76.93541543000
4/3/08 | 496171 | 1209 | U ST | NW | 4/5/08 | 13284 | 1G534 | (Light out) | 4-5-08 roger warren repaired pole #13284 complete ( 40 hps bulb ) FRONT - STREETLIGHT ON METAL POLE BURNT OUT | High Pressure Sodium | 38.91691923000 | -77.02846873000
4/3/08 | 495519 | 0 | WISCONSIN AVE | NW | 4/3/08 | 30180 | 3G006 | (Light out) | 4-3-08 chris ashton repaired pole #30180 complete (400 hps bulb) | High Pressure Sodium | 38.92762077000 | -77.07306785000
4/2/08 | 494977 | 841 | 7TH ST | NW | 4/2/08 | 22422 | 6M662 | (Light out) | 4-2-08 kevin hollins repaired pole #22422 (400 hps bulb) complete | High Pressure Sodium | 38.90021373000 | -77.02201497000
4/2/08 | 494873 | 5730 | UTAH AVE | NW | 4/4/08 | 4B242DC | 4B242 | (Light off/on) | 4-4-08 roger warren repaired pole #4B242DC (150 hps bulb) complete | Mercury Vapor | 38.96701403000 | -77.06072007000
4/2/08 | 494836 | 623 | KENNEDY ST | NW | 4/2/08 | 4M069 | 4M069DC | (Light out) | 4-2-08 roger warren repaired pole #4m169 (400 hps bulb) complete | High Pressure Sodium | 38.95646426000 | -77.02185855000
4/2/08 | 494773 | 2730 | WISCONSIN AVE | NW | 4/2/08 | 30177 | 3G020 | (Light out) | 4-2-08 chris ashton repaired pole #30177dc (400 bulb, powerdoor, tl/pc) complete | High Pressure Sodium | 38.92608314000 | -77.07307216000
4/1/08 | 494248 | 8034 | 16TH ST | NW | 4/1/08 | 4C416 | 4C516 | (Light out) | 4-1-08 darryl hooker repaired pole #4c416 (175 mv bulb) complete | High Pressure Sodium | 38.98993862000 | -77.03642757000
4/1/08 | 494240 | 64 | NEW YORK AVE | NE | 4/1/08 | 56752 | 5M127 | (Light out) | 4-1-08 tim richards repaired pole #56752 (400 hps bulb) complete | High Pressure Sodium | 38.90868561000 | -77.00559893000
3/31/08 | 493706 | 2517 | BENNING RD | NE | 4/1/08 | 59618DC | 5M306DC | (Light out) | 4-1-08 gary hicks repaired pole #59618dc (400 hps bulb, starter) complete | High Pressure Sodium | 38.89804439000 | -76.97077658000
3/31/08 | 493700 | 0 | 2ND ST | NE | 4/2/08 | 62318 | 6S295 | (No current) | 4-2-08 tim richards pole #62318 N/C underground refer to wo #474408 | High Pressure Sodium | 38.90121715000 | -77.00349984000
3/31/08 | 493695 | 800 | 4TH ST | NW | 4/1/08 | 60448 | 6S459 | (No current) | R Rapolla, 4-1-08, Closed work order due to a system malfunction on 3-31-08. Inventory# reviewed the correct address, but when the work order was enterred the wrong inventory data was created. | High Pressure Sodium | 38.90032749000 | -77.01608012000
3/31/08 | 493694 | 811 | 4TH ST | NW | 4/2/08 | 60449 | 6S463 | (No current) | 4-2-08 tim richards pole #60449 N/C underground refer to wo #474612 | High Pressure Sodium | 38.90088288000 | -77.01610076000
3/31/08 | 493693 | 0 | O ST | NE | 4/1/08 | 62315 | 5M112 | (Light off/on) | 4-1-08 gary hicks light found okay | High Pressure Sodium | 38.90852270000 | -77.00482604000
3/31/08 | 493692 | 0 | FLORIDA AVE | NE |  | 61249 | 5M120 | (No current) | R Rapolla, 4-1-08, This is a duplicate to WO#437470. Pepco has this job in egineering and will inform Ddot & Severn when this job is ready to go into construction. | High Pressure Sodium | 38.90877009000 | -77.00462146000
3/31/08 | 493682 | 2366 | BENNING RD | NE | 3/31/08 | 74443DC | 7E174 | (Light out) | 3-31-08 gary hicks repaired pole #74443dc (400 hps bulb, fixture, tl/pc) complete | High Pressure Sodium | 38.89749819000 | -76.96876796000
3/31/08 | 493679 | 500 | OKLAHOMA AVE | NE | 4/2/08 | 74441DC | 7E172 | (Light out) | 4-2-08 darryl hooker repaired pole #74441dc (400 hp bulb) complete | High Pressure Sodium | 38.89756245000 | -76.96942454000
3/31/08 | 493666 | 0 | BENNING RD | NE | 3/31/08 | 59598 | 5M225 | (Light out) | 3-31-08 gary hicks temp pole #59598 | High Pressure Sodium | 38.90009642000 | -76.98233922000
3/28/08 | 493065 | 0 | 22ND ST | NE | 3/29/08 | 63632 | 6M793 | (Light out) | 3-29-08 tim richards light found okay | High Pressure Sodium | 38.89028237000 | -76.97436503000
3/28/08 | 492958 | 300 | D ST | SW | 4/7/08 | 21636 | 6A364 | (Light out) | 4-07-08 UGO/W Kates made splice in m/H installled NWP 3-29-08 kevin hollins pole #21636 N/C @ base | High Pressure Sodium | 38.88513641000 | -77.01402907000
3/28/08 | 492956 | 0 | D ST | SW | 3/29/08 | 21635 | 6A362 | (Light out) | 3-29-08 kevin hollins repaired pole #21635 (250 hps bulb) complete | High Pressure Sodium | 38.88513650000 | -77.01444311000
3/28/08 | 492948 | 2730 | WISCONSIN AVE | NW | 3/29/08 | 30177 | 3G020 | (Light out) | 3-29-08 chris ashton - previously repaired | High Pressure Sodium | 38.92608314000 | -77.07307216000
3/28/08 | 492947 | 2226 | WISCONSIN AVE | NW | 3/29/08 | 30151 | 3G081 | (Light out) | 3-29-08 chris ashton pole #30150 reviously repaired | High Pressure Sodium | 38.92001524000 | -77.07145927000
3/28/08 | 492938 | 0 | 22ND ST | NW | 3/29/08 | 28287 | 2A222 | (Light out) | 3-29-08 kevin hollins light found okay | High Pressure Sodium | 38.90015885000 | -77.04890071000
3/28/08 | 492886 | 2730 | WISCONSIN AVE | NW | 3/28/08 | 30177 | 3G020 | (Light out) | 3-28-08 chris ashton repaired pole #30177dc (tightened pc) complete | High Pressure Sodium | 38.92608314000 | -77.07307216000
3/28/08 | 492885 | 5524 | SOUTHERN AVE | SE | 3/28/08 | 75510 | 75510DC | (Light out) | 3-28-08 darryl hooker repaired pole #75510 (400 hps bulb ) complete | High Pressure Sodium | 38.88359254000 | -76.92141921000
3/28/08 | 492846 | 2226 | WISCONSIN AVE | NW | 3/28/08 | 30151 | 3G081 | (Light out) | 3-28-08 gary hicks repaired pole # (100 hps bulb, starter) complete | High Pressure Sodium | 38.92001524000 | -77.07145927000
3/28/08 | 492845 | 2226 | WISCONSIN AVE | NW | 3/28/08 | 30151 | 3G081 | (Light out) | 3-28-08 chris ashton repaired pole #30151 (400 hps bulb, reconnected wire ) complete | High Pressure Sodium | 38.92001524000 | -77.07145927000
3/27/08 | 492355 | 1301 | U ST | NW | 3/27/08 | 11721 | 1G521 | (Light out) | 3-27-08 gary hicks repaired pole #11721 (400 hps bulb) complete | High Pressure Sodium | 38.91709342000 | -77.03069626000
3/27/08 | 492343 | 1111 | 14TH ST | NW | 12/16/08 | 27350 | 2M423 | (Light out) | 4-07-08 UGO/W Kates Pepco needs to energize the secondary line 4-01-08 O Taylor Need MOT M/H is in center of street 3-31-08 O Taylor - Open M/H not accessible located 6ft from pole need parkings signs 3-28-08 kevin hollins pole #27350 N/C underground | High Pressure Sodium | 38.90469050000 | -77.03208800000
3/27/08 | 492335 | 1112 | Q ST | NW | 3/28/08 | 29306DC | 2U047DC | (Light out) | 3-28-07 kevin hollins repaired pole #29306dc (189 inc bulb) complete | Incandescent | 38.91083084000 | -77.02756095000
3/27/08 | 492318 | 2400 | K ST | NW | 3/28/08 | 24648 | 2G665 | (Light out) | 3-28-08 kevin hollins repaired pole #24648 (400 hps bulb) complete | High Pressure Sodium | 38.90268752000 | -77.05153812000
3/27/08 | 492286 | 4514 | 13TH ST | NW | 3/27/08 | 4K422 | 4U131 | (Light off/on) | 3-27-08 roger warren repaired pole #4k422 (400 hps bulb) complete | High Pressure Sodium | 38.94571765000 | -77.02978404000
3/27/08 | 491761 | 610 | H ST | NW | 4/1/08 | 22559 | 6M700 | (Light out) | 3/28/08 Al Young , new secondary in pepco MH ,need pepco tails installed for SL taps. Refer to pepco. 3-27-08 kevin hollins pole #22559 N/C @ fixture no access to base | High Pressure Sodium | 38.89973402000 | -77.02073448000
3/26/08 | 491756 | 1000 | 5TH ST | SE | 3/27/08 | 67557 | 6B467 | (Light out) | 3-27-08 tim richards repaired pole #67557 (400 hps bulb, tl/pc) complete | High Pressure Sodium | 38.87826913000 | -76.99959928000
3/26/08 | 491726 | 3429 | 14TH ST | NW | 4/1/08 | 13804 | 1G082 | (Light out) | 3-27-08 chris ashton pole #13804 (N/C underground | High Pressure Sodium | 38.93260036000 | -77.03283470000
3/26/08 | 491625 | 933 | K ST | SE | 3/27/08 | 67656 | 6B428 | (Light out) | 3-27-08 tim richards repaired pole #67656 (250 hps bulb) complete | High Pressure Sodium | 38.87847018000 | -76.99984439000
3/26/08 | 492248 | 4520 | HOBAN RD | NW | 3/27/08 | 35820DC | 35820 | (Light out) | 3-27-08 R Waites QC Previously Serviced FRONT - metal pole...burnt out bulb | Incandescent | 38.91406815000 | -77.08570450000
3/26/08 | 491558 | 64 | NEW YORK AVE | NE | 4/5/08 | 56751 | 5M100 | (Light out) | H. Lancaster,4/4/08, made splices in MH & T BASE, JOB COMPLETED. K.Greenfield | High Pressure Sodium | 38.90849482000 | -77.00614254000
3/26/08 | 491557 | 64 | NEW YORK AVE | NE | 3/26/08 | 56752 | 5M127 | (Light out) | 3-26-08 gary hicks repaired pole #56752 (400 hps bulb, starter, tl/pc) complete | High Pressure Sodium | 38.90868561000 | -77.00559893000
3/25/08 | 491035 | 0 | INGRAHAM ST | NW | 1/25/12 | 4M357 | 4M358 | (Light out) | 5/17/08: still under IPMA project W. KATES 3/27/08, NEW POLES & MANHOLE BEING INSTALLED BY OUTSIDE CONTRACTOR, REFER TO DDOT 3-26-08 roger warren pole #4m357 N/C underground - no underground wires to pole | High Pressure Sodium | 38.95408720000 | -77.02592523000
3/25/08 | 491026 | 515 | NEW YORK AVE | NE | 3/26/08 | 56841 | 5A428 | (Light out) | 3-26-08 gary hicks repaired pole #56841 (400 hps bulb, starter, tl/pc) complete 3-25-08 Pole# 56841 | High Pressure Sodium | 38.91151960000 | -76.99667276000
3/25/08 | 491005 | 2122 | 14TH ST | SE | 3/25/08 | 80522 | 8M024 | (Light out) | 3-25-08 darryl hooker repaired pole #80522 (250 hps bulb) complete | High Pressure Sodium | 38.86436582000 | -76.98590224000
3/25/08 | 490948 | 200 | I ST | SE | 3/27/08 | 67648 | 6A422 | (Light out) | 3/27/08 Al Young light found ok. -3-25-08 R Arrington NO Current | High Pressure Sodium | 38.87934724000 | -77.00236217000
3/24/08 | 490458 | 0 | FIRTH STERLING AVE | SE | 3/25/08 | 81558DC | 8M087 | (Light out) | 3-24-08 - refer to WO#490940 | High Pressure Sodium | 38.86197919000 | -76.99894339000
3/24/08 | 490457 | 0 | FIRTH STERLING AVE | SE | 3/25/08 | 81558DC | 8M087 | (Light out) | 3-24-08 - T. Richards light repaired - complete | High Pressure Sodium | 38.86197919000 | -76.99894339000
3/24/08 | 490456 | 0 | FIRTH STERLING AVE | SE | 3/29/08 | 81558DC | 8M087 | (Light out) | 3-28-08 D Smith Peck/Gray Made spliceon secondary wire on pole light working and installed plastic guard over te wire on pole 3-25-08 darryl hooker pole #81558dc N/C to overhead ( lost secondary) | High Pressure Sodium | 38.86197919000 | -76.99894339000
3/24/08 | 490451 | 168 | FIRTH STERLING AVE | SE | 3/26/08 | 82045 | 8M064 | (Light out) | 3-26-08 R Arrington installed 1-400 hps fixture, lamp, TLPC | High Pressure Sodium | 38.86051354000 | -77.00315630000
3/23/08 | 490985 | 740 | 6TH ST | NW | 3/25/08 | 22513 | 6S425 | (Light out) | 3-25-08 DA duplicate ticket to wo #404538 no hansen # 3-25-08 D Webb Found ok 740 6TH STREET NW, WASHINGTON, DC EVEN SIDE - **SRCB** IS THE POLE METAL OR WOOD? - METAL WHAT IS THE PROBLEM WITH THE LIGHT (LIGHT IS OUT, LIGHT IS ALWAYS ON, LIGHT | High Pressure Sodium | 38.89950950000 | -77.02001122000
3/22/08 | 490259 | 1001 | NEW HAMPSHIRE AVE | NW | 3/22/08 | 23865 | 2G675 | (Light out) | 3-22-08 kevin hollins repaired pole #23865 (400 hps bulb) complete | High Pressure Sodium | 38.90290714000 | -77.04949926000
3/22/08 | 490220 | 0 | M ST | NW | 3/22/08 | 23730 | 2U534 | (Light out) | 3-22-08 kevin hollins repaired pole #23730 (400 hps bulb) complete | High Pressure Sodium | 38.90557436000 | -77.04154706000
3/22/08 | 490216 | 4815 | TEXAS AVE | NE | 4/28/08 | 76839 | 76939 | (Light out) | 4/14/08 Jeramiah repaired conduit,made splices in MH, job compoleted, K. Greenfield 3-22-08 tim richards - pole #76839 N/C underground refer to fault crew | High Pressure Sodium | 38.88961077000 | -76.93822815000
3/22/08 | 490215 | 0 | I ST | NW | 3/22/08 | 22487 | 2G985 | (Light out) | 3-22-08 kevin hollins repaired pole #22487 (adjusted tl/pc) complete | High Pressure Sodium | 38.90081220000 | -77.02379981000
3/22/08 | 489814 | 0 | SOUTH DAKOTA AVE | NE | 3/22/08 | 57800DC | 5M195DC | (Light out) | 3-21-08 gary hicks repaired pole #57800dc (400 hps bulb) complete | High Pressure Sodium | 38.92095146000 | -76.95907452000
3/21/08 | 489790 | 2200 | H ST | NW | 3/21/08 | 27997 | 2A216 | (Light out) | 3-21-08 D Smith/R Gray Installed NWPC | High Pressure Sodium | 38.89963632000 | -77.04973980000
3/21/08 | 490237 | 1386 | DELAWARE AVE | NE | 3/25/08 | 61285 | 6S319 | (Light out) | -3-25-08 R Arrington Installed 1-100 hps lamp 3-25-08 tim richards needs van ALLEY - light out.....metal pole | High Pressure Sodium | 38.90554237000 | -77.00303219000
3/21/08 | 490221 | 0 | 16TH ST | NW | 3/25/08 | 4C423 | 4C559 | (Light out) | - 3-25-08 roger warren repaired pole #4C423 (295 inc bulb) complete wooden pole burnt out bulb | High Pressure Sodium | 38.98569078000 | -77.03619028000
3/21/08 | 489677 | 4203 | GEORGIA AVE | NW | 3/21/08 | 4K513 | 4G294 | (Light out) | 3-21-08 chris ashton repaired pole #4k513 (400 hp bulb) complete | High Pressure Sodium | 38.94198605000 | -77.02562660000
3/21/08 | 489666 | 623 | KENNEDY ST | NW | 3/21/08 | 4M069 | 4M069DC | (Light out) | 3-21-08 roger warren repaired pole #4M069 (400 hps bulb) complete | High Pressure Sodium | 38.95646426000 | -77.02185855000
3/21/08 | 489644 | 122 | C ST | NW | 3/21/08 | 60960 | 68292 | (Light out) | 3-21-08 tim richards repaired pole #60960 (400 hps bulb, starter) complete | High Pressure Sodium | 38.89365430000 | -77.01227034000
3/20/08 | 489126 | 1101 | L ST | NW | 3/20/08 | 25942 | 2M218 | (Light out) | 3-20-08 kevin hollins repaired pole #25942 (400 hps bulb) complete | High Pressure Sodium | 38.90408908000 | -77.02717553000
3/19/08 | 488514 | 0 | MASSACHUSETTS AVE | NW | 3/20/08 | 25939 | 2L551 | (Light out) | 3-20-08 kevin hollins - bad address | High Pressure Sodium | 38.90325148000 | -77.02477750000
3/19/08 | 488513 | 0 | MASSACHUSETTS AVE | NW | 3/20/08 | 25939 | 2L551 | (Light out) | 3-20-08 kevin hollins repaired pole #25939 (400 hps bulb) complete | High Pressure Sodium | 38.90325148000 | -77.02477750000
3/19/08 | 488480 | 4815 | TEXAS AVE | NE | 3/26/08 | 76839 | 76939 | (Light out) | -3-25-08 darryl hooker could not locate 3-25-08 R Arrington checked lights on NES & SES all Found ok pole# 74206 NESide 3-24-08 R Arrington Needs beter info | High Pressure Sodium | 38.88961077000 | -76.93822815000
3/19/08 | 488455 | 200 | I ST | SE | 3/19/08 | 67648 | 6A422 | (Light out) | 3-19-08 tim richards repaired pole #67648 (400 hps bulb, tl/pc) complete | High Pressure Sodium | 38.87934724000 | -77.00236217000
3/19/08 | 488447 | 2730 | WISCONSIN AVE | NW | 3/19/08 | 30177 | 3G020 | (Light out) | 3-19-08 kevin hollins repaired pole #30177 (tl/pc) complete | High Pressure Sodium | 38.92608314000 | -77.07307216000
3/18/08 | 487886 | 629 | H ST | NW | 4/1/08 | 22634 | 6M695 | (Light out) | 3-18-08 kevin hollins - pole #22634 N/C underground refer to fault crew D.MOORE--PASSED 03/19/08 | High Pressure Sodium | 38.89990420000 | -77.02118022000
3/18/08 | 487862 | 2730 | WISCONSIN AVE | NW | 3/19/08 | 30177 | 3G020 | (Light out) | 3-19-08 chris ashton repaired pole #30177 (tl/pc) complete | High Pressure Sodium | 38.92608314000 | -77.07307216000
3/18/08 | 487847 | 2 | WESTMORELAND CIR | NW | 4/23/08 | 34380 | 3M038 | (Light out) | 3-19-08 chris ashton -- refer to ddot -- defective 250 mv fixture 4/22/08 There are 5-6 lights, we need a pole #.-Cooper & Patterson. | Mercury Vapor | 38.94941039000 | -77.10097492000
3/18/08 | 487740 | 0 | WISCONSIN AVE | NW | 3/19/08 | 37009 | 3G114 | (Light dim) | 3-19-08 chris ashton - previously repaired | High Pressure Sodium | 38.91709887000 | -77.06871738000
3/17/08 | 487708 | 2730 | WISCONSIN AVE | NW | 3/18/08 | 30177 | 3G020 | (Light out) | LIGHT ON CORNER OF WISCONSIN AND FULTON - 3-18-08 Ron Waites -----repaired | High Pressure Sodium | 38.92608314000 | -77.07307216000
3/17/08 | 487702 | 2730 | WISCONSIN AVE | NW | 3/18/08 | 30177 | 3G020 | (Light out) | NEXT TO COVERED BUS STOP - 3-18-08 Ron Waites -----repaired | High Pressure Sodium | 38.92608314000 | -77.07307216000
3/15/08 | 487016 | 5234 | ILLINOIS AVE | NW | 3/18/08 | 4M218 | 4M219 | (Light out) | 3-18-08 roger warren repaired pole #4m218 (400 hps bulb) complete FRONT - burned out | High Pressure Sodium | 38.95403959000 | -77.02615775000
3/14/08 | 486467 | 0 | FLORIDA AVE | NE | 3/15/08 | 54443 | 5M132 | (Light out) | 3-15-08 gary hicks repaired pole #54443 (400 hps bulb) complete | High Pressure Sodium | 38.90877588000 | -77.00407804000
3/13/08 | 485811 | 841 | 7TH ST | NW | 3/14/08 | 22422 | 6M662 | (Light out) | 3-14-08 DA duplicate ticket to wo #485810 no hansen # | High Pressure Sodium | 38.90021373000 | -77.02201497000
3/13/08 | 485810 | 841 | 7TH ST | NW | 3/14/08 | 22422 | 6M662 | (Light off/on) | 3-14-08 kevin hollins repaired pole #22422 (400 hps bulb) complete | High Pressure Sodium | 38.90021373000 | -77.02201497000
3/13/08 | 485757 | 0 | I ST | NW | 3/14/08 | 22487 | 2G985 | (Light out) | 3-14-08 kevin hollins repaired pole #22487 (400 hps bulb) complete | High Pressure Sodium | 38.90081220000 | -77.02379981000
3/13/08 | 485721 | 2201 | 22ND ST | NW | 3/15/08 | 24267 | 2A050 | (Light out) | 3-15-08 kevin hollins repaired pole #24267 (150 hps bulb, starter, tl/pc) complete | High Pressure Sodium | 38.91165726000 | -77.04875185000
3/13/08 | 486384 | 3925 | GEORGIA AVE | NW | 3/17/08 | 4J343 | 4G263 | (Light out) | FRONT - the light out ....metal pole 3-17-08 R.Waites-----repaired | High Pressure Sodium | 38.93923518000 | -77.02471809000
3/13/08 | 485696 | 2407 | 18TH ST | NW | 3/14/08 | 11533 | 1G491 | (Light off/on) | 3-14-08 chris ashton repaired pole #11533 (400 hps bulb) complete | High Pressure Sodium | 38.92063969000 | -77.04213470000
3/13/08 | 485694 | 711 | D ST | NW | 3/14/08 | 60088 | 2M325 | (Light out) | 3-14-08 tim richards repaired pole #60088 (400 hps bulb) complete | High Pressure Sodium | 38.89485723000 | -77.02246234000
3/13/08 | 485674 | 20 | I ST | SE | 3/13/08 | 67458 | 6A043 | (Light out) | NorthWest corner of intersection at I Street and Half Street West Bound of intersection at I Street and Half Street 3-13-08 I.Paraway-----stadium light | High Pressure Sodium | 38.87938129000 | -77.00840474000
3/12/08 | 485042 | 4500 | ROCK CREEK CHURCH RD | NE | 3/17/08 | 4R757 | 4A798 | (Light out) | 3-17-08 R.Waites-----repaired | High Pressure Sodium | 38.94697525000 | -77.00871139000
3/12/08 | 485041 | 815 | KENNEDY ST | NW | 3/13/08 | 4M078 | 4M078DC | (Light out) | 3-13-08 roger warren repaired pole #4M078 (400 hps bulb) complete | High Pressure Sodium | 38.95637067000 | -77.02492280000
3/12/08 | 485581 | 3460 | 14TH ST | NW |  | 13803 | 1G084 | (Light out) | 3-14-08 gary hicks light out due to construction pole #'s 13904, 13586, 13803, 13804, 13592, & 13681 Marriottsville consruction llc. 202-722-7228 - 301-657-0700 the street lights are on metal poles and there are several out between meridian pl and ne | High Pressure Sodium | 38.93314624000 | -77.03283352000
3/12/08 | 485589 | 1101 | L ST | NW | 3/19/08 | 25942 | 2M218 | (Light out) | 3-19-08 kevin holins completed w/ tl/pc 3-14-08 kevin hollins pole #25942 N/ C underground - refer to fault crew SOUTHEAST CORNER OF INTERSECTION - | High Pressure Sodium | 38.90408908000 | -77.02717553000
3/12/08 | 484920 | 7051 | SPRING PL | NW | 3/14/08 | 4H523DC | 4H523 | (Light out) | 3-14-08 Joe Caetto------repaired | Incandescent | 38.97594098000 | -77.01865986000
3/12/08 | 484919 | 7051 | SPRING PL | NW | 3/14/08 | 4H522DC | 4H522 | (Light out) | 3-14-08 Joe Caetto------repaired | Incandescent | 38.97614004000 | -77.01896257000
3/12/08 | 484862 | 0 | 3RD ST | NW | 3/12/08 | 59991 | 5A184 | (Light out) | 3-12-08 gary hicks repaired pole #59991 (400 hps bulb) complete | High Pressure Sodium | 38.91407956000 | -77.01569433000
3/12/08 | 484861 | 0 | EAST CAPITOL ST | NE | 3/18/08 | 63629 | 6M837 | (Light out) | Jeramiah 3/18/08, made splices in manhole.energized 5 lights. closed by K. greenfield | High Pressure Sodium | 38.88956256000 | -76.97418443000
3/11/08 | 484239 | 4878 | NANNIE HELEN BURROUGHS AVE | NE | 3/12/08 | 71291DC | 7A221DC | (Light out) | 3-12-08 darryl hooker repaired pole #71291dc (250 hps bulb, fixture, tl/pc) complete | High Pressure Sodium | 38.89881397000 | -76.93206898000
3/11/08 | 484231 | 4500 | SHERIDAN RD | SE | 3/14/08 | 81359DC | 8U644 | (Light out) | 3-12-08 darryl hooker repaired pole #81359dc (N/C to overhead ) refer to overhead crews | High Pressure Sodium | 38.85817131000 | -76.99317521000
3/10/08 | 483601 | 501 | H ST | NW | 3/13/08 | 60579 | 6S547 | (Light out) | 3-13-08 tim richards - light found okay Al Young said current in the T-base. 3-11-08 tim richards pole #60579 N/C underground refer to fault crew | High Pressure Sodium | 38.90013088000 | -77.01901668000
3/10/08 | 483533 | 811 | 4TH ST | NW | 2/6/12 | 60449 | 6S463 | (Light out) | 3/11/08, DUPLICATE to wo#474612, 474618, 474619, & 474617. New poles being installed by out side contractor Ft, Meyer) refer to DDot. | High Pressure Sodium | 38.90088288000 | -77.01610076000
3/9/08 | 483495 | 1101 | L ST | NW | 3/10/08 | 25942 | 2M218 | (Light out) | 3-10-08 J Caetto Installed 400w hps lamp, TLPC STREET(THE INTERSECTION IS 11TH STREET AND MASSACHUSTTS AVE N.W.) - caller reporting that there is a streetlight at this location it's on a wooden pole. | High Pressure Sodium | 38.90408908000 | -77.02717553000
3/8/08 | 483406 | 0 | KENILWORTH AVE | NE | 3/8/08 | 70312 | 7M068 | (Light out) | 3-8-08 darryl hooker repaired pole #70312 (400 hps bulb) complete | High Pressure Sodium | 38.90602198000 | -76.93999660000
| 483383 | 1801 | P ST | NW | 3/10/08 | 26339 | 2M169 | (Light out) | -3-10--08 J Caetto Installed 1-400w hps lamp 3-10-08 P Harvin Found ok northwest corner metal pole, req to be repaired | High Pressure Sodium | 38.90971066000 | -77.04178765000
3/7/08 | 482935 | 0 | P ST | NE | 3/8/08 | 57340 | 5M093 | (Light out) | 3-8-08 steve white repaired pole #57340 (400 hps bulb) complete | High Pressure Sodium | 38.90964250000 | -77.00656798000
3/7/08 | 482883 | 5700 | CHILLUM PL | NE | 3/12/08 | 4P516DC | 4U174 | (Light out) | - 3-12-08 roger warren repaired pole #4p516dc (400hps bulb, powerdoor, tl/pc) complete 3-11-08 J Caetto Needs a new fixture 3-09-08 R Waites SEE COMMENTS BELOW..... 3-07-08 R Waites Need a new 400w hps fixture Side of 400 Chillum Place | High Pressure Sodium | 38.95893594000 | -77.00160441000
3/7/08 | 482822 | 1100 | 2ND ST | SE | 3/10/08 | 68135 | 6A409 | (Light out) |  | High Pressure Sodium | 38.87682972000 | -77.00287771000
3/7/08 | 482821 | 2516 | SOUTH DAKOTA AVE | NE | 3/7/08 | 57943DC | 5M212DC | (Light out) | 3-7-08 steve white repaired pole #57943dc (400 hps bulb) complete | High Pressure Sodium | 38.92434283000 | -76.96409029000
3/7/08 | 482332 | 0 | NEW YORK AVE | NE | 3/13/08 | 50001 | 5A035 | (Light out) | 3-13-08 complete (400 hps bulb) 3-13-08 gary hicks - bucket truck wont reach need big boom truck 3-11-08 tim richards pole #50001- needs big boom 3-09-08 L Roberto NEED MOT 3-07-08 P Harvin Need MOT Opposite to 2420 New York Avenue On Median | High Pressure Sodium | 38.91733557000 | -76.97140198000
3/7/08 | 482327 | 2327 | 33RD ST | SE | 3/7/08 | 74832DC | 7A095DC | (Light out) | 3-6-08 darryl hooker repaired pole #74832dc (250 hps bulb) complete | High Pressure Sodium | 38.86054874000 | -76.96053965000
3/6/08 | 482867 | 0 | WISCONSIN AVE | NW | 3/8/08 | 38777 | 3U421 | (Light out) | 3-8-08 chris ashton repaired pole #38777 (400 hps bulb) complete INTERSECTION ON THE SOUTHWEST CORNER - medal pole lightbulb out requesting to have repaired | High Pressure Sodium | 38.93458612000 | -77.07231604000
3/6/08 | 482284 | 900 | NEW JERSEY AVE | SE | 3/7/08 | 67472 | 6A060 | (Light out) | 3-7-08 tim richards repaired pole #67472 (400 hps bulb) complete | High Pressure Sodium | 38.87881747000 | -77.00509329000
3/5/08 | 481725 | 0 | 13TH ST | NW | 3/6/08 | 4K425 | 4U138 | (Light out) | 3-6-08 roger warren repaired pole #4k425 (400 hps bulb) complete | High Pressure Sodium | 38.94497938000 | -77.02978632000
3/5/08 | 481724 | 4514 | 13TH ST | NW | 3/6/08 | 4K422 | 4U131 | (Light out) | 3-6-08 roger warren peviously repaired | High Pressure Sodium | 38.94571765000 | -77.02978404000
3/5/08 | 481717 | 1100 | 11TH ST | SE | 3/7/08 | 67614 | 6L993 | (Light out) | 3-6-08 tim richared checked pole #67614 light found okay 3-06-08M Craig Found ok | High Pressure Sodium | 38.87689854000 | -76.99165831000
3/5/08 | 481707 | 131 | M ST | NE | 3/10/08 | 62267 | 6S353 | (Light out) | 3-6-08 tim richards pole #62267 N/C underground - duplicate to wo #448069 | High Pressure Sodium | 38.90559717000 | -77.00496490000
3/5/08 | 481688 | 0 | 9TH ST | NW | 3/7/08 | 25437 | 2L558 | (Light out) | 3-7-08 kevin hollins pole #25437 light found okay | High Pressure Sodium | 38.90380790000 | -77.02408338000
3/5/08 | 481679 | 2 | L ST | NE | 3/6/08 | 61201 | 6A240 | (Light out) | 3-6-08 tim richards repaired pole #61201 (400 hps bulb) complete | High Pressure Sodium | 38.90378899000 | -77.00858856000
3/5/08 | 481663 | 2407 | 18TH ST | NW | 3/7/08 | 11533 | 1G491 | (Light out) | 3-7-08 roger warren repaired pole #11533 (rewired pole, 400 hps bulb, fixture, tl/pc ) complete | High Pressure Sodium | 38.92063969000 | -77.04213470000
3/5/08 | 481651 | 1100 | 11TH ST | SE | 3/6/08 | 67614 | 6L993 | (Light off/on) | 3-06-08 J Peck Installed 400w hps lamp | High Pressure Sodium | 38.87689854000 | -76.99165831000
3/5/08 | 481649 | 1300 | MAINE AVE | SW | 3/6/08 | 66531 | 6M443 | (Light out) | 3-06-08 L Roberto Installed 1-400w hps lamp, TLPC | High Pressure Sodium | 38.88186010000 | -77.02828319000
3/5/08 | 481205 | 0 | 13TH ST | NW | 3/5/08 | 4K432 | 4U146 | (Light out) | 3-5-08 roger warren repaired pole #4k432 (400 hps bulb, tl/pc) complete | High Pressure Sodium | 38.94308499000 | -77.02978871000
3/5/08 | 481204 | 5127 | NANNIE HELEN BURROUGHS AVE | NE | 3/5/08 | 71269 | 7A201 | (Light out) | 3-5-08 darryl hooker repaired pole #71269 (400 hps bulb) complete | High Pressure Sodium | 38.89826963000 | -76.92624974000
3/4/08 | 481194 | 0 | MONROE ST | NE | 3/6/08 | 56170DC | 5U699 | (Light out) | Side of 4204 13th Place 3-6-08 steve white repaired pole #56170dc (100 hps bulb) complete | High Pressure Sodium | 38.93208411000 | -76.99624768000
3/4/08 | 481615 | 0 | 2ND ST | NE |  | 61291 | 6S307 | (Light out) | 3/11/08 O. Taylor old ploes terminated by ft. Meyer, new ploes being installed. Refer to DDot. FRONT - 3-5-08 tim richards pole #61291 N/C underground - duplicate to wo #474410 metal pole burnt out bulb needs to be repaired | High Pressure Sodium | 38.90340904000 | -77.00350095000
3/4/08 | 481129 | 2328 | 36TH ST | SE | 3/5/08 | 74819DC | 7A083DC | (Light out) | Northeast corner of intersection at Bangor Street and 36th Street Address #3600 3-5-08 darryl hooker repaired pole #74819dc (250 hps bulb, tl/pc) complete | High Pressure Sodium | 38.86055239000 | -76.95626725000
3/4/08 | 481125 | 3960 | PENNSYLVANIA AVE | SE | 3/5/08 | 78580DC | 7E006DC | (Light out) | Front of 3960 Pennsylvania Avenue 3-5-08 darryl hooker repaired pole #78580dc (400 hps bulb) complete | High Pressure Sodium | 38.86466564000 | -76.94882256000
3/4/08 | 481048 | 425 | MASSACHUSETTS AVE | NW | 2/6/12 | 60482 | 6A192 | (Light out) | M. Barnes 3/5/08, new poles being installed by out side contractor, refer to DDOT. 3-4-08 tim richards pole #60482 N/C underground refer to fault crew | Mercury Vapor | 38.90049835000 | -77.01683728000
3/4/08 | 480471 | 00 | INDEPENDENCE AVE | SE | 3/10/08 | 63662 | 6M839 | (Light out) | 3-10-08 - Lights are on Temporary until wire pulled East Bound from 1901 Independence Avenue 3-4-08 tim richards - N/C underground - pole #63662 refer to fault crew - duplocate ticket to wo #458023 | High Pressure Sodium | 38.88775642000 | -76.97553609000
3/4/08 | 480470 | 2034 | INDEPENDENCE AVE | SE | 3/10/08 | 63661 | 6M840 | (Light out) | 3-10-08 - Lights are on Temporary until wire pulled East Bound from 1901 Independence Avenue 3-4-08 tim richards - pole #63661 - N/C underground - duplicate to wo #474426 | High Pressure Sodium | 38.88776077000 | -76.97613660000
3/1/08 | 479850 | 5350 | C ST | SE | 3/1/08 | 75596 | 75596DC | (Light out) | 3-1-08 darryl hooker repaired pole #75596 (295 inc. bulb) complete | Incandescent | 38.88422223000 | -76.92507148000
2/29/08 | 479835 | 800 | 12TH ST | NE | 2/29/08 | 62461 | 6S167 | (Light out) | 2-29-08 tim richards repaired pole #62461 (400 hps bulb, 400 hps kit) complete | High Pressure Sodium | 38.90029932000 | -76.99009243000
2/29/08 | 479832 | 800 | 8TH ST | NW | 3/4/08 | 22969 | 2M383 | (Light out) | 3-4-08 kevin hollins repaired pole #22969 (400 hps bulb) complete | High Pressure Sodium | 38.90023907000 | -77.02300991000
2/29/08 | 479802 | 1231 | NEW YORK AVE | NE | 2/29/08 | 56828 | 5M064 | (Light out) | 2-29-08 tim richards repaired pole #56828 (tl/pc) complete | High Pressure Sodium | 38.91402868000 | -76.98949773000
2/29/08 | 479794 | 711 | D ST | NW | 2/29/08 | 60088 | 2M325 | (Light out) |  | High Pressure Sodium | 38.89485723000 | -77.02246234000
2/29/08 | 479793 | 711 | D ST | NW | 3/1/08 | 60088 | 2M325 | (Light out) | Front of 709 D Street 3-1-08 tim richards repaired pole #60088 (400 hps bulb) complete | High Pressure Sodium | 38.89485723000 | -77.02246234000
2/28/08 | 479247 | 900 | NEW JERSEY AVE | SE | 2/29/08 | 67472 | 6A060 | (Light out) | 2-29-08 J Peck Installed 400w hps lamp North bound of intersection at New Jersey Avenue and K Street | High Pressure Sodium | 38.87881747000 | -77.00509329000
2/28/08 | 479246 | 1100 | 2ND ST | SE | 3/4/08 | 68135 | 6A409 | (Light out) | North bound of intersection at 2nd Street and M Street Block #1100 3-4-08 tim richards repaired pole #68135 (reconnected neturial) complete | High Pressure Sodium | 38.87682972000 | -77.00287771000
2/28/08 | 479202 | 2212 | I ST | NW | 2/29/08 | 28105 | 2A226 | (Light out) | Front of 2212 I Street. 2-29-08 kevin hollins previously repaired 2-27-28 | High Pressure Sodium | 38.90064109000 | -77.04925896000
2/28/08 | 479200 | 0 | 7TH ST | NW | 2/29/08 | 22410 | 6M686 | (Light out) | On 7th Street. 2 Poles South of intersection at 7th Street and K Street. Block #900 | High Pressure Sodium | 38.90182112000 | -77.02201817000
2/28/08 | 479184 | 1231 | NEW YORK AVE | NE | 2/28/08 | 56828 | 5M064 | (Light out) | 2-28-08 tim richards repaired pole #56828 ( tl/pc) complete | High Pressure Sodium | 38.91402868000 | -76.98949773000
2/28/08 | 479177 | 2 | L ST | NE | 2/28/08 | 61201 | 6A240 | (Light out) | 2-28-08 tim richards repaired pole #61201 (tl/pc) complete | High Pressure Sodium | 38.90378899000 | -77.00858856000
2/28/08 | 479174 | 0 | O ST | NE | 2/28/08 | 62315 | 5M112 | (Light out) | 2-28-08 tim richards repaired pole #62315 (250 hps bulb) complete | High Pressure Sodium | 38.90852270000 | -77.00482604000
2/28/08 | 479172 | 0 | O ST | NE | 2/28/08 | 62314 | 5M113 | (Light out) | 2-28-08 DA duplicate ticket to wo #475280 hansen #1717441 | High Pressure Sodium | 38.90852329000 | -77.00447657000
2/28/08 | 479170 | 0 | 1ST ST | NE | 2/28/08 | 61248 | 6A282 | (Light out) | 2-28-08 DA duplicate N/C underground to WO #404559 no hansen # | High Pressure Sodium | 38.90791176000 | -77.00580646000
2/28/08 | 478607 | 0 | MASSACHUSETTS AVE | NW | 2/28/08 | 25964 | 2G953 | (Light out) | 2-28-08 kevin hollins repaired pole #25964 (250 hps bulb, 250 hps fixture, tl/pc) complete | High Pressure Sodium | 38.90320032000 | -77.02510725000
2/28/08 | 478605 | 0 | C ST | SW | 3/6/08 | 21748 | 6A386 | (Light out) | 3-6-08 chris ashton repaired pole #21748 (400 mv bulb) complete 3-5-08 kevin hollins - request for map Northwest corner of intersection at Washington Avenue and C Street. Combo Pole. On island at intersection. | High Pressure Sodium | 38.88607059000 | -77.01250580000
2/27/08 | 479157 | 740 | 6TH ST | NW | 11/20/08 | 22513 | 6S425 | (Light out) | M. Barnes 3/4/08 new poles being installed by out side contractor refer to DDot. - 2-29-08 kevin hollins N/C underground refer to fault crew duplicate ticket to wo #404538 street light on a metal pole is out D.MOORE-PASSED 03/04/08 | High Pressure Sodium | 38.89950950000 | -77.02001122000
2/27/08 | 478570 | 4520 | HOBAN RD | NW | 2/28/08 | 35822DC | 35822 | (Light out) | 2-28-08 chris ashton repaired pole #35822dc (295 inc. bulb) complete | Incandescent | 38.91433459000 | -77.08526855000
2/27/08 | 479151 | 3221 | CONNECTICUT AVE | NW | 3/4/08 | 30101 | 30423 | (Light out) | Al. Young 3/4/08, new poles being installed by out side contractor, refer to DDot 2-29-08 chris ashton pole #30101 N/C underground - refer to fault crew 2-28-08 R Waites REFER to Night Crew (no pole#/address) CONNECTICUT AVENUE AVENUE NW AND DE | High Pressure Sodium | 38.93328522000 | -77.05704960000
2/26/08 | 478511 | 0 | BANGOR ST | SE | 2/27/08 | 74833DC | 7A096DC | (Light out) | 2-27-08 L Roberto Installed 1-400w hps lamp, TL FRONT - METAL STREET LIGHT HAS BEEN OUT FOR TWO DAYS | High Pressure Sodium | 38.86055117000 | -76.96088105000
2/26/08 | 477958 | 1101 | L ST | NW | 2/26/08 | 25942 | 2M218 | (Light out) | 2-26-08 kevin hollins repaired pole #25942 | High Pressure Sodium | 38.90408908000 | -77.02717553000
2/26/08 | 477308 | 2001 | 20TH ST | NW | 2/26/08 | 23846 | 2A072 | (Light out) | 2-26-08 kevin hollins repaired pole #23846 (400 hps bulb) | High Pressure Sodium | 38.90640579000 | -77.04498110000
2/25/08 | 477232 | 0 | NEWARK ST | NW | 2/27/08 | 38996DC | 3U390 | (Light out) | 2-27-08 chris ashton pole #38996dc previously repaired | High Pressure Sodium | 38.93457016000 | -77.07268024000
2/23/08 | 477121 | 0 | WISCONSIN AVE | NW | 2/24/08 | 30135 | 3G009 | (Light out) | - 2-24-08 J Peck Installed 1-400w hps lamp street light out on a wooden pole | High Pressure Sodium | 38.92744531000 | -77.07330577000
2/22/08 | 476677 | 1770 | BENNING RD | NE | 2/25/08 | 63615 | 6M778 | (Light out) | 2-25-08 L Roberto Installed 1-400w hps lamp, TL W/S 17TH STREET, NW 1ST POLE N/O K ST | High Pressure Sodium | 38.89907267000 | -76.97811088000
2/22/08 | 476666 | 470 | K ST | NW | 2/22/08 | 60468 | 6A112 | (Light out) | 2-22-08 kevin hollins repaired pole #60468 | High Pressure Sodium | 38.90245480000 | -77.01835493000
2/22/08 | 476602 | 1000 | L ST | SE | 2/22/08 | 67686 | 67685 | (Light out) | 2-22-08 DA duplicate ticket to wo #464765 no hansen # 2-2-08 tim richards pole #67686 N/C underground refer to fault crew | High Pressure Sodium | 38.87758833000 | -77.00607638000
2/22/08 | 476154 | 0 | NEWARK ST | NW | 2/22/08 | 38996DC | 3U390 | (Light out) | 2-22-08 chris ashton repaired pole #38996dc | High Pressure Sodium | 38.93457016000 | -77.07268024000
2/21/08 | 476112 | 703 | 49TH ST | NE | 3/2/08 | 71285DC | 7A218 | (No current) | 3-02-08 D Smith/Kates/Gray Installed 30ft of #10 cable & made 2 taps - Overhead span down from 71285DC to 71286. Pole is on NEC need feed from NWC (NOTE): New wooden poles put up. This light was cut fron triplex and nevertapped back in | High Pressure Sodium | 38.89869349000 | -76.93152778000
2/21/08 | 476081 | 0 | EAST CAPITOL ST | NE | 2/21/08 | 63620 | 6M830 | (Light out) | 2-21-08 TIM RICHARDS REPAIRED POLE #63620 | High Pressure Sodium | 38.88980872000 | -76.97668782000
2/21/08 | 476062 | 800 | I ST | SE | 11/20/08 | 67465 | 6A037 | (Light out) | AL Young 2/26/08, pole located in construction site no access , refer to DDot. 2-22-08 tim richards pole #67465 N/C undrground refer to fault crew (no wires in pole ) | High Pressure Sodium | 38.87938166000 | -77.00538347000
2/21/08 | 476061 | 301 | K ST | SE | 2/22/08 | 67660 | 6A449 | (Light out) | 2-22-08 tim richards repaired pole #67660 | High Pressure Sodium | 38.87835619000 | -77.00175680000
2/21/08 | 476057 | 826 | 2ND ST | NE | 2/22/08 | 61300 | 6S290 | (Light out) | 2-22-08 tim richards pole #61300 N/C underground 2-22-08 DA duplicat ticket to wo #474368 and hansen #1715704 | High Pressure Sodium | 38.90069257000 | -77.00363545000
2/21/08 | 476056 | 0 | 2ND ST | NE | 2/22/08 | 62318 | 6S295 | (Light out) | 2-22-08 DA duplicate ticket to wo #474408 no hansen # | High Pressure Sodium | 38.90121715000 | -77.00349984000
2/21/08 | 476055 | 911 | 2ND ST | NE | 2/22/08 | 61296 | 6S298 | (Light out) | 2-22-08 tim richards repaired pole #61296 | High Pressure Sodium | 38.90176798000 | -77.00363405000
2/21/08 | 476054 | 131 | M ST | NE | 2/22/08 | 62270 | 6S343 | (Light out) | 2-22-08 DA dupliate ticket to wo #474420 no hansen # | High Pressure Sodium | 38.90570496000 | -77.00395113000
2/21/08 | 476053 | 131 | M ST | NE | 2/22/08 | 62269 | 6S356 | (Light out) | 2-22-08 DA duplicate ticket to wo #474420 no hansen # | High Pressure Sodium | 38.90559826000 | -77.00432213000
2/21/08 | 476052 | 131 | M ST | NE | 2/22/08 | 62268 | 6S346 | (Light out) | 2-22-08 DA duplicate ticket refer to wo #474420 no hansen # | High Pressure Sodium | 38.90570457000 | -77.00451927000
2/21/08 | 476051 | 131 | M ST | NE | 2/22/08 | 62267 | 6S353 | (Light out) | 2-22-08 DA duplicate ticket refer to wo #474420 no hansen # | High Pressure Sodium | 38.90559717000 | -77.00496490000
2/21/08 | 476050 | 0 | 1ST ST | NE | 2/25/08 | 61248 | 6A282 | (Light out) | 2-25-08 L Roberto Installed 2-250w hps lamps, 2-TLPC on two poles | High Pressure Sodium | 38.90791176000 | -77.00580646000
2/21/08 | 476049 | 33 | PATTERSON ST | NE | 2/24/08 | 61267 | 6U241 | (Light out) | 2-24-08 D Smith Installed 1-250 hps lamp, TLPC 2-23-08 tim richards pole #61267 light is on street in front of a club - can not get to light due to the crowd -- REFER TO DAY CREW | High Pressure Sodium | 38.90640945000 | -77.00861364000
2/21/08 | 476647 | 2313 | WISCONSIN AVE | NW | 2/24/08 | 30164 | 3G074 | (Light out) | 2-24-08 J Peck Installed 1-400w hps lamp FRONT - metal street light is always on. street light has a DO NOT ENTER SIGN ON IT. | High Pressure Sodium | 38.92075726000 | -77.07170014000
2/21/08 | 476042 | 0 | 7TH ST | NW | 2/25/08 | 22452 | 6M651 | (Light out) | 2-25-08 kevin hollins light was repaired last week 2-24-08 w Kates Found ok | High Pressure Sodium | 38.89955549000 | -77.02182020000
2/21/08 | 476040 | 0 | 7TH ST | NW | 2/26/08 | 22452 | 6M651 | (Light out) | 2--26-08 O Taylor Installed 1-NWPC Specialty Light China Town 2-24-08 w Kates Found ok watchman hole should be re-drilled to face down, light reflecting off of big screen t.v.'s and other streetlights. | High Pressure Sodium | 38.89955549000 | -77.02182020000
2/21/08 | 476634 | 1200 | CONNECTICUT AVE | NW | 2/26/08 | 27221 | 2U530 | (Light out) | 2-26-08 kevin hollins all lights found okay 2-24-08 w Kates Found ok CONNECTICUT AVENUE NW AND M STREET NW, WASHINGTON, DC SEC CONNECTICUT AVENUE/ M STREET ON CONN. AVE ON THE CORNER - | High Pressure Sodium | 38.90584530000 | -77.04105305000
2/20/08 | 475340 | 2412 | WISCONSIN AVE | NW | 2/21/08 | 30166 | 3G066 | (Light out) | 2-21-08 chris ashton installed 400 hps bulb, pole #30166 | High Pressure Sodium | 38.92154388000 | -77.07218059000
2/20/08 | 475328 | 0 | H ST | NW | 2/20/08 | 22573 | 2M430 | (Light out) | 2-20-08 kevin hollins repaired pole #22573 | High Pressure Sodium | 38.89973534000 | -77.02361844000
2/20/08 | 475323 | 0 | 9TH ST | NW | 2/20/08 | 25437 | 2L558 | (Light out) | 2-20-08 kevin hollins repaired pole #25437 | High Pressure Sodium | 38.90380790000 | -77.02408338000
2/20/08 | 474612 | 811 | 4TH ST | NW |  | 60449 | 6S463 | (Light out) | H. Lancaster, 2/25/08, WO#474612 ,474618, 474617, are all part of the same, new poles being installed by out side contractor, refer to DDot. wrong address, same pole # 60449 as wo#474618, were new pole are being installed. | High Pressure Sodium | 38.90088288000 | -77.01610076000
2/19/08 | 474587 | 0 | 23RD ST | NW | 2/19/08 | 28345 | 2M285 | (Light out) |  | High Pressure Sodium | 38.90189255000 | -77.05000095000
2/19/08 | 474577 | 0 | 14TH ST | NW |  | 12073 | 1G564 | (Light out) | H lancaster 2/26/08 pole located behind fenced construction site can not access, refer to DDOT. D.MOORE--PASSED 02/26/08 | High Pressure Sodium | 38.92089953000 | -77.03174747000
2/19/08 | 474574 | 0 | 13TH ST | NW | 2/21/08 | 4K432 | 4U146 | (Light off/on) | 2-21-08 roger warren repaired pole #4K432 | High Pressure Sodium | 38.94308499000 | -77.02978871000
2/19/08 | 474573 | 4514 | 13TH ST | NW | 2/21/08 | 4K422 | 4U131 | (Light out) | 2-21-08 roger warren repaired pole #4K422 | High Pressure Sodium | 38.94571765000 | -77.02978404000
2/19/08 | 475280 | 0 | O ST | NE | 2/6/12 | 62314 | 5M113 | (Light out) | O. TAYLOR 2/27/08, REFER TO PEPCO NO FEED IN MH. INTERSECTION - street light out on a metal pole 2-23-08 tim richards pole #62314 N/C underground refer to fault crew | High Pressure Sodium | 38.90852329000 | -77.00447657000
2/18/08 | 474428 | 00 | INDEPENDENCE AVE | SE | 4/15/08 | 63662 | 6M839 | (Light out) | 2/20 - Duplicate w/458023 - J Bateman 2-19-08 tim richards pole #63662 N/C underground | High Pressure Sodium | 38.88775642000 | -76.97553609000
2/18/08 | 474426 | 2034 | INDEPENDENCE AVE | SE | 3/13/08 | 63661 | 6M840 | (Light out) | Affiliated w/458023 2-19-08 tim richards pole #63661 N/C underground | High Pressure Sodium | 38.88776077000 | -76.97613660000
2/18/08 | 474421 | 131 | M ST | NE | 11/20/08 | 62267 | 6S353 | (Light out) | M. Barnes 2/21/08, New poles being installed by out side conractor , old poles deactivated. Refer to DDOT. 2-19-08 roger warren pole #62267 N/C underground | High Pressure Sodium | 38.90559717000 | -77.00496490000
2/18/08 | 474420 | 131 | M ST | NE | 3/10/08 | 62268 | 6S346 | (Light out) | 2-19-08 roger warren pole #62268 N/C underground | High Pressure Sodium | 38.90570457000 | -77.00451927000
2/18/08 | 474418 | 131 | M ST | NE | 3/10/08 | 62269 | 6S356 | (Light out) | 2-19-08 roger warren pole #62269 N/C underground | High Pressure Sodium | 38.90559826000 | -77.00432213000
2/18/08 | 474417 | 2010 | 48TH ST | NW | 2/20/08 | 35371DC | 3E028 | (Light out) | 2-20-08 chris ashton repaired pole #35371dc | Incandescent | 38.91732328000 | -77.09428336000
2/18/08 | 474416 | 131 | M ST | NE | 3/13/08 | 62270 | 6S343 | (Light out) | 2-19-08 roger warren pole #62270-62268-62269 | High Pressure Sodium | 38.90570496000 | -77.00395113000
2/18/08 | 474415 | 0 | DELAWARE AVE | NE | 2/21/08 | 61286 | 6S317 | (Light out) | 2-20-08 tim richars road blocked off 2-19-08 roger warren - road blocked off | High Pressure Sodium | 38.90515180000 | -77.00317119000
2/18/08 | 474413 | 1299 | DELAWARE AVE | NE | 2/21/08 | 61287 | 6S315 | (Light out) | 2-20-08 tim richards road blocked 2-19-08 roger warren - road blocked off | High Pressure Sodium | 38.90477566000 | -77.00330616000
2/18/08 | 474411 | 1101 | 2ND ST | NE | 2/19/08 | 61290 | 6S309 | (Light out) | 2-19-08 roger warren repaired pole #61290 | High Pressure Sodium | 38.90386136000 | -77.00350103000
2/18/08 | 474408 | 0 | 2ND ST | NE | 2/6/12 | 62318 | 6S295 | (Light out) | 3-11-08 H Lancaster broken duct 17ft away from pole wires were cut apparently by Ft Myer that were pulled from old pole, refer to DDot. 2-19-08 roger warren - pole #62318 N/C underground | High Pressure Sodium | 38.90121715000 | -77.00349984000
2/18/08 | 474407 | 0 | 2ND ST | NE | 2/19/08 | 62317 | 6S293 | (Light out) | 2-19-08 roger warren light found okay pole #62317 | High Pressure Sodium | 38.90103982000 | -77.00349769000
2/18/08 | 474406 | 600 | 2ND ST | NE | 11/20/08 | 61306 | 6S276 | (Light out) | 3/11/08 W. Kates, new poles being installed by Ft, Meyer. Refer to DDot. 2-19-08 roger warren pole #61306 N/C underground | High Pressure Sodium | 38.89832767000 | -77.00344709000
2/18/08 | 474384 | 2730 | WISCONSIN AVE | NW | 2/19/08 | 30177 | 3G020 | (Light out) | 2-19-08 R Waites Installed TLPC | High Pressure Sodium | 38.92608314000 | -77.07307216000
2/18/08 | 474381 | 2412 | WISCONSIN AVE | NW | 2/22/08 | 30166 | 3G066 | (Light out) | 2-22-08 chris ashton pole # 30166 repaired on 2-20-08 | High Pressure Sodium | 38.92154388000 | -77.07218059000
2/18/08 | 474534 | 2318 | 32ND ST | SE | 2/19/08 | 74838DC | 7A102DC | (Light out) | - 2-19-08 M Tomlin Installed 250 hps lamp medal pole street light is out | High Pressure Sodium | 38.86110733000 | -76.96087329000
2/16/08 | 474368 | 826 | 2ND ST | NE | 4/11/08 | 61300 | 6S290 | (Light out) | IN THE MIDDLE OF BLOCK - metale pole streetlight is out 2-19-08 roger warren pole #61300 N/C underground | High Pressure Sodium | 38.90069257000 | -77.00363545000
2/16/08 | 474205 | 470 | K ST | NW | 2/17/08 | 60468 | 6A112 | (Light out) | J.PECK--REPLACED 250 BULB 02/16/08 | High Pressure Sodium | 38.90245480000 | -77.01835493000
2/16/08 | 474201 | 425 | MASSACHUSETTS AVE | NW | 2/17/08 | 60482 | 6A192 | (Light out) | J.PECK--REPLACED 400 BULB 02/16/08 | Mercury Vapor | 38.90049835000 | -77.01683728000
2/16/08 | 474199 | 457 | MASSACHUSETTS AVE | NW | 2/17/08 | 60481 | 6A195 | (Light out) | J.PECK--REPLACED 400 BULB 02/16/08 | High Pressure Sodium | 38.90073307000 | -77.01753805000
2/16/08 | 474198 | 0 | K ST | NW | 2/19/08 | 22402 | 6A100 | (Light out) | 2-19-08 kevin hollins repaired pole #22402 | High Pressure Sodium | 38.90245268000 | -77.01971021000
2/16/08 | 473748 | 1801 | P ST | NW | 2/16/08 | 26339 | 2M169 | (Light out) | 2-16-08 kevin hollins repaired pole #26339 | High Pressure Sodium | 38.90971066000 | -77.04178765000
2/15/08 | 473656 | 0 | INTERSTATE 295 | SE | 2/15/08 | 86524 | 8L795 | (Light out) | 2-15-08 billy black repaired pole #86524 | High Pressure Sodium | 38.86954928000 | -76.98763482000
2/15/08 | 473258 | 0 | INTERSTATE 295 | SE | 2/15/08 | 86511 | 8L770 | (Light out) | 2-15-08 billy black install 400 hps lamp - pole #86511 | High Pressure Sodium | 38.86604296000 | -76.99135445000
2/14/08 | 473685 | 4128 | GEORGIA AVE | NW | 2/15/08 | 4J351 | 4G286 | (Light out) | 2-15-08 R Waites Installed 400w hps lamp FRONT - metal pole | High Pressure Sodium | 38.94108332000 | -77.02542772000
| 473701 | 1010 | MASSACHUSETTS AVE | NW | 12/10/08 | 25961 | 2M216 | (Light out) | K Greenfield, 3-10-08, Refer to Pepco. Need feed wire installed from man hole to Light Pole NW CORNER - light is out on metal pole 2-16-08 kevin hollins 5 lights pole #s 25961, 29203, 25269, 25274, and 29222 N/C underground D.MOORE--PASSED 02/26 | High Pressure Sodium | 38.90379985000 | -77.02690625000
2/14/08 | 473192 | 1101 | BRENTWOOD RD | NE | 2/14/08 | 56629 | 5A246 | (Light out) | 2-14-08 billy black repaired pole 56629 | High Pressure Sodium | 38.91961170000 | -76.99119145000
2/13/08 | 473153 | 1333 | NEW HAMPSHIRE AVE | NW | 2/16/08 | 24482 | 2G772 | (Light out) | DUPONT CIRCLE NW AND NEW HAMPSHIRE AVENUE NW, WASHINGTON, DC SEC DUPONT CIRCLE AND NEW HAMSPHIRE AVENUE ODD SIDE - | High Pressure Sodium | 38.90845645000 | -77.04444043000
2/13/08 | 473132 | 1331 | CONNECTICUT AVE | NW | 2/14/08 | 24528 | 2U495 | (Light out) | 2-14-08 D Webb Installed 400w hps lamp EVENSIDE - | High Pressure Sodium | 38.90805642000 | -77.04271948000
2/13/08 | 473105 | 808 | 17TH ST | NW | 2/15/08 | 23439 | 2A054 | (Light out) | ON17TH STREET SIDE - 2-15-08 kevin hollins repaired pole #23439 | High Pressure Sodium | 38.90076931000 | -77.03958440000
2/13/08 | 473102 | 1035 | CONNECTICUT AVE | NW | 2/14/08 | 27215 | 2G834 | (Light out) | 2-14-08 D Webb Installed 400w hps lamp ON CONNECTICUT AVENUE - | High Pressure Sodium | 38.90340940000 | -77.03964906000
2/12/08 | 472624 | 1710 | RHODE ISLAND AVE | NW | 2/14/08 | 26387 | 2U755 | (Light out) | 17TH STREET NW AND RHODE ISLAND AVENUE NW, WASHINGTON, DC ON THE SOUTH WEST CORNER - | High Pressure Sodium | 38.90636508000 | -77.03884760000
2/12/08 | 472622 | 1101 | CONNECTICUT AVE | NW | 2/14/08 | 27217 | 2U560 | (Light out) | ON CONNECTICUT AVENUE - 2-14-08 kevin hollins repaired pole #27217 | High Pressure Sodium | 38.90409324000 | -77.04001398000
2/11/08 | 471598 | 0 | SHERMAN AVE | NW | 2/17/08 | 14219 | 1G462 | (Light out) | 2-11-08 Pole# 14219 (Second pole north of Barry St NE) | High Pressure Sodium | 38.92198110000 | -77.02520587000
2/11/08 | 471572 | 0 | 14TH ST | NW |  | 12073 | 1G564 | (Light out) | O. Taylor 2/18/08, light pole inside construction area behind achain link fence with no access from road. | High Pressure Sodium | 38.92089953000 | -77.03174747000
2/11/08 | 471569 | 1901 | 4TH ST | NW | 2/16/08 | 14104 | 15049 | (Light out) | 2-16-08 chris ashton / bad address | High Pressure Sodium | 38.91602650000 | -77.01728653000
2/11/08 | 471568 | 0 | 4TH ST | NW | 2/12/08 | 14103 | 15100 | (Light out) | 2-12-08 chris miller pole 3141036 in process of being replaced | High Pressure Sodium | 38.91580855000 | -77.01738480000
2/11/08 | 471550 | 2407 | 18TH ST | NW | 2/12/08 | 11533 | 1G491 | (Light out) | 2-12-08 octavia taylor pole #11533 -- p/c housing on the back of lights needs to be replaced | High Pressure Sodium | 38.92063969000 | -77.04213470000
2/11/08 | 471542 | 0 | 14TH ST | NW | 2/13/08 | 14690 | 15019 | (Light out) | 2-13-08 Da - duplicate ticket to wo #471544 no hansen # 2-12-08 octavia taylor pole #14690 found within fenced construction area | High Pressure Sodium | 38.92918468000 | -77.03279467000
2/11/08 | 471541 | 0 | SHERMAN AVE | NW | 2/14/08 | 14219 | 1G462 | (Light out) | 2-14-08 chris ashton repaired pole #14219 | High Pressure Sodium | 38.92198110000 | -77.02520587000
2/11/08 | 471540 | 0 | SHERMAN AVE | NW | 2/12/08 | 14219 | 1G462 | (Light out) | 2-11-08 octavia taylor repaired pole #14219 | High Pressure Sodium | 38.92198110000 | -77.02520587000
2/9/08 | 471485 | 3813 | GEORGIA AVE | NW | 5/16/08 | 4J356 | 4G254 | (Light out) | FRONT - street light out 2-12-08 darryl hooker repaired - pole has no id tag Installed tag #4j386 | High Pressure Sodium | 38.93795290000 | -77.02466878000
2/8/08 | 470832 | 3718 | 4TH ST | SE | 2/14/08 | 85723 | 8A134 | (Light out) | 2-12-09 roger warren needs big boom truck 2-9-08- ROGER WARREN POLE #85723 STREET BLOCKED OFF -- NEEDS BIG BOOM TRUCK | High Pressure Sodium | 38.83711140000 | -77.00043425000
2/8/08 | 470831 | 3718 | 4TH ST | SE | 2/14/08 | 85727 | 8A144 | (Light out) | 2-12-08 roger warren - needs big boom truck 2-9-08 roger warren - pole #85727 -chain locked street blocked off --NEEDS BIG BOOM TRUCK | High Pressure Sodium | 38.83851611000 | -77.00004783000
2/8/08 | 470830 | 3718 | 4TH ST | SE | 2/14/08 | 85728 | 8A145 | (Light out) | 2-12-09 roger warren -- need big boom truck 2-9-08 ROGER WARREN POLE #85728 STREET BLOCKED OFF -- NEEDS BIG BOOM TRUCK | High Pressure Sodium | 38.83855580000 | -77.00040988000
2/8/08 | 470748 | 629 | H ST | NW | 2/11/08 | 22634 | 6M695 | (Light out) | 2-11-08 L Roberto Installed 1-400w hps lamp, NWPC | High Pressure Sodium | 38.89990420000 | -77.02118022000
2/8/08 | 470707 | 136 | RHODE ISLAND AVE | NW | 2/9/08 | 59999 | 5A191 | (Light out) | 2-9-08 billy black / pole #59999 repaired on 2-05-08 | High Pressure Sodium | 38.91513978000 | -77.01349288000
2/7/08 | 470203 | 0 | FIRTH STERLING AVE | SE | 2/8/08 | 81559DC | 8M089 | (Light out) |  | High Pressure Sodium | 38.86215072000 | -76.99850166000
2/7/08 | 470188 | 0 | NEW YORK AVE | NE | 2/11/08 | 50001 | 5A035 | (Light out) |  | High Pressure Sodium | 38.91733557000 | -76.97140198000
2/7/08 | 470176 | 0 | 13TH ST | NW | 2/9/08 | 4K432 | 4U146 | (Light out) | 2-9-08 darryl hooker repaired pole #4K432 | High Pressure Sodium | 38.94308499000 | -77.02978871000
2/7/08 | 470645 | 3636 | GEORGIA AVE | NW | 2/9/08 | 12965 | 1G222 | (Light out) | - 2-9-08 chris ashton repaired pole #12965 metal pole..burnt out bulb | High Pressure Sodium | 38.93515126000 | -77.02421018000
2/7/08 | 470014 | 2921 | PENNSYLVANIA AVE | SE | 2/7/08 | 78566DC | 7E089DC | (Light out) |  | High Pressure Sodium | 38.87135609000 | -76.96562776000
2/7/08 | 470002 | 0 | K ST | NW | 2/7/08 | 22402 | 6A100 | (Light out) |  | High Pressure Sodium | 38.90245268000 | -77.01971021000
2/6/08 | 469612 | 1000 | 5TH ST | SE | 2/7/08 | 67557 | 6B467 | (Light out) |  | High Pressure Sodium | 38.87826913000 | -76.99959928000
2/6/08 | 469602 | 1200 | 1ST ST | SE | 11/20/08 | 67744 | 68499 | (Light out) | 2-8-08- gary hicks N/C undrground 2-07-08 J Caetto REFER to Night Crew too much traffic | High Pressure Sodium | 38.87598356000 | -77.00602232000
2/6/08 | 470060 | 3409 | O ST | NW | 2/8/08 | 21099 | 2G161 | (Light out) | FRONT - base of streetlight pole (metal) is open and wires are exposed. rats are going in and out from box.. it needs to be covered (cover is missing) ASAP. 2-08-08 M.TOMLIN-----REPAIRED | High Pressure Sodium | 38.90780538000 | -77.06822529000
2/6/08 | 469574 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 2/6/08 | 71295DC | 7A227 | (Light out) |  | High Pressure Sodium | 38.89887350000 | -76.93373005000
2/5/08 | 468930 | 0 | MOUNT OLIVET RD | NE | 2/7/08 | 54272 | 5M044 | (Light out) | 2-7-08 billy black repaired pole #54272 | High Pressure Sodium | 38.91240042000 | -76.99153361000
2/5/08 | 468916 | 2348 | BENNING RD | NE | 2/6/08 | 74442DC | 7E173 | (Light out) | 2-6-08 roger warren repaired pole #74442dc | High Pressure Sodium | 38.89753179000 | -76.96912923000
2/5/08 | 468904 | 781 | 7TH ST | NW | 2/5/08 | 22451 | 6M649 | (Light out) |  | High Pressure Sodium | 38.89938925000 | -77.02181860000
2/4/08 | 468247 | 2201 | WISCONSIN AVE | NW | 2/4/08 | 30160 | 3G090 | (Light out) | 2-04-08 J Caetto Metal pole# 30160 Installed 1-TLPC | High Pressure Sodium | 38.91927198000 | -77.07055935000
2/4/08 | 468852 | 618 | H ST | NW | 2/5/08 | 22561 | 6M699 | (Light out) | THE STREETLIGHT IS IN FRONT OF 618 H STREET, N.W. - | High Pressure Sodium | 38.89973495000 | -77.02087482000
2/2/08 | 468202 | 0 | KENNEDY ST | NW | 2/5/08 | 4M070 | 4M070DC | (Light out) | SE CORNER - mental pole streetlight is out ///# 4M070 | High Pressure Sodium | 38.95645469000 | -77.02220865000
2/1/08 | 467721 | 2 | WESTMORELAND CIR | NW | 2/1/08 | 34380 | 3M038 | (Light out) | 2-1-08 chris ashton repaired pole #34380 | Mercury Vapor | 38.94941039000 | -77.10097492000
2/1/08 | 467702 | 4520 | HOBAN RD | NW | 2/1/08 | 35821DC | 35821 | (Light out) | 2-1-08 chrs ashton repaired pole #35821DC | Incandescent | 38.91422302000 | -77.08546138000
2/1/08 | 467634 | 100 | 1ST ST | NE | 2/1/08 | 56986 | 5M095 | (Light out) | 2-1-08 tom osvatics repaired pole #56986 | High Pressure Sodium | 38.90945362000 | -77.00612005000
2/1/08 | 467625 | 1410 | 34TH ST | NW | 2/1/08 | 21074 | 2G187 | (Light out) | 2-1-08 kevin hollins repaired pole #21074 | High Pressure Sodium | 38.90809992000 | -77.06790137000
1/31/08 | 467184 | 100 | 1ST ST | NE | 1/31/08 | 56986 | 5M095 | (Light out) | 1-31-08 gary hicks repaired pole #56986 | High Pressure Sodium | 38.90945362000 | -77.00612005000
1/31/08 | 467117 | 0 | RIGGS RD | NE | 1/31/08 | 4P557DC | 4U181 | (Light out) | 1-31-08 darryl hooker repaired pole #4p557dc | High Pressure Sodium | 38.95788979000 | -77.00189601000
1/30/08 | 466734 | 1010 | MASSACHUSETTS AVE | NW | 2/6/08 | 25961 | 2M216 | (Light out) | 2-6-08 kevin hollins repaired pole #25961 | High Pressure Sodium | 38.90379985000 | -77.02690625000
1/30/08 | 466730 | 1111 | 11TH ST | NW | 1/31/08 | 25265 | 2M225 | (Light out) | 1-31-08 kevin hollins repaired pole #25265 | High Pressure Sodium | 38.90512472000 | -77.02692572000
1/30/08 | 466715 | 1333 | NEW HAMPSHIRE AVE | NW | 2/3/08 | 24482 | 2G772 | (Light out) |  | High Pressure Sodium | 38.90845645000 | -77.04444043000
1/30/08 | 466713 | 1007 | NEW HAMPSHIRE AVE | NW | 1/31/08 | 23863 | 2G706 | (Light out) | 1-31-08 kevin hollins repaired pole #23863 | High Pressure Sodium | 38.90335191000 | -77.04923699000
1/30/08 | 466692 | 841 | 7TH ST | NW | 1/30/08 | 22422 | 6M662 | (Light out) | 1-30-08 kevin hollins thia job was completed last night | High Pressure Sodium | 38.90021373000 | -77.02201497000
1/30/08 | 466666 | 100 | 1ST ST | NE | 1/30/08 | 56986 | 5M095 | (Light out) | 1-30-08 kevin hollins repaired pole #56986 | High Pressure Sodium | 38.90945362000 | -77.00612005000
1/30/08 | 466634 | 841 | 7TH ST | NW | 1/30/08 | 22422 | 6M662 | (Light out) | 1-30-08 kevin hollins repaired lose wire in P/C pole #22422 | High Pressure Sodium | 38.90021373000 | -77.02201497000
1/30/08 | 466547 | 806 | RHODE ISLAND AVE | NE | 1/30/08 | 56388DC | 5A274 | (Light out) | 1-30-08 gary hicks repaired | High Pressure Sodium | 38.92176361000 | -76.99420034000
1/30/08 | 466546 | 806 | RHODE ISLAND AVE | NE | 1/30/08 | 56388DC | 5A274 | (Light out) | 1-30-08 tom osvatics repaired pole #56588dc | High Pressure Sodium | 38.92176361000 | -76.99420034000
1/29/08 | 466601 | 3300 | PENNSYLVANIA AVE | SE | 1/31/08 | 78544DC | 7E115DC | (Light out) | FRONT - light is out on wooden pole 1-31-08 roger warren repaired pole #78544dc | High Pressure Sodium | 38.86824545000 | -76.95800685000
1/29/08 | 465973 | 0 | KENILWORTH AVE | NE | 1/29/08 | 72421 | 7M097 | (Light out) | 2nd light from jay street 1-29-08 roger warren repaired pole #72421 | High Pressure Sodium | 38.90111449000 | -76.94569640000
1/29/08 | 465478 | 1025 | CONNECTICUT AVE | NW | 1/29/08 | 27214 | 2G832 | (Light out) | 1-29-08 DA - duplicate ticket to wo# 465381 hansen #1698267 | High Pressure Sodium | 38.90319443000 | -77.03951645000
1/28/08 | 465468 | 711 | ANACOSTIA AVE | NE | 1/29/08 | 72358DC | 7A481 | (Light out) | 1-29-08 roger warren repaired pole #72358dc qc / fixture | High Pressure Sodium | 38.90197539000 | -76.95056600000
1/28/08 | 465467 | 4115 | 42ND ST | NE | 1/29/08 | 70329 | 7M085 | (Light out) | 1-29-08 roger warren - pole #70329 - N/C underground | High Pressure Sodium | 38.90318186000 | -76.94427070000
1/28/08 | 465464 | 0 | JAY ST | NE | 1/29/08 | 72419 | 7M095 | (Light out) | 1-29-08 roger warren repaired pole #72419 qc / fixture | High Pressure Sodium | 38.90160220000 | -76.94523892000
| 465381 | 1025 | CONNECTICUT AVE | NW | 2/11/08 | 27214 | 2G832 | (Light out) | light out on metal pole 02/11/08: Tan refer back to Severn for no current 1-28-08 M.TOMLIN-----NO CURRENT | High Pressure Sodium | 38.90319443000 | -77.03951645000
1/26/08 | 465364 | 0 | RHODE ISLAND AVE | NW | 1/31/08 | 25214 | 2U043 | (Light out) | SOUTHEAST CORNER - caller stating light out on metal pole 1-31-08 kevin hollins repaired pole #25214 reconnected neturial to powerdoor and transformer 1-28-08 kevin hollins - pole #25214 N/C open neturial @ base 1-28-08 M.TOMLIN----NEED POLE# | High Pressure Sodium | 38.91062739000 | -77.02719923000
1/26/08 | 465323 | 4611 | NANNIE HELEN BURROUGHS AVE | NE | 1/26/08 | 71562DC | 7A233 | (Light out) | 1-26-08 roger warren repaired pole #71562dc | High Pressure Sodium | 38.89924568000 | -76.93571393000
1/26/08 | 465315 | 4203 | GEORGIA AVE | NW | 1/26/08 | 4K513 | 4G294 | (Light out) | 1-26-08 tom osvatics repaired pole #4K513 | High Pressure Sodium | 38.94198605000 | -77.02562660000
1/26/08 | 465307 | 0 | GEORGIA AVE | NW | 1/26/08 | 4K022 | 4G301 | (Light out) | 1-26-08 tom osvatics repaired pole #4K022 | High Pressure Sodium | 38.94304861000 | -77.02571897000
1/25/08 | 465284 | 0 | CAMDEN ST | SE | 1/27/08 | 74750DC | 7A064DC | (Light out) | FRONT - Caller reporting streetlight out on wooden pole for several days. Please inspect asap. | High Pressure Sodium | 38.85948091000 | -76.96189661000
1/25/08 | 464765 | 1000 | L ST | SE | 11/20/08 | 67686 | 67685 | (Light out) | AL Young 1/29/08, light located in construction zone no access, REFERE BACK TO DDOT. 1-25-08- gary hicks closed lens pole #67686 pole has N/C | High Pressure Sodium | 38.87758833000 | -77.00607638000
1/25/08 | 464759 | 1004 | 1ST ST | SE | 11/20/08 | 67448 | 6A023 | (Light out) | Al Young 1/29/08, light is located in construction zone , no access. Refer to DDOT. 1-25-08 gary hicks / pole #67448 has N/C | High Pressure Sodium | 38.87799876000 | -77.00576406000
1/25/08 | 464317 | 1000 | 5TH ST | SE | 1/25/08 | 67557 | 6B467 | (Light out) | 1-25-08 gary hicks repaired pole #67557 fixture (cutoff - flat lens ) | High Pressure Sodium | 38.87826913000 | -76.99959928000
1/24/08 | 464237 | 0 | I ST | SE | 1/24/08 | 67651 | 6B445 | (Light out) | 1-24-08 gary hicks repaired pole #67651 1st light on i street | High Pressure Sodium | 38.87934752000 | -77.00122654000
1/24/08 | 464235 | 200 | L ST | SE | 1/24/08 | 67695 | 6A414 | (Light out) | 1-24-08 gary hicks repaired pole #67695 | Incandescent | 38.87766628000 | -77.00287950000
1/23/08 | 463627 | 703 | 49TH ST | NE | 1/23/08 | 71285DC | 7A218 | (Light out) | 1-23-08 roger warren repaired pole #71285dc | High Pressure Sodium | 38.89869349000 | -76.93152778000
1/23/08 | 463587 | 0 | M ST | SE | 1/23/08 | 67318 | 6M790 | (Light out) | 1-23-08 gary hicks repaired pole #67318 | High Pressure Sodium | 38.87636424000 | -77.00920113000
1/23/08 | 463586 | 0 | SOUTH CAPITOL ST | SW |  | 21726 | 68654 | (Light out) | H Lancaster 1/30/08 new poles being installed in area by out side contactor, refer back to DDOT. 1-23-08 gary hicks -- pole #21726 -- N/C underground | High Pressure Sodium | 38.88398813000 | -77.00914717000
| 463513 | 2505 | WISCONSIN AVE | NW | 1/24/08 | 30143 | 3G047 | (Light out) | 1-24-08 OT -Barnes Installed 1-TLPC & 1-100w hps lamp FRONT - light out wood pole | High Pressure Sodium | 38.92330197000 | -77.07328360000
1/22/08 | 463542 | 531 | FERN PL | NW | 1/23/08 | 4D590DC | 4D890DC | (Light out) | 1-23-08 R Waites QC Previously Serviced STREET - one metal pole light is out | High Pressure Sodium | 38.97826238000 | -77.02131042000
1/22/08 | 462951 | 4203 | GEORGIA AVE | NW | 1/28/08 | 4K513 | 4G294 | (Light off/on) | 1-26-08 tom osvatics job was complete as a patrol | High Pressure Sodium | 38.94198605000 | -77.02562660000
1/21/08 | 462911 | 501 | H ST | NW | 5/21/08 | 60579 | 6S547 | (Light out) | New poles & manhole being installed by out contactor. THE TWO ALLEY LIGHTS ARE IN THE ALLEY JUST WEST OF THE RED ROOF INN AT 500 H STREET, N.W. - 1-23-08 gary hicks - 3/ metal pole N/C - no id | High Pressure Sodium | 38.90013088000 | -77.01901668000
1/19/08 | 462890 | 159 | V ST | NW | 1/24/08 | 14155 | 53125 | (Light out) | H Lancaster 1/24/08, 1 #8 buttsplices , reconnected ground wire in manhole. job closed by K.Greenfield V STREET NW AND SECOND STREET NW, WASHINGTON, DC V STREET NW AND 2ND STREET NW, WASHINGTON, DC TH | High Pressure Sodium | 38.91850290000 | -77.01401173000
1/19/08 | 462286 | 900 | 2ND ST | SW | 1/19/08 | 68129 | 6A416 | (Light out) | 1-19-08 G.Hicks repaired pole #68129 | High Pressure Sodium | 38.87878241000 | -77.00287862000
1/19/08 | 462286 | 900 | 2ND ST | SW | 1/19/08 | 68129 | 68621 | (Light out) | 1-19-08 G.Hicks repaired pole #68129 | High Pressure Sodium | 38.90623996000 | -77.01082515000
1/17/08 | 462237 | 2411 | BENNING RD | NE | 1/19/08 | 74703 | 7E164 | (Light out) | FRONT - street light on a metal pole is out 1-19-08 R. Warren repaired pole #74703 | High Pressure Sodium | 38.89794857000 | -76.97170081000
1/17/08 | 461936 | 20 | I ST | SE | 1/18/08 | 67458 | 6A043 | (Light out) | 1-18-08 J Caetto installed 1- 250 hps lamp | High Pressure Sodium | 38.87938129000 | -77.00840474000
1/17/08 | 461931 | 200 | L ST | SE | 1/18/08 | 67695 | 6A414 | (Light out) | 1-18-08 J Caetto Light installed 1- 295 inc lamp | Incandescent | 38.87766628000 | -77.00287950000
1/17/08 | 461926 | 202 | 2ND ST | NE | 1/17/08 | 61303 | 6S277 | (Light out) | 1-17-08 - B. Black - Light Repaired | High Pressure Sodium | 38.89870054000 | -77.00344646000
1/17/08 | 461428 | 202 | 2ND ST | NE | 1/17/08 | 61303 | 6S277 | (Light out) | 1/17/08 billy black repaired pole #61303 | High Pressure Sodium | 38.89870054000 | -77.00344646000
1/16/08 | 461418 | 0 | RHODE ISLAND AVE | NW | 1/19/08 | 25214 | 2U043 | (Light out) | 1-19-08 K. Hollins repaired pole #25214 | High Pressure Sodium | 38.91062739000 | -77.02719923000
1/16/08 | 461393 | 1826 | 18TH ST | NW | 1/19/08 | 26780 | 2M106 | (Light out) | D. Smith--REPLACED 400 MV LAMP 1-19-08 | High Pressure Sodium | 38.91492300000 | -77.04174945000
1/16/08 | 461372 | 600 | 2ND ST | NE |  | 61306 | 6S276 | (Light out) | R Rapolla 5-8-08, Night survey crew found that light is still out and marked NO CURRENT. Waiting on Ddot to give direction. H.Lancaster 1/22/08, Ft. Meyers installing new poles & MH in area, NO FEED in old MH refer back to DDOT. | High Pressure Sodium | 38.89832767000 | -77.00344709000
1/16/08 | 461351 | 457 | MASSACHUSETTS AVE | NW |  | 60481 | 6A195 | (Light out) | 1/16/08 billy black- pole #60481 - refer to ddot due to cinstruction | High Pressure Sodium | 38.90073307000 | -77.01753805000
1/16/08 | 461350 | 425 | MASSACHUSETTS AVE | NW | 2/7/08 | 60482 | 6A192 | (Light out) | 1/16/08 -billy black - pole #60482 pole is leaning and has 400mv defective fixture refer to ddot unable to repair fixture because pole is unstable 1/25/08 | Mercury Vapor | 38.90049835000 | -77.01683728000
1/16/08 | 461330 | 131 | M ST | NE | 1/17/08 | 62268 | 6S346 | (Light out) | 1/17/08 bily black -old poles that are getting ready to be removed | High Pressure Sodium | 38.90570457000 | -77.00451927000
1/16/08 | 461329 | 131 | M ST | NE | 1/17/08 | 62269 | 6S356 | (Light out) | 1/17/08 billy black - old pole that is getting ready to be removed | High Pressure Sodium | 38.90559826000 | -77.00432213000
1/16/08 | 461328 | 131 | M ST | NE | 1/17/08 | 62270 | 6S343 | (Light out) | 1/17/08 billy black - old pole that getting ready to be removed | High Pressure Sodium | 38.90570496000 | -77.00395113000
1/16/08 | 461888 | 0 | M ST | NW | 1/23/08 | 23724 | 2B105 | (Light out) | 1-23-08 chris ashton repaired pole #23724 1-18-08 R Arrington REFER to Night Crew unable to service because of traffic 1-21-08 M.TOMLIN-----REFER TO NIGHT CREW/TRAFFIC 1-22-08 D.WEBB-----TOO BUSY/TRAFFIC | High Pressure Sodium | 38.90574692000 | -77.04395959000
1/16/08 | 461278 | 1262 | NEW HAMPSHIRE AVE | NW | 1/16/08 | 23852 | 2G757 | (Light out) | 1/16/08 kevin hollins repaired pole #23852 | High Pressure Sodium | 38.90669938000 | -77.04633627000
1/16/08 | 461221 | 1200 | 1ST ST | NE | 1/16/08 | 61243 | 6A273 | (Light out) | 1/16/08 Billy Black repaired pole #61243 | High Pressure Sodium | 38.90637775000 | -77.00597499000
1/16/08 | 461886 | 1614 | 7TH ST | NW | 2/26/08 | 25704 | 6A822 | (Light out) | Installed 1-tlpc FROT - street light is out it's a metal pole | High Pressure Sodium | 38.91165663000 | -77.02182317000
1/15/08 | 460809 | 0 | O ST | NE | 4/4/08 | 62315 | 5M112 | (Light out) | 4-3-08, R Rapolla, Sub/Pepco made connection in MH, Job qced, 3-03-08 D Smith/Kates/Gray QC Replaced TLPC H.Lancaster 1/8/08 No power in pepco MH refer to pepco, 1/16/08 Billy Black pole # | High Pressure Sodium | 38.90852270000 | -77.00482604000
1/15/08 | 460808 | 0 | 1ST ST | NE | 7/18/08 | 61248 | 6A282 | (Light out) | 7-9-08 @ 322am K. Hollins pole #61248 is Still A No Current R Rapolla, 5-21-08, Job was completed on 5-15-08 5-6-08 tim richards pole #61248 still a no current there are no wires underground R Rapolla, 4-4-08, Pepco installed New lines and made taps fo | High Pressure Sodium | 38.90791176000 | -77.00580646000
1/15/08 | 461274 | 717 | BARNES ST | NE | 1/17/08 | 72462DC | 7A473 | (Light out) | FRONT OF - one light out,,,,,,metal pole | High Pressure Sodium | 38.90163933000 | -76.95010523000
1/15/08 | 460760 | 38 | NEW YORK AVE | NE | 1/15/08 | 61254 | 6A287 | (Light out) | 1/15/08 tom osvatics repaired pole #61254 | High Pressure Sodium | 38.90772223000 | -77.00767643000
1/14/08 | 460001 | 2 | WESTMORELAND CIR | NW | 1/19/08 | 34380 | 3M038 | (Light out) | 1-19-08 C. Ashton repaired pole #34380 | Mercury Vapor | 38.94941039000 | -77.10097492000
1/11/08 | 459375 | 0 | 23RD ST | NW | 1/15/08 | 28320 | 2M268 | (Light out) | 1/15/08 Kevin hollins - pole #28320 - light found okay | High Pressure Sodium | 38.89242239000 | -77.05003950000
1/11/08 | 459367 | 1333 | NEW HAMPSHIRE AVE | NW | 1/16/08 | 24482 | 2G772 | (Light out) | 1/16/08 kevin hollins repaired pole #24482 | High Pressure Sodium | 38.90845645000 | -77.04444043000
1/11/08 | 459352 | 1111 | 11TH ST | NW | 1/16/08 | 25265 | 2M225 | (Light out) | 1/16/08 Kevin Hollins pole #25265 found okay | High Pressure Sodium | 38.90512472000 | -77.02692572000
1/11/08 | 459345 | 1826 | 18TH ST | NW | 1/14/08 | 26780 | 2M106 | (Light out) | 1-14-08 D Smith W Kates Installed 1-250w hps lamp | High Pressure Sodium | 38.91492300000 | -77.04174945000
1/11/08 | 459327 | 0 | GEORGIA AVE | NW | 1/12/08 | 4K022 | 4G301 | (Light off/on) | 1/12/08 darryl hooker repaired pole #4K022 qc/ fixture | High Pressure Sodium | 38.94304861000 | -77.02571897000
1/11/08 | 459325 | 0 | SHERMAN AVE | NW | 1/16/08 | 12587 | 1G451 | (Light out) | 1-16-08 D Smith Kates/Young Installed 400w hps lamp | High Pressure Sodium | 38.92300485000 | -77.02549655000
1/11/08 | 459272 | 0 | CAMDEN ST | SE | 1/12/08 | 74750DC | 7A064DC | (Light out) | 1/12/08 rodger warren repaired pole #74750dc | High Pressure Sodium | 38.85948091000 | -76.96189661000
1/11/08 | 459264 | 4918 | 49TH PL | NE | 1/15/08 | 71283DC | 7A215 | (Light off/on) | 1-15-08 P Harvin Previously repaired | High Pressure Sodium | 38.89857711000 | -76.93088757000
1/11/08 | 459263 | 703 | 49TH ST | NE | 1/16/08 | 71285DC | 7A218 | (Light out) | 1-15-08 D Smith Kates/Young Light Found Ok 1/15/08 rodger warren pole #71285dc has no current to overhead | High Pressure Sodium | 38.89869349000 | -76.93152778000
1/11/08 | 459881 | 515 | H ST | NE | 1/15/08 | 61722 | 6S062 | (Light out) | 1/15/08 billy black repaired pole #61722 FRONT - caller is requesting streetlight repair metal pole | High Pressure Sodium | 38.90011936000 | -76.99890875000
1/11/08 | 459893 | 931 | 7TH ST | NW | 1/18/08 | 22413 | 6M680 | (Light out) | 1-18-08 W Kates Installed NWPC FRONT - Streetlight on top of building stays on all day. 1/16/08 Kevin hollins light found okay - refer to day crew 24 hour burn | High Pressure Sodium | 38.90145684000 | -77.02201645000
1/11/08 | 458690 | 711 | 4TH ST | NW | 1/11/08 | 60453 | 6S473 | (Light out) | 1/11/08 billy black - pole #60453 - complete w/ 400 hps bulb | High Pressure Sodium | 38.90264718000 | -77.01608462000
1/11/08 | 458688 | 0 | K ST | NW | 1/11/08 | 22402 | 6A100 | (Light out) | 1/11/08 billy black - pole #22402 / completed w/ 400 hps bulb, t/l | High Pressure Sodium | 38.90245268000 | -77.01971021000
1/10/08 | 459167 | 1701 | M ST | NW | 1/12/08 | 26411 | 2U750 | (Light out) | M STREET NW AND 17TH STREET NW, WASHINGTON, DC M STREET NW AND 17TH STREET NW, WASHINGTON, DC STREET SIDE, CORNER - **SRCB** IS THE POLE METAL OR WOOD? - METAL WHAT IS THE PROBLEM WITH THE LIGHT (LIGHT IS OUT, LIGHT IS ALWAYS ON, LIGHT COVER/GLOB | High Pressure Sodium | 38.90572284000 | -77.03887684000
1/9/08 | 458117 | 1341 | Q ST | NW |  | 25403 | 29698 | (Light out) | L. Barclay 1/22/08 wires cut in pepco manhole (NO FEED) refer to pepco. 1/15/08 Kevin Hollins pole #25403 has N/C at base 1-14-08 D Smith W Kates Light inaccessable, due to construction, street blocked off | High Pressure Sodium | 38.91108439000 | -77.03132341000
1/9/08 | 458106 | 0 | SOUTH DAKOTA AVE | NE | 1/16/08 | 57964 | 5M083 | (Light out) | H. Lancaster 4 # 8 buttsplices made splices in T-base & MH job completed 1/16/08. closed by K.Greenfield 1/11/08 tom osvatics pole #57964 N/C underground | High Pressure Sodium | 38.92723868000 | -76.96712989000
1/9/08 | 458058 | 0 | EAST CAPITOL ST | NE | 1/11/08 | 63634 | 6M824 | (Light out) | H. Lancaster 2#2 buttsplices made splices in T-base , job completed 1/11/08. Closed by K. Greenfield 1/10/08 tom osvatics / pole #63634 / N/C at t base refer to fault crew | High Pressure Sodium | 38.89007149000 | -76.97454092000
1/9/08 | 458045 | 1063 | 3RD ST | NE | 1/10/08 | 61352 | 6S416 | (Light out) | 1/10/08 tom osvatics - pole #61352 - installed 250 hps bulb | High Pressure Sodium | 38.90320663000 | -77.00197013000
1/9/08 | 458038 | 900 | 17TH ST | NE | 1/12/08 | 59373 | 5M004 | (Light out) | 1/12/08 tom osvatics repaired pole #59373 qc / fixture 1-10-08 D Smith W Kates Tempory polew/traffic light no arm/fixture | High Pressure Sodium | 38.90100292000 | -76.97890516000
1/9/08 | 458035 | 504 | K ST | NW | 1/11/08 | 60461 | 6A101 | (Light out) | 1/11/08 billy black installed a short cap on pole #60461 | High Pressure Sodium | 38.90260703000 | -77.01950617000
1/9/08 | 458032 | 826 | 2ND ST | NE | 1/11/08 | 61300 | 6S290 | (Light out) | Lou Kendall construction in area new poles being installed closed by K. Greenfield on 1/11/08., 1/10/08 tom osvatics - pole # 61300 - N/C underground | High Pressure Sodium | 38.90069257000 | -77.00363545000
1/9/08 | 458031 | 901 | 2ND ST | NE | 1/10/08 | 61297 | 6S297 | (Light out) | 1/10/08 tom osvatics - pole #61297 - installed 250 hps bulb | High Pressure Sodium | 38.90149765000 | -77.00350429000
1/9/08 | 458030 | 0 | 2ND ST | NE | 1/11/08 | 61291 | 6S307 | (Light out) | Lou. Kendall construction in area new poles being installed closed by K. Greenfield 1/10/08 tom osvatics - pole #61291 - N/C underground | High Pressure Sodium | 38.90340904000 | -77.00350095000
1/9/08 | 458025 | 2034 | INDEPENDENCE AVE | SE |  | 63661 | 6M840 | (Light out) | 1/12/08 billy black pole #63661 N/C underground Affiliated w/458023 | High Pressure Sodium | 38.88776077000 | -76.97613660000
1/9/08 | 458023 | 00 | INDEPENDENCE AVE | SE | 3/10/08 | 63662 | 6M839 | (Light out) | 1/12/08 billy black pole #63662 N/C | High Pressure Sodium | 38.88775642000 | -76.97553609000
1/9/08 | 458009 | 1826 | 18TH ST | NW | 1/11/08 | 26780 | 2M106 | (Light out) | 1/11/08 kevin hollins - pole #26780 - tightened P/C 1-09-08 Pole # 26780 Pendant Pole out | High Pressure Sodium | 38.91492300000 | -77.04174945000
1/8/08 | 457358 | 711 | D ST | NW | 1/9/08 | 60088 | 2M325 | (Light out) | 1/9/08 kevin hollins repaired pole #60088 - qc / fixture | High Pressure Sodium | 38.89485723000 | -77.02246234000
1/8/08 | 457924 | 4010 | SHEPHERD ST | NE | 1/10/08 | 51206DC | 52006DC | (Light out) | 1-10-08 D Smith W Kates Installed 1-100w PDoor FRONT - requesting to have repair a metal pole. | High Pressure Sodium | 38.93996002000 | -76.97564051000
1/8/08 | 457906 | 0 | INGRAHAM ST | NW | 1/10/08 | 4M359 | 4M360 | (Light out) | 1/10/08 darryl hooker - pole #4M359 - installed 400 hps bulb - qc / fixture FRONT - street light out on a metal pole | High Pressure Sodium | 38.95417635000 | -77.02633759000
1/4/08 | 456161 | 4202 | 13TH ST | NW | 1/5/08 | 4K433 | 4U149 | (Light out) | 1-05-08 D Webb Installed 1-400w hps lamp, tlpc | High Pressure Sodium | 38.94238501000 | -77.02962392000
1/4/08 | 456160 | 4514 | 13TH ST | NW | 1/9/08 | 4K422 | 4U131 | (Light out) | 1/9/08darryl hooker repaired pole #4k422 1-05-08 D Webb Found Ok | High Pressure Sodium | 38.94571765000 | -77.02978404000
1/4/08 | 456546 | 1614 | 7TH ST | NW | 1/8/08 | 25704 | 6A822 | (Light out) | ACROSS - would like to request streetlight on metal pole to be repaired, please inspect and repair. | High Pressure Sodium | 38.91165663000 | -77.02182317000
1/4/08 | 456100 | 4514 | 13TH ST | NW | 8/14/08 | 4K422 | 4U131 | (Light out) |  | High Pressure Sodium | 38.94571765000 | -77.02978404000
1/4/08 | 456094 | 841 | 7TH ST | NW | 1/4/08 | 22422 | 6M662 | (Light out) |  | High Pressure Sodium | 38.90021373000 | -77.02201497000
1/3/08 | 455637 | 900 | U ST | NW | 1/3/08 | 13983 | 1G551 | (Light out) |  | High Pressure Sodium | 38.91713116000 | -77.02591861000
1/3/08 | 455628 | 0 | MILITARY RD | NW | 1/5/08 | 34723 | 4B754 | (Light dim) | 1/5/08 darryl hooker - changed temp wire from 240 to 120 - pole #34723 qc / fixture | High Pressure Sodium | 38.96096329000 | -77.06605069000
1/3/08 | 455421 | 2 | WESTMORELAND CIR | NW | 1/3/08 | 34380 | 3M038 | (Light out) |  | Mercury Vapor | 38.94941039000 | -77.10097492000
1/2/08 | 454965 | 4832 | NANNIE HELEN BURROUGHS AVE | NE | 1/2/08 | 71292DC | 7A222DC | (Light out) |  | High Pressure Sodium | 38.89861491000 | -76.93235329000
12/29/07 | 454381 | 840 | E ST | NW | 1/2/08 | 60180 | 2M349 | (Light out) |  | High Pressure Sodium | 38.89605627000 | -77.02249512000
12/28/07 | 453865 | 0 | 56TH ST | NE | 1/2/08 | 72761DC | 79961DC | (Light out) | 1-02-08 D Smith - W Kates - R Young Duplicate to W.O 453866 | High Pressure Sodium | 38.89530833000 | -76.92045321000
12/28/07 | 453766 | 1411 | 37TH ST | NW | 12/28/07 | 21142 | 2G206 | (Light out) |  | High Pressure Sodium | 38.90801099000 | -77.07168004000
12/27/07 | 453199 | 2418 | 18TH ST | NW | 12/27/07 | 11531 | 1G485 | (Light out) |  | High Pressure Sodium | 38.92129769000 | -77.04231632000
12/22/07 | 452542 | 0 | I ST | NW | 12/27/07 | 22487 | 2G985 | (Light out) | FRONT/ NE CORNER - street light is out it's a metal pole | High Pressure Sodium | 38.90081220000 | -77.02379981000
12/20/07 | 451350 | 777 | BARNES ST | NE | 12/21/07 | 72464DC | 7A470 | (Light out) |  | High Pressure Sodium | 38.90215555000 | -76.94944817000
12/20/07 | 451279 | 0 | I ST | NW | 12/22/07 | 22487 | 2G985 | (Light out) |  | High Pressure Sodium | 38.90081220000 | -77.02379981000
12/20/07 | 451277 | 0 | 7TH ST | NW | 12/21/07 | 22409 | 6M688 | (Light out) |  | High Pressure Sodium | 38.90199325000 | -77.02201951000
12/19/07 | 450545 | 0 | EAST CAPITOL ST | NE | 1/7/08 | 63629 | 6M837 | (Light out) | 1-4-08-C.Miller QC Follow up- light on -Complete H. Lancaster streetlight Found ok on 1/3/08, closed by K.Greenfield | High Pressure Sodium | 38.88956256000 | -76.97418443000
12/19/07 | 450540 | 1004 | 1ST ST | SE | 12/20/07 | 67448 | 6A023 | (Light out) |  | High Pressure Sodium | 38.87799876000 | -77.00576406000
12/19/07 | 450510 | 410 | 7TH ST | NW | 12/21/07 | 60647 | 6M616 | (Light out) |  | High Pressure Sodium | 38.89512871000 | -77.02201224000
12/19/07 | 450503 | 711 | D ST | NW | 12/21/07 | 60088 | 2M325 | (Light out) |  | High Pressure Sodium | 38.89485723000 | -77.02246234000
12/19/07 | 450481 | 504 | K ST | NW | 12/21/07 | 60461 | 6A101 | (Light out) |  | High Pressure Sodium | 38.90260703000 | -77.01950617000
12/19/07 | 450620 | 0 | FLORIDA AVE | NE | 12/21/07 | 62311 | 5M111 | (Light out) | FRONT/ 300 BLOCK OF FLORDIA AVE NE - street light is out metal pole | High Pressure Sodium | 38.90852286000 | -77.00517917000
12/18/07 | 450096 | 3400 | O ST | NW | 12/20/07 | 21097 | 2G195 | (Light out) | 12-20-07 J.PECK------SECURE GLOBE AND LENS | High Pressure Sodium | 38.90785532000 | -77.06897784000
12/17/07 | 449428 | 1001 | NEW HAMPSHIRE AVE | NW | 12/18/07 | 23862 | 2G674 | (Light out) | Red Tape D.Smith | High Pressure Sodium | 38.90308383000 | -77.04974132000
12/17/07 | 449427 | 1826 | 18TH ST | NW | 12/18/07 | 26780 | 2M106 | (Light out) | Red Tape D.Smith | High Pressure Sodium | 38.91492300000 | -77.04174945000
12/17/07 | 449425 | 1500 | PARK RD | NW | 12/18/07 | 12959 | 1G362 | (Light out) | D.Smith | High Pressure Sodium | 38.93151986000 | -77.03595981000
12/17/07 | 449404 | 0 | CALIFORNIA ST | NW | 12/20/07 | 11159 | 1A102 | (Light out) | Red Tape D.Smith | High Pressure Sodium | 38.91772320000 | -77.04056351000
12/17/07 | 449361 | 2 | L ST | NE | 12/19/07 | 61201 | 6A240 | (Light out) | 12-17-07 Pole# 61201 | High Pressure Sodium | 38.90378899000 | -77.00858856000
12/17/07 | 449360 | 504 | K ST | NW | 12/18/07 | 60461 | 6A101 | (Light out) | 12-17-07 Pole# 60461 12-18-07 D Smith - W Kates Installed 1-400w hps lamp, TLPC | High Pressure Sodium | 38.90260703000 | -77.01950617000
12/17/07 | 449331 | 504 | K ST | NW | 12/18/07 | 60461 | 6A101 | (Light out) | 500 BLOCK K ST NW ( NE CORNER ) 12-18-07 D Smith - W Kates Duplicate REFER to W/O# 449360 | High Pressure Sodium | 38.90260703000 | -77.01950617000
12/14/07 | 449176 | 3817 | GEORGIA AVE | NW | 4/30/08 | 4J341 | 4G253 | (Light out) | ACROSS - street light is out, metal pole, please repair. pole #4J341; found ok. smanning--4/29/2008 | High Pressure Sodium | 38.93827040000 | -77.02448591000
12/14/07 | 449188 | 0 | WILTBERGER ST | NW | 12/18/07 | 29509 | 1M010 | (Light out) | FRONT - caller reports that the light has been out for awhile, needs immediate attention 12-17-07 E Graves REFER to NIGHT CReW This need 400w hps kit, NWPC pole marked w red tape | High Pressure Sodium | 38.91554664000 | -77.02082826000
12/14/07 | 448668 | 334 | OAKDALE PL | NW | 12/20/07 | 14190DC | 14802DC | (Light out) |  | High Pressure Sodium | 38.91817964000 | -77.01706140000
12/14/07 | 448661 | 3400 | SHERMAN AVE | NW | 12/15/07 | 13070 | 1L297 | (Light out) |  | High Pressure Sodium | 38.93240466000 | -77.02663265000
12/14/07 | 448655 | 0 | CALIFORNIA ST | NW | 12/15/07 | 11159 | 1A102 | (Light out) |  | High Pressure Sodium | 38.91772320000 | -77.04056351000
12/14/07 | 448653 | 0 | 14TH ST | NW | 12/15/07 | 13019 | 1G015 | (Light out) |  | High Pressure Sodium | 38.92900455000 | -77.03255621000
12/14/07 | 449193 | 3400 | R ST | NW | 1/23/08 | 20592 | 29651 | (Light out) | R STREET NW AND 34 STREET NW, WASHINGTON, DC HI - G EDWARDS 120 FT # 10 CABLE | High Pressure Sodium | 38.91364705000 | -77.06799552000
12/14/07 | 448631 | 3800 | GEORGIA AVE | NW | 12/14/07 | 4J340 | 4G247 | (Light out) | 12-14-07 D Smith W Kates REplaced 400 hps lamp | High Pressure Sodium | 38.93772617000 | -77.02442661000
12/13/07 | 448083 | 26 | K ST | NE | 12/14/07 | 61212 | 6S445 | (Light out) |  | High Pressure Sodium | 38.90260111000 | -77.00711708000
12/13/07 | 448079 | 711 | 4TH ST | NW | 12/14/07 | 60453 | 6S473 | (Light out) |  | High Pressure Sodium | 38.90264718000 | -77.01608462000
12/13/07 | 448078 | 1222 | 1ST ST | NE | 12/14/07 | 61244 | 6A275 | (Light out) |  | High Pressure Sodium | 38.90676525000 | -77.00596728000
12/13/07 | 448077 | 0 | O ST | NE | 12/14/07 | 62314 | 5M113 | (Light out) |  | High Pressure Sodium | 38.90852329000 | -77.00447657000
12/13/07 | 448076 | 0 | O ST | NE | 12/14/07 | 62315 | 5M112 | (Light out) |  | High Pressure Sodium | 38.90852270000 | -77.00482604000
12/13/07 | 448074 | 0 | 1ST ST | NE | 12/14/07 | 61248 | 6A282 | (Light out) |  | High Pressure Sodium | 38.90791176000 | -77.00580646000
12/13/07 | 448073 | 131 | M ST | NE |  | 62270 | 6S343 | (Light out) | new construction project - old poles have been deactivated | High Pressure Sodium | 38.90570496000 | -77.00395113000
12/13/07 | 448072 | 131 | M ST | NE | 12/17/07 | 62269 | 6S356 | (Light out) | 12-14-07 M Craig REFER to Night Crew (light marked with NC tape) | High Pressure Sodium | 38.90559826000 | -77.00432213000
12/13/07 | 448069 | 131 | M ST | NE | 2/6/12 | 62267 | 6S353 | (Light out) | new construction project - old poles have been deactivated | High Pressure Sodium | 38.90559717000 | -77.00496490000
12/13/07 | 448595 | 0 | L ST | NE | 12/14/07 | 61206 | 6S237 | (Light out) | UNIT BLOCK - 61206 one metal pole light cover is down ....please repair 12-14-07 D Smith W Kates - closed hanging lens, light working ok | High Pressure Sodium | 38.90378817000 | -77.00651378000
12/13/07 | 448030 | 5503 | HAYES ST | NE | 12/13/07 | 72672DC | 72673DC | (Light out) |  | High Pressure Sodium | 38.89893864000 | -76.92143833000
12/13/07 | 448007 | 457 | MASSACHUSETTS AVE | NW | 1/4/08 | 60481 | 6A195 | (Light out) | 1-4-08 - C Miller test burned light. light working. | High Pressure Sodium | 38.90073307000 | -77.01753805000
12/13/07 | 448001 | 909 | H ST | NE | 12/14/07 | 62341 | 6S091 | (Light out) |  | High Pressure Sodium | 38.90011988000 | -76.99361661000
12/13/07 | 447990 | 909 | H ST | NE | 12/13/07 | 62341 | 6S091 | (Light out) |  | High Pressure Sodium | 38.90011988000 | -76.99361661000
12/12/07 | 447951 | 0 | GEORGIA AVE | NW |  | 4K022 | 4G301 | (Light out) | NBORTHEAST CORNER - 4K022 caller reports a metal street light pole is out 12-13-07 R Waites "REFER to W/O# 446748" QC No Current - No Hot Wire in TBASE | High Pressure Sodium | 38.94304861000 | -77.02571897000
12/11/07 | 446876 | 0 | HIATT PL | NW | 12/13/07 | 13014 | 15045 | (Light out) |  | High Pressure Sodium | 38.93010824000 | -77.03483439000
12/11/07 | 447345 | 2418 | 18TH ST | NW | 12/13/07 | 11531 | 1G485 | (Light out) | IN FRONT OF M'DAWG HOT DOG SHOP - | High Pressure Sodium | 38.92129769000 | -77.04231632000
12/11/07 | 447344 | 2407 | 18TH ST | NW | 12/13/07 | 11533 | 1G491 | (Light out) | IN FRONT OF FELIX RESTAURANT - | High Pressure Sodium | 38.92063969000 | -77.04213470000
12/11/07 | 447360 | 2448 | 18TH ST | NW | 12/13/07 | 11530 | 1G481 | (Light out) | IN FRONT OF THE REEF RESTAURANT - | High Pressure Sodium | 38.92184690000 | -77.04249788000
12/10/07 | 446185 | 0 | GEORGIA AVE | NW | 12/15/07 | 4K022 | 4G301 | (Light out) | 12-14-07 R WaitesNeed GPS Coordanance | High Pressure Sodium | 38.94304861000 | -77.02571897000
12/10/07 | 446748 | 0 | GEORGIA AVE | NW | 12/17/07 | 4K022 | 4G301 | (Light out) | INTERSECTION - STREET LIGHT ON METAL POLE IS OUT | High Pressure Sodium | 38.94304861000 | -77.02571897000
12/10/07 | 446128 | 0 | WISCONSIN AVE | NW |  | 30134 | 3G003 | (Light off/on) | 12-10-07 Pole# 30134 CYCLING | High Pressure Sodium | 38.92806668000 | -77.07330376000
12/10/07 | 446765 | 1702 | SHEPHERD ST | NW | 12/14/07 | 4F232DC | 4F231DC | (Light out) | REAR - TWO WOODEN POLE LIGHTS HAVE BEEN OUT FOR A WHILE AS A RESULT OF A STORM. THE REAR OF THIS BUILDING IS "17 ST" N.W. 12-14-07 R Waites Installed 1-250 hps lamp, TLPC , 1-250 hps PD pole# 4F232DC | High Pressure Sodium | 38.93971259000 | -77.03814519000
12/10/07 | 446068 | 4800 | NANNIE HELEN BURROUGHS AVE | NE | 12/11/07 | 71294DC | 7A226 | (Light out) |  | High Pressure Sodium | 38.89882951000 | -76.93342319000
12/8/07 | 445979 | 0 | INTERSTATE 395 | SW | 1/2/08 | 28688 | 6A579 | (Light out) |  | High Pressure Sodium | 38.88293251000 | -77.01275060000
12/7/07 | 445578 | 0 | H ST | NW | 12/10/07 | 22739 | 2G965 | (Light out) | 12-10-07 I Paraway pole# 22739 & 22740 both working properly on H St | High Pressure Sodium | 38.89969019000 | -77.02607864000
12/7/07 | 445572 | 931 | 7TH ST | NW | 12/13/07 | 22458 | 6M673 | (Light out) | 12-13-07 I Paraway Troubleshoot circuit installed 1-150 hps kit & NWPC | High Pressure Sodium | 38.90144435000 | -77.02181926000
12/7/07 | 445571 | 841 | 7TH ST | NW | 12/11/07 | 22422 | 6M662 | (Light out) |  | High Pressure Sodium | 38.90021373000 | -77.02201497000
12/7/07 | 445542 | 1333 | NEW HAMPSHIRE AVE | NW | 12/8/07 | 24482 | 2G772 | (Light out) |  | High Pressure Sodium | 38.90845645000 | -77.04444043000
12/7/07 | 445533 | 0 | NEW HAMPSHIRE AVE | NW | 12/8/07 | 28346 | 2G683 | (Light out) |  | High Pressure Sodium | 38.90205645000 | -77.05068674000
12/7/07 | 445480 | 1333 | NEW HAMPSHIRE AVE | NW | 12/7/07 | 24482 | 2G772 | (Light out) |  | High Pressure Sodium | 38.90845645000 | -77.04444043000
12/6/07 | 445491 | 719 | 15TH ST | SE | 5/21/08 | 64363DC | 6A053 | (Light out) | STREET - street light on wooden pole is out , | Incandescent | 38.88032991000 | -76.98412324000
12/5/07 | 445132 | 2319 | PENNSYLVANIA AVE | NW | 12/6/07 | 24653 | 2G667 | (Light out) | FRONT------LIGHT IS HANGING DOWN - STREETLIGHT ON METAL POLE IS HANGING DOWN AND IS SHINING INTO MS BEDARD'S OFFICE. 12-06-07 J Caetto Rehung light globe pole# 24653 | High Pressure Sodium | 38.90301348000 | -77.05112594000
12/5/07 | 444848 | 0 | INTERSTATE 295 | SE | 12/5/07 | 68019 | 6L894 | (Light out) |  | High Pressure Sodium | 38.87329255000 | -76.99048281000
12/5/07 | 444847 | 708 | 7TH ST | NW | 12/5/07 | 22445 | 6M637 | (Light out) |  | High Pressure Sodium | 38.89870447000 | -77.02181913000
12/5/07 | 444753 | 0 | SOUTH DAKOTA AVE | NE | 12/5/07 | 57944 | 5M215 | (Light out) |  | High Pressure Sodium | 38.92501946000 | -76.96509579000
12/4/07 | 444785 | 26 | K ST | NE | 12/7/07 | 61212 | 6S445 | (Light out) | ACROSS OF STREET - light is out on metal pole | High Pressure Sodium | 38.90260111000 | -77.00711708000
12/4/07 | 444781 | 5920 | GEORGIA AVE | NW | 12/8/07 | 4E219 | 4A824 | (Light out) | FRONT - metal pole lightbulb out requesting to have repaired | High Pressure Sodium | 38.96170865000 | -77.02785877000
12/4/07 | 444763 | 0 | CAMDEN ST | SE | 12/8/07 | 74755DC | 7A069DC | (Light out) | FRONT - wooden pole..burnt out bulb | High Pressure Sodium | 38.85947895000 | -76.95992491000
12/4/07 | 444801 | 1231 | 11TH ST | NW | 12/6/07 | 25260 | 2M233 | (Light out) | FRONT - would like to request streetlight on metal pole to be repaired. 12-06-07 J Caetto Found ok pole# 25260 | High Pressure Sodium | 38.90681635000 | -77.02692053000
12/4/07 | 444343 | 4488 | F ST | SE | 12/5/07 | 75750 | 75750DC | (Light out) |  | High Pressure Sodium | 38.88189492000 | -76.93692879000
12/4/07 | 444818 | 3649 | BANGOR ST | SE | 12/8/07 | 74811DC | 7A091DC | (Light out) | REAR - ALL THE WOODEN POLE LIGHTS ARE OUT, EXCEPT FOR ONE THIS IS A "T" SHAPE ALLEY | High Pressure Sodium | 38.86030744000 | -76.95386367000
12/4/07 | 444279 | 4832 | NANNIE HELEN BURROUGHS AVE | NE | 12/4/07 | 71292DC | 7A222DC | (Light out) |  | High Pressure Sodium | 38.89861491000 | -76.93235329000
12/4/07 | 444266 | 1231 | 11TH ST | NW | 12/5/07 | 25260 | 2M233 | (Light out) |  | High Pressure Sodium | 38.90681635000 | -77.02692053000
12/4/07 | 443810 | 0 | RICHARDSON PL | NW | 12/4/07 | 59918DC | 59918 | (Light out) |  | High Pressure Sodium | 38.91362402000 | -77.01687221000
12/3/07 | 444206 | 708 | 7TH ST | NW | 12/5/07 | 22445 | 6M637 | (Light out) | IN FRONT OF THE CLYDES RESTURANT - Caller reporting streetlight globe fell off and wires are expose. Please inspect asap. | High Pressure Sodium | 38.89870447000 | -77.02181913000
12/3/07 | 444204 | 131 | M ST | NE | 2/6/12 | 62268 | 6S346 | (Light out) | IN FRONT OF THE BUILDING - Secondary feeder not hot in Pepco manhole - Pepco working down the street. There are new 18 poles in this area. This pole is possibly being removed. | High Pressure Sodium | 38.90570457000 | -77.00451927000
12/3/07 | 444259 | 708 | 7TH ST | NW | 12/7/07 | 22445 | 6M637 | (Light out) | ON 7TH ST NW/BY CLYDES RESTAURANT AND VERIZON CENTER - STREET LIGH BULB IS HANGING READY TO FALL, FRONT OF CLYDES RESTAURANT, PLEASE REPAIR. | High Pressure Sodium | 38.89870447000 | -77.02181913000
12/3/07 | 443773 | 610 | H ST | NW | 12/4/07 | 22559 | 6M700 | (Light out) |  | High Pressure Sodium | 38.89973402000 | -77.02073448000
12/3/07 | 443750 | 0 | 10TH ST | NW | 12/4/07 | 22742 | 2A208 | (Light out) |  | High Pressure Sodium | 38.89889412000 | -77.02589879000
12/3/07 | 443738 | 509 | 7TH ST | NW | 12/4/07 | 22431 | 6M628 | (Light out) |  | High Pressure Sodium | 38.89648966000 | -77.02200839000
12/2/07 | 444262 | 0 | CAMDEN ST | SE | 12/5/07 | 74755DC | 7A069DC | (Light out) | FRONT THE ENTIRE STREET - ALL THE STREET LIGHTS ON THIS STREET BURNT OUT. | High Pressure Sodium | 38.85947895000 | -76.95992491000
12/1/07 | 443681 | 3718 | 4TH ST | SE | 12/4/07 | 85728 | 8A145 | (Light out) | 295 SB BEFORE OVERLOOK POLE # 85728 - GIOVANNOI DUP. OF WO 443675 HANSEN 1656793 | High Pressure Sodium | 38.83855580000 | -77.00040988000
12/1/07 | 443675 | 3718 | 4TH ST | SE | 12/22/07 | 85728 | 8A145 | (Light out) | I 295 SOUTH BOUND BEFORE OVERLOOK ON MCGURIE AVE POLE # 85728 - OVERLOOK street light pole hit | High Pressure Sodium | 38.83855580000 | -77.00040988000
11/30/07 | 443686 | 0 | WISCONSIN AVE | NW | 12/4/07 | 30174 | 3G034 | (Light out) | SE CORNER - medal pole street light is out | High Pressure Sodium | 38.92463296000 | -77.07306999000
11/30/07 | 443562 | 741 | 51ST ST | SE | 12/3/07 | 75475 | 75475DC | (Light out) | ALLEY - 75475 wood pole light out. requesting for repair. 12-01-07 I Paraway - S Manning Repl 295 INC lamp, TL | Incandescent | 38.87911825000 | -76.93033276000
11/30/07 | 442821 | 1004 | 1ST ST | SE | 2/6/12 | 67448 | 6A023 | (Light out) | Re to DDOT - 12/10 - inside construction zone - affiliated w/442820 | High Pressure Sodium | 38.87799876000 | -77.00576406000
11/30/07 | 442820 | 900 | 1ST ST | SE |  | 67453 | 6A035 | (Light out) | Re to DDOT - 12/10 - inside construction zone - affiliated w/442821 | High Pressure Sodium | 38.87920221000 | -77.00570771000
11/30/07 | 442819 | 901 | HALF ST | SE | 12/1/07 | 67433 | 6U342 | (Light out) |  | High Pressure Sodium | 38.87894793000 | -77.00752512000
11/30/07 | 442818 | 900 | HALF ST | SE | 12/1/07 | 67434 | 6U343 | (Light out) |  | High Pressure Sodium | 38.87873279000 | -77.00752418000
11/30/07 | 442795 | 0 | SOUTH CAPITOL ST | SE | 12/5/07 | 82044 | 8M062 | (Light out) |  | High Pressure Sodium | 38.86042806000 | -77.00347620000
11/30/07 | 442765 | 0 | ANACOSTIA FWY | NE | 12/4/07 | 79490 | 7A159 | (Light out) |  | High Pressure Sodium | 38.88986353000 | -76.95869496000
11/30/07 | 442257 | 900 | U ST | NW | 11/30/07 | 13983 | 1G551 | (Light out) |  | High Pressure Sodium | 38.91713116000 | -77.02591861000
11/29/07 | 442704 | 1222 | 1ST ST | NE |  | 61245 | 6A276 | (Light out) | STREET LIGHT OUT - 1300 New Avenue, N.W. in rear of Intermerican Development Bank has two light out on metal pole. bad address close | High Pressure Sodium | 38.90699632000 | -77.00596394000
11/29/07 | 442733 | 4600 | NANNIE HELEN BURROUGHS AVE | NE | 12/1/07 | 71301DC | 7A236 | (Light out) | ACROSS THE STREET. BY 4611 NANNIE HELEN BURROUGH AVE. NE. - streetlight on wooden pole is going on and off... it's really dark when is out and the church people don't feel too safe.. please repair. | High Pressure Sodium | 38.89952817000 | -76.93621663000
11/29/07 | 442106 | 901 | 9TH ST | NW | 11/29/07 | 22987 | 2G988 | (Light out) |  | High Pressure Sodium | 38.90092176000 | -77.02415354000
11/29/07 | 442101 | 611 | K ST | NW | 4/17/08 | 22404 | 6A973 | (Light out) | faound already tagged--d. webb pole #22404 4/17/2008 | High Pressure Sodium | 38.90245457000 | -77.02040204000
11/29/07 | 441962 | 901 | 9TH ST | NW | 11/29/07 | 22987 | 2G988 | (Light out) |  | High Pressure Sodium | 38.90092176000 | -77.02415354000
11/29/07 | 441573 | 0 | H ST | NE | 11/29/07 | 62345 | 6S103 | (Light out) |  | High Pressure Sodium | 38.90012051000 | -76.99138683000
11/28/07 | 442080 | 1400 | 17TH ST | NW | 11/30/07 | 26729 | 2M081 | (Light out) | OPPOSITE - METAL POLE LIGHT WORKED FOR A NIGHT OR TWO AND NOW IT IS OFF | High Pressure Sodium | 38.90872626000 | -77.03858078000
11/28/07 | 441465 | 0 | O ST | NE | 11/29/07 | 62314 | 5M113 | (Light out) | pole# 62314 | High Pressure Sodium | 38.90852329000 | -77.00447657000
11/28/07 | 441459 | 709 | H ST | NW | 11/28/07 | 22630 | 2M424 | (Light out) |  | High Pressure Sodium | 38.89990397000 | -77.02240296000
11/28/07 | 441344 | 917 | U ST | NW | 11/28/07 | 14405 | 1G555 | (Light out) |  | High Pressure Sodium | 38.91709088000 | -77.02460528000
11/27/07 | 441366 | 0 | O ST | NE | 11/29/07 | 62315 | 5M112 | (Light out) | 200 BLOCK OF O ST NE / FRONT - street lights out #62315 and #62314 on a metal pole | High Pressure Sodium | 38.90852270000 | -77.00482604000
11/27/07 | 441369 | 0 | 1ST ST | NE | 11/29/07 | 61248 | 6A282 | (Light out) | 1300 BLOCK IF FIRST NE..EAST SIDE - light in need of repair on metal pole.....#61248 | High Pressure Sodium | 38.90791176000 | -77.00580646000
11/27/07 | 441381 | 64 | NEW YORK AVE | NE | 11/29/07 | 56751 | 5M100 | (Light out) | - light in need of repair on metal pole | High Pressure Sodium | 38.90849482000 | -77.00614254000
11/27/07 | 440636 | 5920 | GEORGIA AVE | NW | 11/28/07 | 4E219 | 4A824 | (Light out) |  | High Pressure Sodium | 38.96170865000 | -77.02785877000
11/26/07 | 440653 | 5326 | CONNECTICUT AVE | NW | 11/28/07 | 30542 | 3E017 | (Light out) | THE POLE IS ACROSS CONNECTICUT AVENUE FROM THIS ADDRESS, ON THE ODD SIDE OF THE STREET, IN THE MIDDLE OF THE BLOCK. - | High Pressure Sodium | 38.96076273000 | -77.07303810000
11/26/07 | 440039 | 0 | SOUTH CAPITOL ST | SE | 12/1/07 | 82044 | 8M062 | (Light out) | 11-24-07pole# 82044 REFER TO#442795 | High Pressure Sodium | 38.86042806000 | -77.00347620000
11/25/07 | 440022 | 1222 | 1ST ST | NE | 11/27/07 | 61245 | 6A276 | (Light out) | FRONT - streetlight missing | High Pressure Sodium | 38.90699632000 | -77.00596394000
11/21/07 | 439575 | 5928 | GEORGIA AVE | NW | 11/25/07 | 4E220 | 4A828 | (Light out) | FRONT - metal pole..burnt out bulb 11-24-07 I Paraway - S Manning - Repl TLPC, pole# 4E220 | High Pressure Sodium | 38.96245901000 | -77.02779791000
11/21/07 | 439574 | 1701 | MASSACHUSETTS AVE | NW | 11/25/07 | 27021 | 2M086 | (Light out) | NORTHWEST CORNER - metal streetlight is out #27021 11-24-07 K Greenfield Inst 400w HPS lamp, pole# 27021 | High Pressure Sodium | 38.90807048000 | -77.03866125000
11/20/07 | 438253 | 509 | 7TH ST | NW | 11/21/07 | 22431 | 6M628 | (Light out) |  | High Pressure Sodium | 38.89648966000 | -77.02200839000
11/20/07 | 438164 | 709 | H ST | NW | 11/28/07 | 22630 | 2M424 | (Light out) |  | High Pressure Sodium | 38.89990397000 | -77.02240296000
11/20/07 | 438074 | 509 | 7TH ST | NW | 11/20/07 | 22431 | 6M628 | (Light out) |  | High Pressure Sodium | 38.89648966000 | -77.02200839000
11/19/07 | 437599 | 900 | U ST | NW | 11/20/07 | 13983 | 1G551 | (Light out) |  | High Pressure Sodium | 38.91713116000 | -77.02591861000
11/19/07 | 438104 | 500 | H ST | NW | 11/22/07 | 22554 | 6M703 | (Light out) | THE STREETLIGHT IS IN FRONT OF 500 H STREET, N.W. - | High Pressure Sodium | 38.89973304000 | -77.01944712000
11/17/07 | 437470 | 0 | O ST | NE | 4/4/08 | 62315 | 5M112 | (Light out) | R Rapolla, 4-3-08, Check PT#'s 62315, 62314 These poles are energized. SL/PT#61248 needs construction conduit broke down. Refer to WO#460808. NEW YORK AVE AND M ST NE ON 1ST - street light all block on metal pole is out , Pepco has removed all f | High Pressure Sodium | 38.90852270000 | -77.00482604000
11/16/07 | 437356 | 0 | U ST | NW | 11/17/07 | 13288 | 1G548 | (Light out) | - street lights on a metal pole are out 11-17-07 L Roberto - N Woodland Repl 400w HPS lamp | High Pressure Sodium | 38.91691836000 | -77.02612231000
11/16/07 | 436441 | 0 | MASSACHUSETTS AVE | NW | 11/16/07 | 25938 | 2L555 | (Light out) |  | High Pressure Sodium | 38.90304936000 | -77.02416740000
11/15/07 | 436841 | 1300 | BRYANT ST | NE | 11/20/07 | 51336DC | 5A254 | (Light out) | ON SIDEWALK NEAR TREE BOX AREA. - ON THE SIDEWALK UP FROM 1300 BRYANT STREET, N.E. (ACROSS FROM ISRAEL BAPTIST CHURCH, RIGHT AT THE ALLEY ON THE SIDEWALK NEAR THE GRASS).. Light fixture is hanging and it desperate needs to be replaced. Caller says th | High Pressure Sodium | 38.92097735000 | -76.98895164000
11/13/07 | 434761 | 3300 | PENNSYLVANIA AVE | SE | 11/14/07 | 78544DC | 7E115DC | (Light out) | 11-13-07 30ft Wood pole - | High Pressure Sodium | 38.86824545000 | -76.95800685000
11/13/07 | 434700 | 0 | MASSACHUSETTS AVE | NW | 11/27/07 | 25938 | 2L555 | (Light out) | 11-13-07 30ft Metal pole - Needs 400 HPS Fixture (Front Corner) | High Pressure Sodium | 38.90304936000 | -77.02416740000
11/13/07 | 434640 | 775 | H ST | NE | 11/14/07 | 61991 | 6S197 | (Light out) | 11-13-07 30ft Metal pole - Needs 250 HPS Fixture | High Pressure Sodium | 38.90030060000 | -76.99586046000
11/13/07 | 434621 | 777 | H ST | NE | 11/14/07 | 61993 | 6S193 | (Light out) | 11-13-07 30ft Metal pole (Front Corner) - Needs 250 HPS fixture | High Pressure Sodium | 38.90029929000 | -76.99512291000
11/13/07 | 434617 | 26 | K ST | NE | 11/13/07 | 61212 | 6S445 | (No current) | 11-13-07 30ft Metal pole - Needs 400 HPS fixture Dup w/291667 | High Pressure Sodium | 38.90260111000 | -77.00711708000
11/13/07 | 434610 | 900 | 7TH ST | NW | 11/14/07 | 22462 | 6A084 | (Light out) | 11-13-07 30ft Metal pole - Needs a 400 HPS fixture (Front Corner) | High Pressure Sodium | 38.90225041000 | -77.02177737000
11/10/07 | 434310 | 44 | H ST | NW | 12/12/07 | 60398 | 6A199 | (No current surface with cut in dirt, sidewalk, street, and alley) | 4 splices | High Pressure Sodium | 38.90030973000 | -77.01534450000
11/10/07 | 434281 | 0 | H ST | NW | 11/10/07 | 22621 | 2G970 | (Light out) |  | High Pressure Sodium | 38.89990649000 | -77.02521079000
11/8/07 | 433425 | 1306 | L ST | SE | 11/8/07 | 66199 | 6U007 | (Light out) |  | High Pressure Sodium | 38.87748181000 | -76.98785343000
11/7/07 | 433321 | 0 | P ST | NW | 11/9/07 | 25809 | 6U459 | (Light out) | 9TH STREET NW AND P STREET NW, WASHINGTON, DC SOUTHEAST CORNER LIGHT IS OUT (THE BLOCK WHERE THE GIANT STORE IS) - | High Pressure Sodium | 38.90959101000 | -77.02381355000
11/6/07 | 432673 | 0 | LYMAN PL | NE | 11/9/07 | 59564 | 5B256 | (Light out) | ACTUALLY IN FRONT OF 1638 LYMAN PLACE, AN ABANDONED APT. BUILDING - the light is out(metal) | High Pressure Sodium | 38.90493680000 | -76.97981871000
11/6/07 | 432152 | 0 | WISCONSIN AVE | NW | 11/6/07 | 30135 | 3G009 | (Light out) |  | High Pressure Sodium | 38.92744531000 | -77.07330577000
11/3/07 | 429252 | 0 | PENNSYLVANIA AVE | NW | 11/3/07 | 28039 | 2G694 | (Light out) |  | High Pressure Sodium | 38.90227133000 | -77.04894911000
| 430917 | 0 | INTERSTATE 295 | SE | 4/16/12 | 86494 | 8A073 | (Light out) | Referred WO to Ddot (Brenda Kenney) for help in checking Contractor responsibilities for energizing new SL poles. 11-06-2007 Pole# 86494 THESE LIGHTS WERE PUT IN BY FORT MYERS AND NEVER TURNED ON | High Pressure Sodium | 38.84482511000 | -77.00710099000
| 430918 | 0 | INTERSTATE 295 | SE | 4/16/12 | 86495 | 8A074 | (Light out) | Referred WO to Ddot (Brenda Kenney) for help in checking Contractor responsibilities for energizing new SL poles. Pole# 86495 THESE LIGHTS WERE PUT IN BY FORT MYERS AND NEVER TURNED ON | High Pressure Sodium | 38.84532586000 | -77.00708398000
| 430953 | 0 | N ST | NW | 11/6/07 | 25583 | 6A791 | (Light dim) | Pole# 25583 11-06-07 L Roberto - 400 HPS, TLPC | High Pressure Sodium | 38.90719742000 | -77.02175566000
| 431004 | 418 | NEW YORK AVE | NW | 11/5/07 | 60063 | 6A172 | (Light out) | Pole# 60063 11-04-07 L Roberto Need MOT 11-05-07 P Harvin 1-400 HPS lamp | High Pressure Sodium | 38.90441345000 | -77.01718759000
| 431059 | 0 | INTERSTATE 295 | SE | 11/6/07 | 86494 | 8A073 | (Light out) | Pole# 86494 | High Pressure Sodium | 38.84482511000 | -77.00710099000
| 431060 | 0 | INTERSTATE 295 | SE | 11/6/07 | 86495 | 8A074 | (Light out) | Pole# 86495 | High Pressure Sodium | 38.84532586000 | -77.00708398000
| 431115 | 64 | NEW YORK AVE | NE | 11/3/07 | 56752 | 5M127 | (Light out) | Pole# 56752 | High Pressure Sodium | 38.90868561000 | -77.00559893000
| 431116 | 64 | NEW YORK AVE | NE | 2/14/08 | 56751 | 5M100 | (Light out) | Pole# 56751 11-04-07 N Woodland - No Current REFER TO DDOT---TRAFFIC POLE( CABLE SHARES SAME DUCT WITH TRAFFIC) | High Pressure Sodium | 38.90849482000 | -77.00614254000
| 431122 | 1301 | U ST | NW | 11/4/07 | 11721 | 1G521 | (Light out) | Pole# 11721 11-04-07 S Parker inst 400 HPS lamp, TLPC | High Pressure Sodium | 38.91709342000 | -77.03069626000
| 431186 | 0 | NEW YORK AVE | NE | 11/3/07 | 56832 | 5M053 | (Light out) | Pole# 56832 | High Pressure Sodium | 38.91324438000 | -76.99169504000
| 431197 | 0 | SOUTH CAPITOL ST | SE | 11/7/07 | 82044 | 8M062 | (Light out) | Pole# 82044 | High Pressure Sodium | 38.86042806000 | -77.00347620000
| 431221 | 3440 | WISCONSIN AVE | NW | 11/6/07 | 38771 | 3U404 | (Light out) | Pole# 38771 11-04-07M Tomlin - PC is broken, when you put pc on it won't go down without sparking 11-06-07 L Barclay - I Paraway -400 HPS Power door, TLPC | High Pressure Sodium | 38.93547449000 | -77.07299335000
11/1/07 | 428625 | 0 | MEIGS PL | NE | 11/3/07 | 54049 | 5B257 | (Light out) | CORNER - TWO STREET LIGHT ARE OUT, METAL POLES, PLEASE REPAIR. | High Pressure Sodium | 38.90542870000 | -76.98023749000
| 425578 | 3327 | O ST | NW | 11/1/07 | 21103 | 2G165 | (Light out) | Pole# 21103 38.90784692 -77.06707661 | High Pressure Sodium | 38.90782993000 | -77.06720414000
| 425646 | 1333 | NEW HAMPSHIRE AVE | NW | 10/31/07 | 24482 | 2G772 | (Light out) | Pole# 24482 38.91076291 -77.04224607 | High Pressure Sodium | 38.90845645000 | -77.04444043000
| 425764 | 0 | MONTANA AVE | NE | 10/28/07 | 59014DC | 59014 | (Light out) | Pole# 59014DC | Mercury Vapor | 38.91668894000 | -76.97782076000
| 425769 | 1400 | FLORIDA AVE | NE | 10/28/07 | 54409 | 5M287 | (Light out) | Pole# 54409 | High Pressure Sodium | 38.90038000000 | -76.98467707000
| 425775 | 0 | L ST | SE | 11/13/07 | 67703 | 6B463 | (Light out) | Pole# 67703 38.87761165 -76.99982643 2 splices | High Pressure Sodium | 38.87758688000 | -76.99992078000
| 425776 | 301 | K ST | SE | 11/2/07 | 67660 | 6A449 | (Light dim) | Pole# 67660 | High Pressure Sodium | 38.87835619000 | -77.00175680000
| 420014 | 3300 | SHERMAN AVE | NW | 11/3/07 | 12897 | 1L285 | (Light out) | Pole# 12897 38.93138299 -77.02647539 10-28-07 S Parker Defective fixture Needs 400 HPS | High Pressure Sodium | 38.93143652000 | -77.02651725000
| 420015 | 3400 | SHERMAN AVE | NW | 10/28/07 | 13070 | 1L297 | (Light out) | Pole# 13070 38.93251163 -77.02663662 10-28-07 S Parker 1-400w HPS lamp, TLPC | High Pressure Sodium | 38.93240466000 | -77.02663265000
| 420064 | 901 | 9TH ST | NW | 10/28/07 | 22987 | 2G988 | (Light out) | Pole# 22987 38.9008999 -77.02420055 | High Pressure Sodium | 38.90092176000 | -77.02415354000
| 420065 | 0 | I ST | NW | 10/28/07 | 22487 | 2G985 | (Light out) | Pole# 22487 38.90078913 -77.02344953 | High Pressure Sodium | 38.90081220000 | -77.02379981000
| 420066 | 0 | 9TH ST | NW | 10/28/07 | 22988 | 2G982 | (Light out) | Pole# 22988 38.90045274 -77.02408754 | High Pressure Sodium | 38.90042206000 | -77.02407679000
| 420073 | 737 | 7TH ST | NW | 10/28/07 | 22450 | 6M647 | (Light out) | Pole# 22450 38.89927703 -77.0218383 | High Pressure Sodium | 38.89929255000 | -77.02181765000
| 420074 | 900 | 7TH ST | NW | 10/30/07 | 22462 | 6A084 | (Light out) | Pole# 22462 38.90230948 -77.02176671 10-30-07 L Roberto 400w HPS lamp | High Pressure Sodium | 38.90225041000 | -77.02177737000
| 420078 | 0 | RHODE ISLAND AVE | NW | 11/1/07 | 25186 | 6A828 | (Light dim) | Pole# 25186 | High Pressure Sodium | 38.91225676000 | -77.02175276000
| 420113 | 0 | C ST | SW | 10/30/07 | 21785 | 6A373 | (Light out) | Pole# 21785 GPS 38.88597842 -77.01379329 | High Pressure Sodium | 38.88597703000 | -77.01373350000
| 420151 | 0 | H ST | NW | 10/28/07 | 22621 | 2G970 | (Light out) | Pole# 22621 | High Pressure Sodium | 38.89990649000 | -77.02521079000
| 420153 | 629 | H ST | NW | 10/30/07 | 22562 | 6M698 | (Light out) | Pole# 22562 | High Pressure Sodium | 38.89973430000 | -77.02106497000
| 420161 | 2201 | 22ND ST | NW | 10/31/07 | 24723 | 2G689 | (Light out) | Pole# 24723 38.90268325 -77.04896948 | High Pressure Sodium | 38.90269343000 | -77.04895947000
| 420351 | 0 | EAST CAPITOL ST | NE | 11/26/07 | 63634 | 6M824 | (Light out) | Pole# 63634 38.89005865 -76.97441271 6 splices | High Pressure Sodium | 38.89007149000 | -76.97454092000
| 420369 | 0 | H ST | NE | 10/30/07 | 62345 | 6S103 | (Light out) | Pole# 62345 38.90009025 -76.99145139 | High Pressure Sodium | 38.90012051000 | -76.99138683000
| 420418 | 4930 | NANNIE HELEN BURROUGHS AVE | NE | 10/30/07 | 71279DC | 7A213 | (Light out) | Pole# 71279DC 38.898434 -76.92987765 | High Pressure Sodium | 38.89845445000 | -76.92986688000
| 420419 | 4918 | 49TH PL | NE | 10/29/07 | 71283DC | 7A215 | (Light off/on) | Pole# 71283DC 10-29-07 M Craig 400 HPS lamp pole# 71283 | High Pressure Sodium | 38.89857711000 | -76.93088757000
10/18/07 | 405270 | 777 | H ST | NE | 2/14/08 | 61993 | 6S193 | (Light out) | LIGHT IS NEXT TO THE BANK OF AMERICA ON THE CORNER OF 8TH. ST. 8TH. & H ST. NE - 38.9003044 -76.99508551 Shared Traffic Conduit | High Pressure Sodium | 38.90029929000 | -76.99512291000
10/18/07 | 404559 | 0 | 1ST ST | NE |  | 61248 | 6A282 | (Light out) | 10-26-07 H Lancaster Manhole covered w/water on surface can't get to manhole 11-1-07 - H Lancaster - WA Chester working in area - manhole unaccessable - no feed in pole Pepco has removed all feeds from manholes - podssible redesign for new building | High Pressure Sodium | 38.90791176000 | -77.00580646000
10/18/07 | 404538 | 740 | 6TH ST | NW |  | 22513 | 6S425 | (Light out) | 10-31-07 Lights on eastside of street all have a new feed that have not been tied in as of 10/30/07 - New construction, all new foundations and feeds - 1-pole on westside (front) 740 has a broke down wrote up and drawn up 6 mos ago. Refer to construction | High Pressure Sodium | 38.89950950000 | -77.02001122000
10/17/07 | 403887 | 811 | 7TH ST | NW | 1/9/08 | 22421 | 6M664 | (Light out) | 1-8-08-C.Miller light working- complete | High Pressure Sodium | 38.90029959000 | -77.02201191000
10/5/07 | 397699 | 0 | INTERSTATE 295 | SE | 11/29/07 | 68021 | 6L976 | (Light out) | 1ST AND 2ND POLE WEST OF 11TH STREET 11-29-07 I Paraway REmoved two MV transformers, power hooked straight to fixture, inst 2-TLC on poles # 68021 & 68022 also, used butt splices | High Pressure Sodium | 38.87825876000 | -76.99174759000
9/24/07 | 391600 | 1800 | S ST | NW | 12/9/07 | 26212 | 2M114 | (Light out) | FRONT OF GAS STATION / ON S ST, NW - light is out on metal pole 9-27-07 H Lancaster - T Claggett Wires exposed in ground, 1 side HOT wire (active) coming from manhole ( Refer to Const Crew) 26212 A.Young- Installed 210' of #10 cable and made 2 spli | High Pressure Sodium | 38.91415158000 | -77.04178551000
9/11/07 | 383963 | 0 | SOUTH CAPITOL ST | SE | 11/5/07 | 82193 | 8A003 | (Light out) | Proximity: South Capitol St. and Boling AF Base | High Pressure Sodium | 38.84236743000 | -77.00879836000
7/29/07 | 291667 | 26 | K ST | NE | 12/17/07 | 61212 | 6S445 | (Light out) | ANY PRPBLEMS YOU CAN CONTACT MPO J. BURGESS @ 703 850 6489 - NEEDS M.H.CLEANED OUT Need Pepco Plat | High Pressure Sodium | 38.90260111000 | -77.00711708000